## Notes
Guidance Notes for the use of the Design Demand Calculator (DDC)
1) The DDC has been developed to utilise the Equivalent ADMD formulas provided within IMP/001/911 - Code of Practice for the Economic Development of the LV System. This tool should be used in conjunction with IMP/001/911 so that the user is familiar with the relevant design assumptions and caveats of LV system design implemented via this tool.
2) DDC provides the Equivalent ADMD (kW) for any given LV feeder depending on the number of customers and the type of load connected.
3) Based on the Equivalent ADMD (kW) values the DDC calculates the total design demand (i.e. total load) in kVA that any supplying transformer will have to supply.
4) Where a new transformer, or substation is to be established it calculates the optimum transformer size based on the total design demand values to comply with IMP/001/911.
5) The DDC calculates the Equivalent ADMD (kW) values for three typical loads which is assumed to be the majority of the network load i.e. General Domestic (GD) with no electric heating, GD with Heatpumps and GD with Electric vehicles (16A or 32A). For Equivalent ADMD (kW) values or load calculations of other forms of heating like GD with storage heaters, Direct acting space heating (DASH) and other electric heating refer to IMP/001/911.
6) The design demand in kVA can be used to establish the adequacy of any LV overhead lines, underground cables and distribution transformer sizing. The calculated equivalent ADMD values in kW are used for voltage regulation calculations in the NPg's Volt Regulation and Fault Level Calculator.
7) Where more than one LV feeder is to be used for a connection then the equivalent ADMD needs to be calculated for each individual LV feeder based on the number of properties supplied by that LV feeder. The total design demand on the LV feeder will then be provided in cell D7 to ensure the rating of the LV feeder or plant can be assessed as being adequate and an equivalent ADMD figure in kW will be provided for use with NPg's LV Volt Regulation and Fault Level calculator.
8) The optimum transformer size calculation is for new transformers to be installed. Existing transformers can be loaded up to their appropriate rating. For further info on new and existing transformer loadings refer to IMP/001/911.

## Calculator
Design Demand Calculator
Type of Demand | Customer No's | Design Demand (kVA) | Equivalent ADMD (kW) |  |  | 2026-08-05
General Domestic (GD) | 0 | 0 | No Demand | Version Details | V2.0 | 2018-08-15
GD + Heat Pumps (HP) | 0 | 0 | Eq Demand N/A
GD + 16A Electric Vehicles (EV) | 0 | 0 | Eq Demand N/A
GD + 32A Electric Vehicles (EV) | 0 | 0 | Eq Demand N/A
Total Customer No's/Demand Type and Design Demand | 0 GD, plus 0 with GD+HP, plus 0 with GD+16A EV and 0 with GD+32A EV | 0
Type of Transformer | GM |  |  |  | Input Cells
Optimum Transformer Size (kVA) | 315 |  |  |  | Calculated Cells
Note on C4: Northern Powergrid: Input the number of general domestic (GD) customers on the LV feeder or substation for what the equivalent ADMD (kW) and/or design demand (kVA) is to be calculated.
Note on C5: Northern Powergrid: Input the number of GD + heat pump customers on the LV feeder or substation for what the equivalent ADMD (kW) and/or design demand (kVA) is to be calculated.
Note on C6: Northern Powergrid: Input the number of GD + 16A Electric Vehicles customers on the LV feeder or substation for what the equivalent ADMD(kW) and/or design demand (kVA) is to be calculated.
Note on C7: Northern Powergrid: Input the number of GD + 32A Electric Vehicles customers on the LV feeder or substation for what the equivalent ADMD(kW) and/or design demand (kVA) is to be calculated.
Note on C10: Northern Powergrid: Select the type of transformer (PM = pole mounted or GM = ground mounted) what is going to be installed.
Note on C11: Northern Powergrid: The optimum transformer size is for new transformers only and based on achieving losses compliance. Other potential transformer sizes available for dedicated customer connections. For network transformers above the largest size requirement; alternative point of connections ( HV POC or multiple transformers) should be considered.

## Calculations (hidden)
Transformer Size Boundings |  |  |  | Customer | Diversified Demand of Customer (kW) |  |  |  | Sum of Demands by CMAX (kW) |  |  |  | Total Sums for Graph Line (kW) |  | (Transformer Line) | Diversified Demand of Customer (kVA) |  |  |  | Sum of Demands by CMAX (kVA) |  |  |  | Total Sums for Graph Line (kVA)
Tx Type | Lbound(kVA) | Ubound(kVA) | Size | Customer Number | General Domestic | GD + Heat Pump | GD+ 16A EV | GD+ 32A EV | Agg. General Domestic | Agg. GD + Heat Pump | GD+ 16A EV | GD+ 32A EV | Summed Demand | Agg. Sum Demand | Transformer Helper | General Domestic | GD + Heat Pump | GD+ 16A EV | GD+ 32A EV | Agg. General Domestic | Agg. GD + Heat Pump | GD+ 16A EV | GD+ 32A EV | Summed Demand | Agg. Sum Demand
PM | 0 | 20 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PM | 20 | 34 | 50 | 1 | 4.6 | 6.1 | 7.185 | 9.77 | 4.6 | 6.1 | 7.185 | 9.77 | 0 | 0 | 0 | 4.8421 | 6.4211 | 7.5632 | 10.2842 | 4.8421 | 6.4211 | 7.5632 | 10.2842 | 0 | 0
PM | 34 | 84 | 100 | 2 | 3.9494 | 5.1125 | 6.2807 | 8.6121 | 8.5494 | 11.2125 | 13.4657 | 18.3821 | 0 | 0 | 0 | 4.1573 | 5.3816 | 6.6113 | 9.0654 | 8.9994 | 11.8027 | 14.1745 | 19.3496 | 0 | 0
PM | 84 | 134 | 200 | 3 | 3.6124 | 4.6107 | 5.807 | 8.0017 | 12.1618 | 15.8233 | 19.2728 | 26.3838 | 0 | 0 | 0 | 3.8025 | 4.8534 | 6.1127 | 8.4228 | 12.8019 | 16.6561 | 20.2871 | 27.7724 | 0 | 0
PM | 134 | 265 | 315 | 4 | 3.3908 | 4.2849 | 5.4934 | 7.596 | 15.5526 | 20.1082 | 24.7662 | 33.9798 | 0 | 0 | 0 | 3.5693 | 4.5104 | 5.7825 | 7.9958 | 16.3711 | 21.1665 | 26.0697 | 35.7682 | 0 | 0
GM | 0 | 49 | 315 | 5 | 3.2284 | 4.0481 | 5.2622 | 7.296 | 18.781 | 24.1562 | 30.0284 | 41.2758 | 0 | 0 | 0 | 3.3983 | 4.2611 | 5.5392 | 7.68 | 19.7694 | 25.4276 | 31.6088 | 43.4482 | 0 | 0
GM | 49 | 219 | 315 | 6 | 3.1014 | 3.8643 | 5.0808 | 7.0601 | 21.8824 | 28.0206 | 35.1092 | 48.3359 | 0 | 0 | 0 | 3.2647 | 4.0677 | 5.3482 | 7.4317 | 23.0341 | 29.4954 | 36.957 | 50.8799 | 0 | 0
GM | 219 | 314 | 500 | 7 | 2.998 | 3.7155 | 4.9324 | 6.8668 | 24.8804 | 31.7361 | 40.0416 | 55.2027 | 0 | 0 | 0 | 3.1558 | 3.9111 | 5.192 | 7.2282 | 26.1899 | 33.4064 | 42.149 | 58.1081 | 0 | 0
GM | 314 | 554 | 800 | 8 | 2.9112 | 3.5912 | 4.8075 | 6.7038 | 27.7917 | 35.3274 | 44.8491 | 61.9065 | 0 | 0 | 0 | 3.0645 | 3.7803 | 5.0605 | 7.0566 | 29.2544 | 37.1867 | 47.2096 | 65.1647 | 0 | 0
GM | 554 | 624 | 1000 | 9 | 2.8368 | 3.4851 | 4.7001 | 6.5633 | 30.6285 | 38.8124 | 49.5491 | 68.4698 | 0 | 0 | 0 | 2.9861 | 3.6685 | 4.9474 | 6.9088 | 32.2405 | 40.8552 | 52.157 | 72.0735 | 0 | 0
GM | 624 | 1000 | 1250 | 10 | 2.7718 | 3.3928 | 4.606 | 6.4403 | 33.4002 | 42.2052 | 54.1552 | 74.9101 | 0 | 0 | 0 | 2.9177 | 3.5713 | 4.8485 | 6.7793 | 35.1581 | 44.4265 | 57.0054 | 78.8527 | 0 | 0
PM | 265 | 2147483647 | #VALUE! | 11 | 2.7143 | 3.3114 | 4.5227 | 6.331 | 36.1145 | 45.5166 | 58.6778 | 81.2411 | 0 | 0 | 0 | 2.8571 | 3.4857 | 4.7607 | 6.6643 | 38.0152 | 47.9122 | 61.7661 | 85.517 | 0 | 0
GM | 1000 | 2147483647 | #VALUE! | 12 | 2.6628 | 3.2388 | 4.4479 | 6.233 | 38.7773 | 48.7554 | 63.1257 | 87.4741 | 0 | 0 | 0 | 2.8029 | 3.4092 | 4.682 | 6.561 | 40.8182 | 51.3214 | 66.4481 | 92.078 | 0 | 0
|  |  |  | 13 | 2.6163 | 3.1734 | 4.3803 | 6.1442 | 41.3936 | 51.9288 | 67.506 | 93.6183 | 0 | 0 | 0 | 2.754 | 3.3404 | 4.6108 | 6.4676 | 43.5722 | 54.6619 | 71.0589 | 98.5456 | 0 | 0
Chart Helper (Populates Bar Chart) |  |  |  | 14 | 2.574 | 3.114 | 4.3186 | 6.0631 | 43.9676 | 55.0428 | 71.8245 | 99.6815 | 0 | 0 | 0 | 2.7095 | 3.2779 | 4.5459 | 6.3823 | 46.2817 | 57.9398 | 75.6048 | 104.9279 | 0 | 0
Series | Aggregate Demand | Transformer Capacity |  | 15 | 2.5352 | 3.0598 | 4.262 | 5.9887 | 46.5028 | 58.1026 | 76.0865 | 105.6702 | 0 | 0 | 0 | 2.6687 | 3.2208 | 4.4863 | 6.3039 | 48.9504 | 61.1606 | 80.091 | 111.2317 | 0 | 0
GD Demand | 0 | 0 |  | 16 | 2.4995 | 3.0099 | 4.2097 | 5.9199 | 49.0023 | 61.1125 | 80.2962 | 111.59 | 0 | 0 | 0 | 2.631 | 3.1683 | 4.4313 | 6.2315 | 51.5814 | 64.3289 | 84.5223 | 117.4632 | 0 | 0
GD + HP Demand | 0 | 0 |  | 17 | 2.4664 | 2.9638 | 4.1612 | 5.856 | 51.4687 | 64.0763 | 84.4574 | 117.4461 | 0 | 0 | 0 | 2.5962 | 3.1197 | 4.3802 | 6.1642 | 54.1776 | 67.4487 | 88.9025 | 123.6274 | 0 | 0
GD + 16A EV Demand | 0 | 0 |  | 18 | 2.4356 | 2.9209 | 4.116 | 5.7964 | 53.9043 | 66.9972 | 88.5734 | 123.2425 | 0 | 0 | 0 | 2.5637 | 3.0746 | 4.3326 | 6.1015 | 56.7413 | 70.5233 | 93.2351 | 129.729 | 0 | 0
GD + 32A EV Demand | 0 | 0 |  | 19 | 2.4068 | 2.8809 | 4.0737 | 5.7407 | 56.311 | 69.8781 | 92.6471 | 128.9832 | 0 | 0 | 0 | 2.5334 | 3.0326 | 4.2881 | 6.0428 | 59.2748 | 73.5559 | 97.5233 | 135.7718 | 0 | 0
Transformer Capacity | 0 | 315 |  | 20 | 2.3797 | 2.8435 | 4.034 | 5.6883 | 58.6908 | 72.7216 | 96.6811 | 134.6715 | 0 | 0 | 0 | 2.505 | 2.9932 | 4.2463 | 5.9877 | 61.7798 | 76.5491 | 101.7696 | 141.7595 | 0 | 0
|  |  |  | 21 | 2.3543 | 2.8084 | 3.9966 | 5.6389 | 61.0451 | 75.5301 | 100.6778 | 140.3104 | 0 | 0 | 0 | 2.4783 | 2.9562 | 4.207 | 5.9357 | 64.258 | 79.5053 | 105.9766 | 147.6952 | 0 | 0
|  |  |  | 22 | 2.3304 | 2.7753 | 3.9613 | 5.5923 | 63.3755 | 78.3054 | 104.6391 | 145.9027 | 0 | 0 | 0 | 2.453 | 2.9214 | 4.1698 | 5.8866 | 66.711 | 82.4267 | 110.1464 | 153.5818 | 0 | 0
|  |  |  | 23 | 2.3077 | 2.7441 | 3.9279 | 5.5481 | 65.6832 | 81.0495 | 108.5669 | 151.4507 | 0 | 0 | 0 | 2.4291 | 2.8885 | 4.1346 | 5.8401 | 69.1402 | 85.3152 | 114.281 | 159.4218 | 0 | 0
|  |  |  | 24 | 2.2862 | 2.7145 | 3.8961 | 5.5061 | 67.9694 | 83.7639 | 112.4631 | 156.9568 | 0 | 0 | 0 | 2.4065 | 2.8573 | 4.1012 | 5.7959 | 71.5467 | 88.1726 | 118.3822 | 165.2177 | 0 | 0
|  |  |  | 25 | 2.2657 | 2.6864 | 3.8659 | 5.4661 | 70.2351 | 86.4503 | 116.329 | 162.4229 | 0 | 0 | 0 | 2.385 | 2.8278 | 4.0694 | 5.7538 | 73.9317 | 91.0004 | 122.4516 | 170.9714 | 0 | 0
|  |  |  | 26 | 2.2463 | 2.6597 | 3.8371 | 5.428 | 72.4814 | 89.11 | 120.1661 | 167.8509 | 0 | 0 | 0 | 2.3645 | 2.7997 | 4.0391 | 5.7137 | 76.2962 | 93.8 | 126.4906 | 176.6851 | 0 | 0
|  |  |  | 27 | 2.2277 | 2.6342 | 3.8096 | 5.3916 | 74.7091 | 91.7443 | 123.9758 | 173.2424 | 0 | 0 | 0 | 2.345 | 2.7729 | 4.0101 | 5.6753 | 78.6411 | 96.5729 | 130.5008 | 182.3604 | 0 | 0
|  |  |  | 28 | 2.21 | 2.6099 | 3.7833 | 5.3567 | 76.919 | 94.3542 | 127.7591 | 178.5991 | 0 | 0 | 0 | 2.3263 | 2.7473 | 3.9825 | 5.6386 | 80.9674 | 99.3202 | 134.4832 | 187.9991 | 0 | 0
|  |  |  | 29 | 2.193 | 2.5867 | 3.7581 | 5.3233 | 79.112 | 96.9409 | 131.5172 | 183.9224 | 0 | 0 | 0 | 2.3084 | 2.7229 | 3.9559 | 5.6035 | 83.2758 | 102.0431 | 138.4392 | 193.6026 | 0 | 0
|  |  |  | 30 | 2.1767 | 2.5645 | 3.734 | 5.2912 | 81.2887 | 99.5054 | 135.2512 | 189.2137 | 0 | 0 | 0 | 2.2912 | 2.6994 | 3.9305 | 5.5697 | 85.567 | 104.7425 | 142.3697 | 199.1723 | 0 | 0
|  |  |  | 31 | 2.161 | 2.5431 | 3.7107 | 5.2604 | 83.4497 | 102.0485 | 138.9619 | 194.4741 | 0 | 0 | 0 | 2.2748 | 2.677 | 3.906 | 5.5373 | 87.8418 | 107.4195 | 146.2757 | 204.7096 | 0 | 0
|  |  |  | 32 | 2.146 | 2.5226 | 3.6884 | 5.2307 | 85.5956 | 104.5711 | 142.6503 | 199.7049 | 0 | 0 | 0 | 2.2589 | 2.6554 | 3.8825 | 5.5061 | 90.1007 | 110.0749 | 150.1582 | 210.2156 | 0 | 0
|  |  |  | 33 | 2.1315 | 2.5029 | 3.6668 | 5.2022 | 87.7271 | 107.0741 | 146.3171 | 204.907 | 0 | 0 | 0 | 2.2437 | 2.6347 | 3.8598 | 5.476 | 92.3444 | 112.7095 | 154.018 | 215.6916 | 0 | 0
|  |  |  | 34 | 2.1175 | 2.484 | 3.6461 | 5.1746 | 89.8447 | 109.558 | 149.9631 | 210.0816 | 0 | 0 | 0 | 2.229 | 2.6147 | 3.838 | 5.4469 | 94.5734 | 115.3243 | 157.8559 | 221.1385 | 0 | 0
|  |  |  | 35 | 2.1041 | 2.4657 | 3.626 | 5.1479 | 91.9488 | 112.0237 | 153.5892 | 215.2295 | 0 | 0 | 0 | 2.2148 | 2.5955 | 3.8169 | 5.4189 | 96.7882 | 117.9197 | 161.6728 | 226.5574 | 0 | 0
|  |  |  | 36 | 2.0911 | 2.4481 | 3.6066 | 5.1222 | 94.0399 | 114.4718 | 157.1958 | 220.3517 | 0 | 0 | 0 | 2.2011 | 2.5769 | 3.7965 | 5.3918 | 98.9893 | 120.4966 | 165.4693 | 231.9492 | 0 | 0
|  |  |  | 37 | 2.0785 | 2.431 | 3.5879 | 5.0973 | 96.1184 | 116.9028 | 160.7837 | 225.449 | 0 | 0 | 0 | 2.1879 | 2.559 | 3.7767 | 5.3656 | 101.1772 | 123.0556 | 169.246 | 237.3147 | 0 | 0
|  |  |  | 38 | 2.0664 | 2.4146 | 3.5698 | 5.0731 | 98.1847 | 119.3174 | 164.3534 | 230.5221 | 0 | 0 | 0 | 2.1751 | 2.5417 | 3.7576 | 5.3402 | 103.3523 | 125.5973 | 173.0036 | 242.6549 | 0 | 0
|  |  |  | 39 | 2.0546 | 2.3986 | 3.5522 | 5.0498 | 100.2393 | 121.7161 | 167.9056 | 235.5719 | 0 | 0 | 0 | 2.1627 | 2.5249 | 3.7391 | 5.3155 | 105.5151 | 128.1222 | 176.7427 | 247.9704 | 0 | 0
|  |  |  | 40 | 2.0432 | 2.3832 | 3.5351 | 5.0271 | 102.2825 | 124.0993 | 171.4407 | 240.599 | 0 | 0 | 0 | 2.1507 | 2.5087 | 3.7212 | 5.2916 | 107.6658 | 130.6308 | 180.4639 | 253.2621 | 0 | 0
|  |  |  | 41 | 2.0321 | 2.3683 | 3.5186 | 5.005 | 104.3146 | 126.4676 | 174.9593 | 245.604 | 0 | 0 | 0 | 2.1391 | 2.4929 | 3.7038 | 5.2685 | 109.8048 | 133.1238 | 184.1677 | 258.5305 | 0 | 0
|  |  |  | 42 | 2.0214 | 2.3538 | 3.5025 | 4.9836 | 106.3359 | 128.8214 | 178.4618 | 250.5876 | 0 | 0 | 0 | 2.1277 | 2.4777 | 3.6868 | 5.2459 | 111.9326 | 135.6014 | 187.8545 | 263.7765 | 0 | 0
|  |  |  | 43 | 2.0109 | 2.3397 | 3.4869 | 4.9628 | 108.3469 | 131.1611 | 181.9487 | 255.5505 | 0 | 0 | 0 | 2.1168 | 2.4629 | 3.6704 | 5.224 | 114.0493 | 138.0643 | 191.5249 | 269.0005 | 0 | 0
|  |  |  | 44 | 2.0008 | 2.3261 | 3.4717 | 4.9426 | 110.3476 | 133.4871 | 185.4204 | 260.4931 | 0 | 0 | 0 | 2.1061 | 2.4485 | 3.6544 | 5.2027 | 116.1554 | 140.5128 | 195.1793 | 274.2032 | 0 | 0
|  |  |  | 45 | 1.9909 | 2.3128 | 3.4569 | 4.9229 | 112.3385 | 135.7999 | 188.8773 | 265.416 | 0 | 0 | 0 | 2.0957 | 2.4345 | 3.6388 | 5.182 | 118.2511 | 142.9472 | 198.8182 | 279.3852 | 0 | 0
|  |  |  | 46 | 1.9813 | 2.2999 | 3.4425 | 4.9037 | 114.3198 | 138.0997 | 192.3198 | 270.3197 | 0 | 0 | 0 | 2.0856 | 2.4209 | 3.6237 | 5.1618 | 120.3367 | 145.3682 | 202.4419 | 284.547 | 0 | 0
|  |  |  | 47 | 1.972 | 2.2873 | 3.4285 | 4.885 | 116.2918 | 140.387 | 195.7482 | 275.2047 | 0 | 0 | 0 | 2.0757 | 2.4077 | 3.6089 | 5.1421 | 122.4124 | 147.7758 | 206.0508 | 289.6891 | 0 | 0
|  |  |  | 48 | 1.9628 | 2.2751 | 3.4148 | 4.8668 | 118.2546 | 142.6621 | 199.163 | 280.0714 | 0 | 0 | 0 | 2.0661 | 2.3948 | 3.5945 | 5.1229 | 124.4786 | 150.1706 | 209.6453 | 294.812 | 0 | 0
|  |  |  | 49 | 1.954 | 2.2631 | 3.4015 | 4.849 | 120.2086 | 144.9252 | 202.5645 | 284.9204 | 0 | 0 | 0 | 2.0568 | 2.3822 | 3.5805 | 5.1042 | 126.5354 | 152.5529 | 213.2258 | 299.9162 | 0 | 0
|  |  |  | 50 | 1.9453 | 2.2515 | 3.3884 | 4.8316 | 122.1539 | 147.1767 | 205.953 | 289.752 | 0 | 0 | 0 | 2.0477 | 2.37 | 3.5668 | 5.0859 | 128.583 | 154.9229 | 216.7926 | 305.0021 | 0 | 0
|  |  |  | 51 | 1.9368 | 2.2402 | 3.3757 | 4.8146 | 124.0907 | 149.4169 | 209.3287 | 294.5667 | 0 | 0 | 0 | 2.0388 | 2.3581 | 3.5534 | 5.068 | 130.6218 | 157.281 | 220.346 | 310.0702 | 0 | 0
|  |  |  | 52 | 1.9286 | 2.2291 | 3.3633 | 4.7981 | 126.0193 | 151.646 | 212.692 | 299.3647 | 0 | 0 | 0 | 2.0301 | 2.3465 | 3.5403 | 5.0506 | 132.6519 | 159.6274 | 223.8863 | 315.1208 | 0 | 0
|  |  |  | 53 | 1.9205 | 2.2183 | 3.3512 | 4.7819 | 127.9398 | 153.8644 | 216.0432 | 304.1466 | 0 | 0 | 0 | 2.0216 | 2.3351 | 3.5276 | 5.0336 | 134.6735 | 161.9625 | 227.4139 | 320.1543 | 0 | 0
|  |  |  | 54 | 1.9126 | 2.2078 | 3.3393 | 4.766 | 129.8524 | 156.0722 | 219.3826 | 308.9127 | 0 | 0 | 0 | 2.0133 | 2.324 | 3.5151 | 5.0169 | 136.6868 | 164.2865 | 230.929 | 325.1712 | 0 | 0
|  |  |  | 55 | 1.9049 | 2.1975 | 3.3277 | 4.7505 | 131.7574 | 158.2697 | 222.7103 | 313.6632 | 0 | 0 | 0 | 2.0052 | 2.3132 | 3.5029 | 5.0006 | 138.692 | 166.5997 | 234.4319 | 330.1718 | 0 | 0
|  |  |  | 56 | 1.8974 | 2.1874 | 3.3164 | 4.7354 | 133.6548 | 160.4571 | 226.0267 | 318.3986 | 0 | 0 | 0 | 1.9973 | 2.3026 | 3.4909 | 4.9846 | 140.6892 | 168.9022 | 237.9228 | 335.1564 | 0 | 0
|  |  |  | 57 | 1.89 | 2.1776 | 3.3053 | 4.7205 | 135.5448 | 162.6347 | 229.3319 | 323.1191 | 0 | 0 | 0 | 1.9895 | 2.2922 | 3.4792 | 4.969 | 142.6787 | 171.1944 | 241.402 | 340.1254 | 0 | 0
|  |  |  | 58 | 1.8828 | 2.168 | 3.2944 | 4.706 | 137.4276 | 164.8027 | 232.6263 | 327.8251 | 0 | 0 | 0 | 1.9819 | 2.2821 | 3.4678 | 4.9537 | 144.6606 | 173.4765 | 244.8698 | 345.0791 | 0 | 0
|  |  |  | 59 | 1.8757 | 2.1585 | 3.2837 | 4.6917 | 139.3033 | 166.9612 | 235.9101 | 332.5168 | 0 | 0 | 0 | 1.9745 | 2.2722 | 3.4566 | 4.9387 | 146.6351 | 175.7487 | 248.3264 | 350.0177 | 0 | 0
|  |  |  | 60 | 1.8688 | 2.1493 | 3.2733 | 4.6778 | 141.1721 | 169.1105 | 239.1834 | 337.1946 | 0 | 0 | 0 | 1.9672 | 2.2624 | 3.4456 | 4.924 | 148.6022 | 178.0111 | 251.772 | 354.9417 | 0 | 0
|  |  |  | 61 | 1.862 | 2.1403 | 3.2631 | 4.6641 | 143.0341 | 171.2508 | 242.4464 | 341.8587 | 0 | 0 | 0 | 1.96 | 2.2529 | 3.4348 | 4.9096 | 150.5622 | 180.264 | 255.2067 | 359.8512 | 0 | 0
|  |  |  | 62 | 1.8554 | 2.1314 | 3.253 | 4.6506 | 144.8895 | 173.3823 | 245.6994 | 346.5093 | 0 | 0 | 0 | 1.953 | 2.2436 | 3.4242 | 4.8954 | 152.5153 | 182.5077 | 258.631 | 364.7467 | 0 | 0
|  |  |  | 63 | 1.8489 | 2.1228 | 3.2432 | 4.6375 | 146.7384 | 175.505 | 248.9426 | 351.1468 | 0 | 0 | 0 | 1.9462 | 2.2345 | 3.4139 | 4.8815 | 154.4614 | 184.7421 | 262.0448 | 369.6282 | 0 | 0
|  |  |  | 64 | 1.8425 | 2.1143 | 3.2335 | 4.6245 | 148.5808 | 177.6193 | 252.1761 | 355.7713 | 0 | 0 | 0 | 1.9394 | 2.2255 | 3.4037 | 4.8679 | 156.4009 | 186.9677 | 265.4485 | 374.4962 | 0 | 0
|  |  |  | 65 | 1.8362 | 2.1059 | 3.224 | 4.6118 | 150.417 | 179.7252 | 255.4001 | 360.3832 | 0 | 0 | 0 | 1.9328 | 2.2168 | 3.3937 | 4.8546 | 158.3337 | 189.1845 | 268.8422 | 379.3507 | 0 | 0
|  |  |  | 66 | 1.83 | 2.0978 | 3.2147 | 4.5994 | 152.247 | 181.823 | 258.6148 | 364.9826 | 0 | 0 | 0 | 1.9263 | 2.2082 | 3.3839 | 4.8415 | 160.26 | 191.3926 | 272.2261 | 384.1922 | 0 | 0
|  |  |  | 67 | 1.824 | 2.0897 | 3.2056 | 4.5871 | 154.071 | 183.9127 | 261.8204 | 369.5697 | 0 | 0 | 0 | 1.92 | 2.1997 | 3.3743 | 4.8286 | 162.18 | 193.5924 | 275.6004 | 389.0208 | 0 | 0
|  |  |  | 68 | 1.8181 | 2.0819 | 3.1966 | 4.5751 | 155.8891 | 185.9946 | 265.017 | 374.1448 | 0 | 0 | 0 | 1.9137 | 2.1914 | 3.3648 | 4.8159 | 164.0938 | 195.7838 | 278.9652 | 393.8367 | 0 | 0
|  |  |  | 69 | 1.8122 | 2.0741 | 3.1878 | 4.5633 | 157.7013 | 188.0687 | 268.2047 | 378.7081 | 0 | 0 | 0 | 1.9076 | 2.1833 | 3.3555 | 4.8035 | 166.0014 | 197.9671 | 282.3207 | 398.6401 | 0 | 0
|  |  |  | 70 | 1.8065 | 2.0665 | 3.1791 | 4.5517 | 159.5078 | 190.1353 | 271.3838 | 383.2598 | 0 | 0 | 0 | 1.9016 | 2.1753 | 3.3464 | 4.7912 | 167.9029 | 200.1424 | 285.6671 | 403.4314 | 0 | 0
|  |  |  | 71 | 1.8009 | 2.0591 | 3.1706 | 4.5402 | 161.3087 | 192.1944 | 274.5543 | 387.8 | 0 | 0 | 0 | 1.8956 | 2.1675 | 3.3374 | 4.7792 | 169.7986 | 202.3099 | 289.0046 | 408.2106 | 0 | 0
|  |  |  | 72 | 1.7953 | 2.0518 | 3.1622 | 4.529 | 163.104 | 194.2461 | 277.7165 | 392.3291 | 0 | 0 | 0 | 1.8898 | 2.1598 | 3.3286 | 4.7674 | 171.6884 | 204.4696 | 292.3332 | 412.978 | 0 | 0
|  |  |  | 73 | 1.7899 | 2.0446 | 3.1539 | 4.518 | 164.8939 | 196.2907 | 280.8704 | 396.847 | 0 | 0 | 0 | 1.8841 | 2.1522 | 3.3199 | 4.7557 | 173.5725 | 206.6218 | 295.6531 | 417.7337 | 0 | 0
|  |  |  | 74 | 1.7845 | 2.0375 | 3.1458 | 4.5071 | 166.6784 | 198.3282 | 284.0163 | 401.3541 | 0 | 0 | 0 | 1.8785 | 2.1447 | 3.3114 | 4.7443 | 175.451 | 208.7665 | 298.9645 | 422.478 | 0 | 0
|  |  |  | 75 | 1.7793 | 2.0305 | 3.1378 | 4.4964 | 168.4577 | 200.3587 | 287.1541 | 405.8505 | 0 | 0 | 0 | 1.8729 | 2.1374 | 3.303 | 4.733 | 177.3239 | 210.9039 | 302.2675 | 427.211 | 0 | 0
|  |  |  | 76 | 1.7741 | 2.0237 | 3.13 | 4.4859 | 170.2318 | 202.3824 | 290.2841 | 410.3363 | 0 | 0 | 0 | 1.8675 | 2.1302 | 3.2947 | 4.7219 | 179.1914 | 213.0341 | 305.5622 | 431.933 | 0 | 0
|  |  |  | 77 | 1.769 | 2.017 | 3.1222 | 4.4755 | 172.0008 | 204.3994 | 293.4063 | 414.8118 | 0 | 0 | 0 | 1.8621 | 2.1231 | 3.2866 | 4.711 | 181.0535 | 215.1573 | 308.8488 | 436.644 | 0 | 0
|  |  |  | 78 | 1.764 | 2.0103 | 3.1146 | 4.4653 | 173.7648 | 206.4098 | 296.5209 | 419.2771 | 0 | 0 | 0 | 1.8568 | 2.1162 | 3.2786 | 4.7003 | 182.9103 | 217.2734 | 312.1273 | 441.3443 | 0 | 0
|  |  |  | 79 | 1.7591 | 2.0038 | 3.1071 | 4.4552 | 175.5239 | 208.4136 | 299.6281 | 423.7323 | 0 | 0 | 0 | 1.8516 | 2.1093 | 3.2707 | 4.6897 | 184.762 | 219.3827 | 315.398 | 446.034 | 0 | 0
|  |  |  | 80 | 1.7542 | 1.9974 | 3.0997 | 4.4453 | 177.2781 | 210.411 | 302.7278 | 428.1776 | 0 | 0 | 0 | 1.8465 | 2.1026 | 3.2629 | 4.6793 | 186.6085 | 221.4853 | 318.6609 | 450.7133 | 0 | 0
|  |  |  | 81 | 1.7494 | 1.9911 | 3.0925 | 4.4355 | 179.0275 | 212.4021 | 305.8203 | 432.6131 | 0 | 0 | 0 | 1.8415 | 2.0959 | 3.2552 | 4.669 | 188.45 | 223.5812 | 321.9161 | 455.3822 | 0 | 0
|  |  |  | 82 | 1.7447 | 1.9849 | 3.0853 | 4.4259 | 180.7722 | 214.387 | 308.9056 | 437.039 | 0 | 0 | 0 | 1.8365 | 2.0894 | 3.2477 | 4.6589 | 190.2865 | 225.6706 | 325.1638 | 460.0411 | 0 | 0
|  |  |  | 83 | 1.74 | 1.9788 | 3.0782 | 4.4164 | 182.5122 | 216.3658 | 311.9838 | 441.4555 | 0 | 0 | 0 | 1.8316 | 2.0829 | 3.2402 | 4.6489 | 192.1181 | 227.7535 | 328.404 | 464.69 | 0 | 0
|  |  |  | 84 | 1.7355 | 1.9727 | 3.0713 | 4.4071 | 184.2477 | 218.3385 | 315.0551 | 445.8625 | 0 | 0 | 0 | 1.8268 | 2.0766 | 3.2329 | 4.639 | 193.9449 | 229.83 | 331.637 | 469.329 | 0 | 0
|  |  |  | 85 | 1.731 | 1.9668 | 3.0644 | 4.3979 | 185.9786 | 220.3054 | 318.1195 | 450.2604 | 0 | 0 | 0 | 1.8221 | 2.0703 | 3.2257 | 4.6293 | 195.767 | 231.9004 | 334.8626 | 473.9583 | 0 | 0
|  |  |  | 86 | 1.7265 | 1.961 | 3.0576 | 4.3888 | 187.7051 | 222.2663 | 321.1771 | 454.6492 | 0 | 0 | 0 | 1.8174 | 2.0642 | 3.2186 | 4.6198 | 197.5843 | 233.9645 | 338.0812 | 478.5781 | 0 | 0
|  |  |  | 87 | 1.7221 | 1.9552 | 3.051 | 4.3798 | 189.4272 | 224.2215 | 324.2281 | 459.029 | 0 | 0 | 0 | 1.8128 | 2.0581 | 3.2115 | 4.6103 | 199.3971 | 236.0226 | 341.2927 | 483.1884 | 0 | 0
|  |  |  | 88 | 1.7178 | 1.9495 | 3.0444 | 4.371 | 191.145 | 226.171 | 327.2725 | 463.3999 | 0 | 0 | 0 | 1.8082 | 2.0521 | 3.2046 | 4.601 | 201.2053 | 238.0747 | 344.4973 | 487.7894 | 0 | 0
|  |  |  | 89 | 1.7135 | 1.9439 | 3.0379 | 4.3622 | 192.8586 | 228.1149 | 330.3104 | 467.7621 | 0 | 0 | 0 | 1.8037 | 2.0462 | 3.1978 | 4.5918 | 203.009 | 240.121 | 347.6951 | 492.3812 | 0 | 0
|  |  |  | 90 | 1.7093 | 1.9384 | 3.0315 | 4.3536 | 194.5679 | 230.0533 | 333.3418 | 472.1157 | 0 | 0 | 0 | 1.7993 | 2.0404 | 3.191 | 4.5827 | 204.8083 | 242.1613 | 350.8861 | 496.9639 | 0 | 0
|  |  |  | 91 | 1.7052 | 1.9329 | 3.0251 | 4.3451 | 196.2731 | 231.9862 | 336.367 | 476.4609 | 0 | 0 | 0 | 1.7949 | 2.0347 | 3.1844 | 4.5738 | 206.6032 | 244.196 | 354.0705 | 501.5377 | 0 | 0
|  |  |  | 92 | 1.7011 | 1.9276 | 3.0189 | 4.3367 | 197.9742 | 233.9138 | 339.3859 | 480.7976 | 0 | 0 | 0 | 1.7906 | 2.029 | 3.1778 | 4.565 | 208.3938 | 246.225 | 357.2483 | 506.1027 | 0 | 0
|  |  |  | 93 | 1.697 | 1.9222 | 3.0127 | 4.3284 | 199.6712 | 235.836 | 342.3986 | 485.126 | 0 | 0 | 0 | 1.7864 | 2.0234 | 3.1713 | 4.5562 | 210.1802 | 248.2484 | 360.4196 | 510.659 | 0 | 0
|  |  |  | 94 | 1.693 | 1.917 | 3.0067 | 4.3203 | 201.3642 | 237.753 | 345.4053 | 489.4463 | 0 | 0 | 0 | 1.7822 | 2.0179 | 3.1649 | 4.5476 | 211.9624 | 250.2663 | 363.5845 | 515.2066 | 0 | 0
|  |  |  | 95 | 1.6891 | 1.9119 | 3.0006 | 4.3122 | 203.0534 | 239.6649 | 348.4059 | 493.7585 | 0 | 0 | 0 | 1.778 | 2.0125 | 3.1586 | 4.5391 | 213.7404 | 252.2788 | 366.7431 | 519.7457 | 0 | 0
|  |  |  | 96 | 1.6852 | 1.9068 | 2.9947 | 4.3042 | 204.7386 | 241.5716 | 351.4006 | 498.0627 | 0 | 0 | 0 | 1.7739 | 2.0071 | 3.1523 | 4.5307 | 215.5143 | 254.2859 | 369.8954 | 524.2765 | 0 | 0
|  |  |  | 97 | 1.6814 | 1.9017 | 2.9889 | 4.2963 | 206.42 | 243.4734 | 354.3895 | 502.359 | 0 | 0 | 0 | 1.7699 | 2.0018 | 3.1462 | 4.5224 | 217.2842 | 256.2878 | 373.0416 | 528.7989 | 0 | 0
|  |  |  | 98 | 1.6776 | 1.8968 | 2.9831 | 4.2885 | 208.0976 | 245.3702 | 357.3725 | 506.6475 | 0 | 0 | 0 | 1.7659 | 1.9966 | 3.1401 | 4.5143 | 219.0501 | 258.2844 | 376.1816 | 533.3132 | 0 | 0
|  |  |  | 99 | 1.6739 | 1.8919 | 2.9774 | 4.2809 | 209.7714 | 247.262 | 360.3499 | 510.9284 | 0 | 0 | 0 | 1.762 | 1.9914 | 3.1341 | 4.5062 | 220.812 | 260.2758 | 379.3157 | 537.8194 | 0 | 0
|  |  |  | 100 | 1.6702 | 1.887 | 2.9717 | 4.2733 | 211.4416 | 249.1491 | 363.3216 | 515.2016 | 0 | 0 | 0 | 1.7581 | 1.9864 | 3.1281 | 4.4982 | 222.5701 | 262.2622 | 382.4438 | 542.3175 | 0 | 0
|  |  |  | 101 | 1.6665 | 1.8823 | 2.9661 | 4.2657 | 213.1081 | 251.0313 | 366.2877 | 519.4674 | 0 | 0 | 0 | 1.7542 | 1.9813 | 3.1222 | 4.4903 | 224.3243 | 264.2435 | 385.566 | 546.8078 | 0 | 0
|  |  |  | 102 | 1.6629 | 1.8775 | 2.9606 | 4.2583 | 214.771 | 252.9089 | 369.2484 | 523.7257 | 0 | 0 | 0 | 1.7504 | 1.9764 | 3.1164 | 4.4824 | 226.0747 | 266.2198 | 388.6825 | 551.2902 | 0 | 0
|  |  |  | 103 | 1.6593 | 1.8729 | 2.9552 | 4.251 | 216.4303 | 254.7817 | 372.2035 | 527.9767 | 0 | 0 | 0 | 1.7467 | 1.9714 | 3.1107 | 4.4747 | 227.8214 | 268.1913 | 391.7932 | 555.765 | 0 | 0
|  |  |  | 104 | 1.6558 | 1.8683 | 2.9498 | 4.2437 | 218.0861 | 256.65 | 375.1533 | 532.2205 | 0 | 0 | 0 | 1.743 | 1.9666 | 3.105 | 4.4671 | 229.5643 | 270.1579 | 394.8982 | 560.2321 | 0 | 0
|  |  |  | 105 | 1.6523 | 1.8637 | 2.9444 | 4.2366 | 219.7385 | 258.5137 | 378.0977 | 536.457 | 0 | 0 | 0 | 1.7393 | 1.9618 | 3.0994 | 4.4595 | 231.3036 | 272.1197 | 397.9976 | 564.6916 | 0 | 0
|  |  |  | 106 | 1.6489 | 1.8592 | 2.9392 | 4.2295 | 221.3873 | 260.373 | 381.0369 | 540.6865 | 0 | 0 | 0 | 1.7357 | 1.9571 | 3.0939 | 4.4521 | 233.0393 | 274.0768 | 401.0915 | 569.1437 | 0 | 0
|  |  |  | 107 | 1.6455 | 1.8548 | 2.934 | 4.2225 | 223.0328 | 262.2277 | 383.9709 | 544.909 | 0 | 0 | 0 | 1.7321 | 1.9524 | 3.0884 | 4.4447 | 234.7714 | 276.0292 | 404.1799 | 573.5884 | 0 | 0
|  |  |  | 108 | 1.6421 | 1.8504 | 2.9288 | 4.2155 | 224.6749 | 264.0781 | 386.8997 | 549.1245 | 0 | 0 | 0 | 1.7285 | 1.9478 | 3.083 | 4.4374 | 236.4999 | 277.977 | 407.2629 | 578.0258 | 0 | 0
|  |  |  | 109 | 1.6388 | 1.8461 | 2.9237 | 4.2087 | 226.3137 | 265.9242 | 389.8235 | 553.3332 | 0 | 0 | 0 | 1.725 | 1.9432 | 3.0776 | 4.4302 | 238.225 | 279.9202 | 410.3405 | 582.456 | 0 | 0
|  |  |  | 110 | 1.6355 | 1.8418 | 2.9187 | 4.2019 | 227.9492 | 267.766 | 392.7422 | 557.5351 | 0 | 0 | 0 | 1.7216 | 1.9387 | 3.0723 | 4.423 | 239.9466 | 281.8589 | 413.4128 | 586.879 | 0 | 0
|  |  |  | 111 | 1.6323 | 1.8375 | 2.9137 | 4.1952 | 229.5815 | 269.6035 | 395.6559 | 561.7303 | 0 | 0 | 0 | 1.7182 | 1.9342 | 3.0671 | 4.416 | 241.6647 | 283.7931 | 416.4799 | 591.295 | 0 | 0
|  |  |  | 112 | 1.629 | 1.8333 | 2.9088 | 4.1885 | 231.2105 | 271.4368 | 398.5647 | 565.9188 | 0 | 0 | 0 | 1.7148 | 1.9298 | 3.0619 | 4.409 | 243.3795 | 285.7229 | 419.5418 | 595.704 | 0 | 0
|  |  |  | 113 | 1.6259 | 1.8292 | 2.9039 | 4.182 | 232.8364 | 273.266 | 401.4686 | 570.1008 | 0 | 0 | 0 | 1.7114 | 1.9255 | 3.0567 | 4.4021 | 245.0909 | 287.6484 | 422.5985 | 600.1061 | 0 | 0
|  |  |  | 114 | 1.6227 | 1.8251 | 2.8991 | 4.1755 | 234.4591 | 275.0911 | 404.3677 | 574.2763 | 0 | 0 | 0 | 1.7081 | 1.9211 | 3.0517 | 4.3952 | 246.799 | 289.5695 | 425.6502 | 604.5013 | 0 | 0
|  |  |  | 115 | 1.6196 | 1.821 | 2.8943 | 4.169 | 236.0787 | 276.9121 | 407.262 | 578.4453 | 0 | 0 | 0 | 1.7048 | 1.9169 | 3.0466 | 4.3885 | 248.5039 | 291.4864 | 428.6968 | 608.8898 | 0 | 0
|  |  |  | 116 | 1.6165 | 1.817 | 2.8896 | 4.1627 | 237.6952 | 278.7291 | 410.1516 | 582.608 | 0 | 0 | 0 | 1.7016 | 1.9126 | 3.0417 | 4.3818 | 250.2054 | 293.399 | 431.7385 | 613.2715 | 0 | 0
|  |  |  | 117 | 1.6135 | 1.813 | 2.8849 | 4.1564 | 239.3086 | 280.5421 | 413.0365 | 586.7643 | 0 | 0 | 0 | 1.6984 | 1.9085 | 3.0367 | 4.3751 | 251.9038 | 295.3075 | 434.7752 | 617.6467 | 0 | 0
|  |  |  | 118 | 1.6104 | 1.8091 | 2.8803 | 4.1501 | 240.9191 | 282.3513 | 415.9168 | 590.9145 | 0 | 0 | 0 | 1.6952 | 1.9043 | 3.0319 | 4.3686 | 253.599 | 297.2118 | 437.8071 | 622.0152 | 0 | 0
|  |  |  | 119 | 1.6075 | 1.8052 | 2.8757 | 4.1439 | 242.5265 | 284.1565 | 418.7925 | 595.0584 | 0 | 0 | 0 | 1.6921 | 1.9002 | 3.0271 | 4.362 | 255.2911 | 299.1121 | 440.8342 | 626.3773 | 0 | 0
|  |  |  | 120 | 1.6045 | 1.8014 | 2.8712 | 4.1378 | 244.131 | 285.9579 | 421.6636 | 599.1962 | 0 | 0 | 0 | 1.6889 | 1.8962 | 3.0223 | 4.3556 | 256.98 | 301.0083 | 443.8564 | 630.7329 | 0 | 0
|  |  |  | 121 | 1.6016 | 1.7976 | 2.8667 | 4.1318 | 245.7326 | 287.7554 | 424.5303 | 603.328 | 0 | 0 | 0 | 1.6859 | 1.8922 | 3.0175 | 4.3492 | 258.6659 | 302.9005 | 446.874 | 635.0821 | 0 | 0
|  |  |  | 122 | 1.5987 | 1.7938 | 2.8622 | 4.1258 | 247.3312 | 289.5493 | 427.3925 | 607.4538 | 0 | 0 | 0 | 1.6828 | 1.8882 | 3.0129 | 4.3429 | 260.3487 | 304.7887 | 449.8868 | 639.425 | 0 | 0
|  |  |  | 123 | 1.5958 | 1.7901 | 2.8578 | 4.1198 | 248.927 | 291.3393 | 430.2503 | 611.5736 | 0 | 0 | 0 | 1.6798 | 1.8843 | 3.0082 | 4.3367 | 262.0285 | 306.673 | 452.8951 | 643.7617 | 0 | 0
|  |  |  | 124 | 1.593 | 1.7864 | 2.8535 | 4.1139 | 250.52 | 293.1257 | 433.1038 | 615.6876 | 0 | 0 | 0 | 1.6768 | 1.8804 | 3.0036 | 4.3305 | 263.7053 | 308.5534 | 455.8987 | 648.0922 | 0 | 0
|  |  |  | 125 | 1.5901 | 1.7827 | 2.8491 | 4.1081 | 252.1102 | 294.9085 | 435.9529 | 619.7957 | 0 | 0 | 0 | 1.6738 | 1.8766 | 2.9991 | 4.3243 | 265.3791 | 310.43 | 458.8978 | 652.4165 | 0 | 0
|  |  |  | 126 | 1.5874 | 1.7791 | 2.8449 | 4.1023 | 253.6975 | 296.6876 | 438.7978 | 623.898 | 0 | 0 | 0 | 1.6709 | 1.8728 | 2.9946 | 4.3183 | 267.05 | 312.3028 | 461.8924 | 656.7348 | 0 | 0
|  |  |  | 127 | 1.5846 | 1.7756 | 2.8406 | 4.0966 | 255.2821 | 298.4632 | 441.6384 | 627.9946 | 0 | 0 | 0 | 1.668 | 1.869 | 2.9901 | 4.3122 | 268.718 | 314.1718 | 464.8825 | 661.047 | 0 | 0
|  |  |  | 128 | 1.5819 | 1.772 | 2.8364 | 4.091 | 256.864 | 300.2352 | 444.4748 | 632.0856 | 0 | 0 | 0 | 1.6651 | 1.8653 | 2.9857 | 4.3063 | 270.3832 | 316.037 | 467.8682 | 665.3533 | 0 | 0
|  |  |  | 129 | 1.5792 | 1.7685 | 2.8323 | 4.0853 | 258.4432 | 302.0037 | 447.3071 | 636.171 | 0 | 0 | 0 | 1.6623 | 1.8616 | 2.9813 | 4.3004 | 272.0454 | 317.8986 | 470.8495 | 669.6536 | 0 | 0
|  |  |  | 130 | 1.5765 | 1.765 | 2.8281 | 4.0798 | 260.0196 | 303.7687 | 450.1352 | 640.2507 | 0 | 0 | 0 | 1.6595 | 1.8579 | 2.977 | 4.2945 | 273.7049 | 319.7565 | 473.8265 | 673.9482 | 0 | 0
|  |  |  | 131 | 1.5738 | 1.7616 | 2.8241 | 4.0743 | 261.5935 | 305.5303 | 452.9593 | 644.325 | 0 | 0 | 0 | 1.6567 | 1.8543 | 2.9727 | 4.2887 | 275.3616 | 321.6108 | 476.7992 | 678.2369 | 0 | 0
|  |  |  | 132 | 1.5712 | 1.7582 | 2.82 | 4.0688 | 263.1647 | 307.2884 | 455.7793 | 648.3938 | 0 | 0 | 0 | 1.6539 | 1.8507 | 2.9684 | 4.283 | 277.0155 | 323.4615 | 479.7676 | 682.5198 | 0 | 0
|  |  |  | 133 | 1.5686 | 1.7548 | 2.816 | 4.0634 | 264.7333 | 309.0432 | 458.5953 | 652.4572 | 0 | 0 | 0 | 1.6512 | 1.8471 | 2.9642 | 4.2773 | 278.6666 | 325.3087 | 482.7318 | 686.7971 | 0 | 0
|  |  |  | 134 | 1.566 | 1.7514 | 2.812 | 4.058 | 266.2993 | 310.7947 | 461.4073 | 656.5153 | 0 | 0 | 0 | 1.6484 | 1.8436 | 2.96 | 4.2716 | 280.315 | 327.1523 | 485.6919 | 691.0687 | 0 | 0
|  |  |  | 135 | 1.5635 | 1.7481 | 2.8081 | 4.0527 | 267.8627 | 312.5428 | 464.2154 | 660.568 | 0 | 0 | 0 | 1.6457 | 1.8401 | 2.9559 | 4.266 | 281.9608 | 328.9924 | 488.6477 | 695.3347 | 0 | 0
|  |  |  | 136 | 1.5609 | 1.7448 | 2.8042 | 4.0474 | 269.4237 | 314.2877 | 467.0195 | 664.6154 | 0 | 0 | 0 | 1.6431 | 1.8367 | 2.9518 | 4.2605 | 283.6038 | 330.8291 | 491.5995 | 699.5952 | 0 | 0
|  |  |  | 137 | 1.5584 | 1.7416 | 2.8003 | 4.0422 | 270.9821 | 316.0293 | 469.8198 | 668.6576 | 0 | 0 | 0 | 1.6404 | 1.8333 | 2.9477 | 4.255 | 285.2443 | 332.6624 | 494.5472 | 703.8501 | 0 | 0
|  |  |  | 138 | 1.5559 | 1.7384 | 2.7965 | 4.037 | 272.538 | 317.7676 | 472.6163 | 672.6947 | 0 | 0 | 0 | 1.6378 | 1.8299 | 2.9437 | 4.2495 | 286.8821 | 334.4922 | 497.4909 | 708.0997 | 0 | 0
|  |  |  | 139 | 1.5534 | 1.7352 | 2.7927 | 4.0319 | 274.0914 | 319.5028 | 475.409 | 676.7266 | 0 | 0 | 0 | 1.6352 | 1.8265 | 2.9397 | 4.2441 | 288.5173 | 336.3187 | 500.4305 | 712.3438 | 0 | 0
|  |  |  | 140 | 1.551 | 1.732 | 2.7889 | 4.0268 | 275.6424 | 321.2348 | 478.1979 | 680.7534 | 0 | 0 | 0 | 1.6326 | 1.8232 | 2.9357 | 4.2387 | 290.1499 | 338.1419 | 503.3662 | 716.5825 | 0 | 0
|  |  |  | 141 | 1.5486 | 1.7289 | 2.7852 | 4.0218 | 277.191 | 322.9637 | 480.983 | 684.7751 | 0 | 0 | 0 | 1.6301 | 1.8199 | 2.9317 | 4.2334 | 291.78 | 339.9618 | 506.2979 | 720.8159 | 0 | 0
|  |  |  | 142 | 1.5462 | 1.7258 | 2.7815 | 4.0167 | 278.7371 | 324.6894 | 483.7645 | 688.7919 | 0 | 0 | 0 | 1.6275 | 1.8166 | 2.9278 | 4.2282 | 293.4075 | 341.7784 | 509.2258 | 725.0441 | 0 | 0
|  |  |  | 143 | 1.5438 | 1.7227 | 2.7778 | 4.0118 | 280.2809 | 326.4121 | 486.5423 | 692.8036 | 0 | 0 | 0 | 1.625 | 1.8133 | 2.924 | 4.2229 | 295.0325 | 343.5917 | 512.1498 | 729.267 | 0 | 0
|  |  |  | 144 | 1.5414 | 1.7196 | 2.7741 | 4.0069 | 281.8223 | 328.1317 | 489.3164 | 696.8105 | 0 | 0 | 0 | 1.6225 | 1.8101 | 2.9201 | 4.2177 | 296.6551 | 345.4018 | 515.0699 | 733.4847 | 0 | 0
|  |  |  | 145 | 1.5391 | 1.7166 | 2.7705 | 4.002 | 283.3614 | 329.8483 | 492.0869 | 700.8125 | 0 | 0 | 0 | 1.6201 | 1.8069 | 2.9163 | 4.2126 | 298.2751 | 347.2088 | 517.9862 | 737.6973 | 0 | 0
|  |  |  | 146 | 1.5367 | 1.7136 | 2.7669 | 3.9971 | 284.8981 | 331.5619 | 494.8538 | 704.8096 | 0 | 0 | 0 | 1.6176 | 1.8038 | 2.9126 | 4.2075 | 299.8927 | 349.0126 | 520.8988 | 741.9048 | 0 | 0
|  |  |  | 147 | 1.5344 | 1.7106 | 2.7634 | 3.9923 | 286.4325 | 333.2725 | 497.6172 | 708.8019 | 0 | 0 | 0 | 1.6152 | 1.8006 | 2.9088 | 4.2024 | 301.5079 | 350.8132 | 523.8076 | 746.1073 | 0 | 0
|  |  |  | 148 | 1.5321 | 1.7077 | 2.7598 | 3.9875 | 287.9647 | 334.9802 | 500.3771 | 712.7894 | 0 | 0 | 0 | 1.6128 | 1.7975 | 2.9051 | 4.1974 | 303.1207 | 352.6107 | 526.7127 | 750.3047 | 0 | 0
|  |  |  | 149 | 1.5299 | 1.7047 | 2.7563 | 3.9828 | 289.4946 | 336.6849 | 503.1334 | 716.7722 | 0 | 0 | 0 | 1.6104 | 1.7945 | 2.9014 | 4.1924 | 304.7311 | 354.4052 | 529.6141 | 754.4971 | 0 | 0
|  |  |  | 150 | 1.5276 | 1.7018 | 2.7529 | 3.9781 | 291.0222 | 338.3868 | 505.8863 | 720.7504 | 0 | 0 | 0 | 1.608 | 1.7914 | 2.8978 | 4.1875 | 306.3392 | 356.1966 | 532.5119 | 758.6846 | 0 | 0
|  |  |  | 151 | 1.5254 | 1.699 | 2.7494 | 3.9735 | 292.5476 | 340.0857 | 508.6357 | 724.7238 | 0 | 0 | 0 | 1.6057 | 1.7884 | 2.8941 | 4.1826 | 307.9448 | 357.985 | 535.406 | 762.8672 | 0 | 0
|  |  |  | 152 | 1.5232 | 1.6961 | 2.746 | 3.9688 | 294.0708 | 341.7818 | 511.3817 | 728.6927 | 0 | 0 | 0 | 1.6034 | 1.7854 | 2.8905 | 4.1777 | 309.5482 | 359.7703 | 538.2965 | 767.0449 | 0 | 0
|  |  |  | 153 | 1.521 | 1.6933 | 2.7426 | 3.9643 | 295.5918 | 343.4751 | 514.1243 | 732.6569 | 0 | 0 | 0 | 1.601 | 1.7824 | 2.887 | 4.1729 | 311.1492 | 361.5527 | 541.1835 | 771.2178 | 0 | 0
|  |  |  | 154 | 1.5188 | 1.6905 | 2.7393 | 3.9597 | 297.1106 | 345.1655 | 516.8636 | 736.6166 | 0 | 0 | 0 | 1.5987 | 1.7794 | 2.8834 | 4.1681 | 312.748 | 363.3321 | 544.067 | 775.3859 | 0 | 0
|  |  |  | 155 | 1.5166 | 1.6877 | 2.7359 | 3.9552 | 298.6272 | 346.8532 | 519.5995 | 740.5718 | 0 | 0 | 0 | 1.5965 | 1.7765 | 2.8799 | 4.1634 | 314.3444 | 365.1086 | 546.9469 | 779.5493 | 0 | 0
|  |  |  | 156 | 1.5145 | 1.6849 | 2.7326 | 3.9507 | 300.1417 | 348.5381 | 522.3321 | 744.5225 | 0 | 0 | 0 | 1.5942 | 1.7736 | 2.8764 | 4.1586 | 315.9387 | 366.8822 | 549.8233 | 783.7079 | 0 | 0
|  |  |  | 157 | 1.5124 | 1.6822 | 2.7293 | 3.9463 | 301.6541 | 350.2203 | 525.0615 | 748.4688 | 0 | 0 | 0 | 1.592 | 1.7707 | 2.873 | 4.154 | 317.5306 | 368.6529 | 552.6963 | 787.8619 | 0 | 0
|  |  |  | 158 | 1.5103 | 1.6794 | 2.7261 | 3.9419 | 303.1644 | 351.8997 | 527.7875 | 752.4107 | 0 | 0 | 0 | 1.5898 | 1.7678 | 2.8695 | 4.1493 | 319.1204 | 370.4208 | 555.5658 | 792.0112 | 0 | 0
|  |  |  | 159 | 1.5082 | 1.6768 | 2.7228 | 3.9375 | 304.6725 | 353.5765 | 530.5103 | 756.3482 | 0 | 0 | 0 | 1.5875 | 1.765 | 2.8661 | 4.1447 | 320.7079 | 372.1858 | 558.4319 | 796.1559 | 0 | 0
|  |  |  | 160 | 1.5061 | 1.6741 | 2.7196 | 3.9331 | 306.1786 | 355.2506 | 533.23 | 760.2813 | 0 | 0 | 0 | 1.5854 | 1.7622 | 2.8627 | 4.1401 | 322.2933 | 373.948 | 561.2947 | 800.2961 | 0 | 0
|  |  |  | 161 | 1.504 | 1.6714 | 2.7164 | 3.9288 | 307.6827 | 356.922 | 535.9464 | 764.2101 | 0 | 0 | 0 | 1.5832 | 1.7594 | 2.8594 | 4.1356 | 323.8765 | 375.7073 | 564.1541 | 804.4317 | 0 | 0
|  |  |  | 162 | 1.502 | 1.6688 | 2.7133 | 3.9245 | 309.1846 | 358.5908 | 538.6596 | 768.1346 | 0 | 0 | 0 | 1.581 | 1.7566 | 2.8561 | 4.1311 | 325.4575 | 377.464 | 567.0101 | 808.5628 | 0 | 0
|  |  |  | 163 | 1.4999 | 1.6662 | 2.7101 | 3.9203 | 310.6846 | 360.2569 | 541.3697 | 772.0549 | 0 | 0 | 0 | 1.5789 | 1.7539 | 2.8528 | 4.1266 | 327.0364 | 379.2178 | 569.8629 | 812.6894 | 0 | 0
|  |  |  | 164 | 1.4979 | 1.6636 | 2.707 | 3.9161 | 312.1825 | 361.9205 | 544.0767 | 775.971 | 0 | 0 | 0 | 1.5768 | 1.7511 | 2.8495 | 4.1222 | 328.6132 | 380.969 | 572.7124 | 816.8115 | 0 | 0
|  |  |  | 165 | 1.4959 | 1.661 | 2.7039 | 3.9119 | 313.6785 | 363.5815 | 546.7806 | 779.8828 | 0 | 0 | 0 | 1.5747 | 1.7484 | 2.8462 | 4.1178 | 330.1878 | 382.7174 | 575.5586 | 820.9293 | 0 | 0
|  |  |  | 166 | 1.4939 | 1.6584 | 2.7008 | 3.9077 | 315.1724 | 365.24 | 549.4815 | 783.7905 | 0 | 0 | 0 | 1.5726 | 1.7457 | 2.843 | 4.1134 | 331.7604 | 384.4631 | 578.4015 | 825.0427 | 0 | 0
|  |  |  | 167 | 1.492 | 1.6559 | 2.6978 | 3.9036 | 316.6644 | 366.8959 | 552.1792 | 787.6941 | 0 | 0 | 0 | 1.5705 | 1.7431 | 2.8398 | 4.109 | 333.3309 | 386.2062 | 581.2413 | 829.1517 | 0 | 0
|  |  |  | 168 | 1.49 | 1.6534 | 2.6947 | 3.8995 | 318.1544 | 368.5493 | 554.874 | 791.5936 | 0 | 0 | 0 | 1.5684 | 1.7404 | 2.8366 | 4.1047 | 334.8993 | 387.9466 | 584.0779 | 833.2564 | 0 | 0
|  |  |  | 169 | 1.4881 | 1.6509 | 2.6917 | 3.8954 | 319.6424 | 370.2002 | 557.5657 | 795.489 | 0 | 0 | 0 | 1.5664 | 1.7378 | 2.8334 | 4.1004 | 336.4657 | 389.6844 | 586.9113 | 837.3568 | 0 | 0
|  |  |  | 170 | 1.4861 | 1.6484 | 2.6887 | 3.8914 | 321.1286 | 371.8486 | 560.2545 | 799.3803 | 0 | 0 | 0 | 1.5644 | 1.7352 | 2.8303 | 4.0962 | 338.0301 | 391.4196 | 589.7415 | 841.453 | 0 | 0
|  |  |  | 171 | 1.4842 | 1.646 | 2.6858 | 3.8873 | 322.6128 | 373.4945 | 562.9402 | 803.2677 | 0 | 0 | 0 | 1.5623 | 1.7326 | 2.8271 | 4.0919 | 339.5924 | 393.1522 | 592.5687 | 845.5449 | 0 | 0
|  |  |  | 172 | 1.4823 | 1.6435 | 2.6828 | 3.8833 | 324.0951 | 375.1381 | 565.6231 | 807.151 | 0 | 0 | 0 | 1.5603 | 1.73 | 2.824 | 4.0877 | 341.1528 | 394.8822 | 595.3927 | 849.6326 | 0 | 0
|  |  |  | 173 | 1.4804 | 1.6411 | 2.6799 | 3.8794 | 325.5756 | 376.7791 | 568.303 | 811.0304 | 0 | 0 | 0 | 1.5583 | 1.7275 | 2.821 | 4.0836 | 342.7111 | 396.6096 | 598.2137 | 853.7162 | 0 | 0
|  |  |  | 174 | 1.4786 | 1.6387 | 2.677 | 3.8754 | 327.0541 | 378.4178 | 570.98 | 814.9058 | 0 | 0 | 0 | 1.5564 | 1.7249 | 2.8179 | 4.0794 | 344.2675 | 398.3346 | 601.0315 | 857.7956 | 0 | 0
|  |  |  | 175 | 1.4767 | 1.6363 | 2.6741 | 3.8715 | 328.5308 | 380.0541 | 573.6541 | 818.7774 | 0 | 0 | 0 | 1.5544 | 1.7224 | 2.8149 | 4.0753 | 345.8219 | 400.057 | 603.8464 | 861.8709 | 0 | 0
|  |  |  | 176 | 1.4748 | 1.6339 | 2.6712 | 3.8677 | 330.0056 | 381.688 | 576.3253 | 822.645 | 0 | 0 | 0 | 1.5525 | 1.7199 | 2.8118 | 4.0712 | 347.3744 | 401.7769 | 606.6582 | 865.9421 | 0 | 0
|  |  |  | 177 | 1.473 | 1.6316 | 2.6684 | 3.8638 | 331.4786 | 383.3196 | 578.9937 | 826.5088 | 0 | 0 | 0 | 1.5505 | 1.7174 | 2.8088 | 4.0672 | 348.9249 | 403.4943 | 609.4671 | 870.0093 | 0 | 0
|  |  |  | 178 | 1.4712 | 1.6292 | 2.6656 | 3.86 | 332.9498 | 384.9488 | 581.6593 | 830.3688 | 0 | 0 | 0 | 1.5486 | 1.715 | 2.8059 | 4.0631 | 350.4735 | 405.2093 | 612.273 | 874.0724 | 0 | 0
|  |  |  | 179 | 1.4694 | 1.6269 | 2.6628 | 3.8562 | 334.4192 | 386.5757 | 584.3221 | 834.225 | 0 | 0 | 0 | 1.5467 | 1.7125 | 2.8029 | 4.0591 | 352.0202 | 406.9218 | 615.0759 | 878.1315 | 0 | 0
|  |  |  | 180 | 1.4676 | 1.6246 | 2.66 | 3.8524 | 335.8868 | 388.2003 | 586.982 | 838.0773 | 0 | 0 | 0 | 1.5448 | 1.7101 | 2.8 | 4.0551 | 353.565 | 408.6319 | 617.8758 | 882.1867 | 0 | 0
|  |  |  | 181 | 1.4658 | 1.6223 | 2.6572 | 3.8486 | 337.3525 | 389.8226 | 589.6393 | 841.926 | 0 | 0 | 0 | 1.5429 | 1.7077 | 2.7971 | 4.0512 | 355.1079 | 410.3396 | 620.6729 | 886.2379 | 0 | 0
|  |  |  | 182 | 1.464 | 1.62 | 2.6545 | 3.8449 | 338.8165 | 391.4426 | 592.2937 | 845.7709 | 0 | 0 | 0 | 1.5411 | 1.7053 | 2.7942 | 4.0473 | 356.649 | 412.0448 | 623.4671 | 890.2851 | 0 | 0
|  |  |  | 183 | 1.4622 | 1.6178 | 2.6517 | 3.8412 | 340.2788 | 393.0604 | 594.9454 | 849.6121 | 0 | 0 | 0 | 1.5392 | 1.7029 | 2.7913 | 4.0434 | 358.1882 | 413.7477 | 626.2583 | 894.3285 | 0 | 0
|  |  |  | 184 | 1.4605 | 1.6155 | 2.649 | 3.8375 | 341.7393 | 394.6759 | 597.5944 | 853.4496 | 0 | 0 | 0 | 1.5374 | 1.7005 | 2.7884 | 4.0395 | 359.7255 | 415.4483 | 629.0468 | 898.368 | 0 | 0
|  |  |  | 185 | 1.4587 | 1.6133 | 2.6463 | 3.8338 | 343.198 | 396.2892 | 600.2407 | 857.2834 | 0 | 0 | 0 | 1.5355 | 1.6982 | 2.7856 | 4.0356 | 361.2611 | 417.1465 | 631.8323 | 902.4036 | 0 | 0
|  |  |  | 186 | 1.457 | 1.6111 | 2.6436 | 3.8302 | 344.655 | 397.9002 | 602.8843 | 861.1136 | 0 | 0 | 0 | 1.5337 | 1.6959 | 2.7828 | 4.0318 | 362.7948 | 418.8423 | 634.6151 | 906.4354 | 0 | 0
|  |  |  | 187 | 1.4553 | 1.6089 | 2.6409 | 3.8266 | 346.1103 | 399.5091 | 605.5253 | 864.9402 | 0 | 0 | 0 | 1.5319 | 1.6935 | 2.7799 | 4.028 | 364.3267 | 420.5359 | 637.395 | 910.4634 | 0 | 0
|  |  |  | 188 | 1.4536 | 1.6067 | 2.6383 | 3.823 | 347.5639 | 401.1158 | 608.1636 | 868.7632 | 0 | 0 | 0 | 1.5301 | 1.6912 | 2.7772 | 4.0242 | 365.8568 | 422.2271 | 640.1722 | 914.4876 | 0 | 0
|  |  |  | 189 | 1.4519 | 1.6045 | 2.6357 | 3.8194 | 349.0158 | 402.7203 | 610.7992 | 872.5827 | 0 | 0 | 0 | 1.5283 | 1.689 | 2.7744 | 4.0205 | 367.3851 | 423.9161 | 642.9466 | 918.5081 | 0 | 0
|  |  |  | 190 | 1.4502 | 1.6024 | 2.6331 | 3.8159 | 350.466 | 404.3227 | 613.4323 | 876.3986 | 0 | 0 | 0 | 1.5265 | 1.6867 | 2.7716 | 4.0167 | 368.9116 | 425.6028 | 645.7182 | 922.5248 | 0 | 0
|  |  |  | 191 | 1.4485 | 1.6002 | 2.6305 | 3.8124 | 351.9146 | 405.9229 | 616.0628 | 880.2109 | 0 | 0 | 0 | 1.5248 | 1.6844 | 2.7689 | 4.013 | 370.4364 | 427.2872 | 648.4871 | 926.5378 | 0 | 0
|  |  |  | 192 | 1.4469 | 1.5981 | 2.6279 | 3.8089 | 353.3614 | 407.521 | 618.6906 | 884.0198 | 0 | 0 | 0 | 1.523 | 1.6822 | 2.7662 | 4.0093 | 371.9594 | 428.9694 | 651.2533 | 930.5472 | 0 | 0
|  |  |  | 193 | 1.4452 | 1.596 | 2.6253 | 3.8054 | 354.8067 | 409.117 | 621.3159 | 887.8252 | 0 | 0 | 0 | 1.5213 | 1.68 | 2.7635 | 4.0057 | 373.4807 | 430.6494 | 654.0168 | 934.5528 | 0 | 0
|  |  |  | 194 | 1.4436 | 1.5939 | 2.6228 | 3.8019 | 356.2503 | 410.7108 | 623.9387 | 891.6271 | 0 | 0 | 0 | 1.5196 | 1.6778 | 2.7608 | 4.002 | 375.0003 | 432.3272 | 656.7776 | 938.5549 | 0 | 0
|  |  |  | 195 | 1.442 | 1.5918 | 2.6202 | 3.7985 | 357.6922 | 412.3026 | 626.5589 | 895.4256 | 0 | 0 | 0 | 1.5178 | 1.6756 | 2.7581 | 3.9984 | 376.5181 | 434.0028 | 659.5357 | 942.5533 | 0 | 0
|  |  |  | 196 | 1.4403 | 1.5897 | 2.6177 | 3.7951 | 359.1325 | 413.8923 | 629.1766 | 899.2207 | 0 | 0 | 0 | 1.5161 | 1.6734 | 2.7555 | 3.9948 | 378.0342 | 435.6761 | 662.2912 | 946.5481 | 0 | 0
|  |  |  | 197 | 1.4387 | 1.5877 | 2.6152 | 3.7917 | 360.5713 | 415.48 | 631.7918 | 903.0124 | 0 | 0 | 0 | 1.5144 | 1.6712 | 2.7528 | 3.9912 | 379.5487 | 437.3474 | 665.044 | 950.5393 | 0 | 0
|  |  |  | 198 | 1.4371 | 1.5856 | 2.6127 | 3.7883 | 362.0084 | 417.0656 | 634.4045 | 906.8007 | 0 | 0 | 0 | 1.5128 | 1.6691 | 2.7502 | 3.9877 | 381.0614 | 439.0164 | 667.7942 | 954.527 | 0 | 0
|  |  |  | 199 | 1.4355 | 1.5836 | 2.6102 | 3.7849 | 363.4439 | 418.6492 | 637.0148 | 910.5856 | 0 | 0 | 0 | 1.5111 | 1.6669 | 2.7476 | 3.9842 | 382.5725 | 440.6834 | 670.5419 | 958.5112 | 0 | 0
|  |  |  | 200 | 1.4339 | 1.5816 | 2.6078 | 3.7816 | 364.8778 | 420.2307 | 639.6225 | 914.3672 | 0 | 0 | 0 | 1.5094 | 1.6648 | 2.745 | 3.9806 | 384.0819 | 442.3482 | 673.2869 | 962.4918 | 0 | 0
|  |  |  | 201 | 1.4324 | 1.5795 | 2.6053 | 3.7783 | 366.3102 | 421.8103 | 642.2279 | 918.1455 | 0 | 0 | 0 | 1.5078 | 1.6627 | 2.7425 | 3.9772 | 385.5897 | 444.0108 | 676.0293 | 966.469 | 0 | 0
|  |  |  | 202 | 1.4308 | 1.5776 | 2.6029 | 3.775 | 367.741 | 423.3878 | 644.8308 | 921.9205 | 0 | 0 | 0 | 1.5061 | 1.6606 | 2.7399 | 3.9737 | 387.0958 | 445.6714 | 678.7692 | 970.4427 | 0 | 0
|  |  |  | 203 | 1.4293 | 1.5756 | 2.6005 | 3.7717 | 369.1703 | 424.9634 | 647.4313 | 925.6923 | 0 | 0 | 0 | 1.5045 | 1.6585 | 2.7374 | 3.9702 | 388.6003 | 447.3299 | 681.5066 | 974.4129 | 0 | 0
|  |  |  | 204 | 1.4277 | 1.5736 | 2.5981 | 3.7685 | 370.598 | 426.537 | 650.0293 | 929.4607 | 0 | 0 | 0 | 1.5028 | 1.6564 | 2.7348 | 3.9668 | 390.1031 | 448.9863 | 684.2414 | 978.3797 | 0 | 0
|  |  |  | 205 | 1.4262 | 1.5716 | 2.5957 | 3.7652 | 372.0241 | 428.1087 | 652.625 | 933.2259 | 0 | 0 | 0 | 1.5012 | 1.6544 | 2.7323 | 3.9634 | 391.6044 | 450.6407 | 686.9737 | 982.3431 | 0 | 0
|  |  |  | 206 | 1.4246 | 1.5697 | 2.5933 | 3.762 | 373.4488 | 429.6783 | 655.2184 | 936.9879 | 0 | 0 | 0 | 1.4996 | 1.6523 | 2.7298 | 3.96 | 393.104 | 452.293 | 689.7035 | 986.3031 | 0 | 0
|  |  |  | 207 | 1.4231 | 1.5678 | 2.591 | 3.7588 | 374.8719 | 431.2461 | 657.8093 | 940.7467 | 0 | 0 | 0 | 1.498 | 1.6503 | 2.7273 | 3.9566 | 394.602 | 453.9433 | 692.4309 | 990.2597 | 0 | 0
|  |  |  | 208 | 1.4216 | 1.5658 | 2.5886 | 3.7556 | 376.2935 | 432.8119 | 660.3979 | 944.5023 | 0 | 0 | 0 | 1.4964 | 1.6482 | 2.7249 | 3.9533 | 396.0985 | 455.5915 | 695.1557 | 994.213 | 0 | 0
|  |  |  | 209 | 1.4201 | 1.5639 | 2.5863 | 3.7524 | 377.7137 | 434.3759 | 662.9842 | 948.2548 | 0 | 0 | 0 | 1.4949 | 1.6462 | 2.7224 | 3.9499 | 397.5933 | 457.2377 | 697.8781 | 998.1629 | 0 | 0
|  |  |  | 210 | 1.4186 | 1.562 | 2.584 | 3.7493 | 379.1323 | 435.9379 | 665.5682 | 952.0041 | 0 | 0 | 0 | 1.4933 | 1.6442 | 2.72 | 3.9466 | 399.0866 | 458.882 | 700.5981 | 1002.1096 | 0 | 0
|  |  |  | 211 | 1.4171 | 1.5601 | 2.5817 | 3.7462 | 380.5494 | 437.498 | 668.1498 | 955.7502 | 0 | 0 | 0 | 1.4917 | 1.6422 | 2.7175 | 3.9433 | 400.5784 | 460.5242 | 703.3156 | 1006.0529 | 0 | 0
|  |  |  | 212 | 1.4157 | 1.5583 | 2.5794 | 3.7431 | 381.9651 | 439.0563 | 670.7292 | 959.4933 | 0 | 0 | 0 | 1.4902 | 1.6403 | 2.7151 | 3.9401 | 402.0685 | 462.1645 | 706.0307 | 1009.9929 | 0 | 0
|  |  |  | 213 | 1.4142 | 1.5564 | 2.5771 | 3.74 | 383.3793 | 440.6126 | 673.3063 | 963.2333 | 0 | 0 | 0 | 1.4886 | 1.6383 | 2.7127 | 3.9368 | 403.5572 | 463.8028 | 708.7435 | 1013.9297 | 0 | 0
|  |  |  | 214 | 1.4128 | 1.5545 | 2.5748 | 3.7369 | 384.7921 | 442.1672 | 675.8811 | 966.9701 | 0 | 0 | 0 | 1.4871 | 1.6363 | 2.7103 | 3.9336 | 405.0443 | 465.4391 | 711.4538 | 1017.8633 | 0 | 0
|  |  |  | 215 | 1.4113 | 1.5527 | 2.5726 | 3.7338 | 386.2034 | 443.7199 | 678.4537 | 970.7039 | 0 | 0 | 0 | 1.4856 | 1.6344 | 2.708 | 3.9303 | 406.5299 | 467.0735 | 714.1618 | 1021.7936 | 0 | 0
|  |  |  | 216 | 1.4099 | 1.5508 | 2.5703 | 3.7308 | 387.6132 | 445.2707 | 681.024 | 974.4347 | 0 | 0 | 0 | 1.4841 | 1.6325 | 2.7056 | 3.9271 | 408.0139 | 468.706 | 716.8674 | 1025.7208 | 0 | 0
|  |  |  | 217 | 1.4084 | 1.549 | 2.5681 | 3.7277 | 389.0217 | 446.8197 | 683.5921 | 978.1625 | 0 | 0 | 0 | 1.4826 | 1.6306 | 2.7033 | 3.9239 | 409.4965 | 470.3366 | 719.5706 | 1029.6447 | 0 | 0
|  |  |  | 218 | 1.407 | 1.5472 | 2.5659 | 3.7247 | 390.4287 | 448.3669 | 686.1579 | 981.8872 | 0 | 0 | 0 | 1.4811 | 1.6286 | 2.7009 | 3.9208 | 410.9776 | 471.9652 | 722.2715 | 1033.5655 | 0 | 0
|  |  |  | 219 | 1.4056 | 1.5454 | 2.5637 | 3.7217 | 391.8343 | 449.9123 | 688.7216 | 985.6089 | 0 | 0 | 0 | 1.4796 | 1.6267 | 2.6986 | 3.9176 | 412.4571 | 473.5919 | 724.9701 | 1037.4831 | 0 | 0
|  |  |  | 220 | 1.4042 | 1.5436 | 2.5615 | 3.7188 | 393.2385 | 451.456 | 691.2831 | 989.3277 | 0 | 0 | 0 | 1.4781 | 1.6249 | 2.6963 | 3.9145 | 413.9352 | 475.2168 | 727.6664 | 1041.3975 | 0 | 0
|  |  |  | 221 | 1.4028 | 1.5418 | 2.5593 | 3.7158 | 394.6413 | 452.9978 | 693.8424 | 993.0435 | 0 | 0 | 0 | 1.4766 | 1.623 | 2.694 | 3.9114 | 415.4119 | 476.8398 | 730.3604 | 1045.3089 | 0 | 0
|  |  |  | 222 | 1.4014 | 1.5401 | 2.5571 | 3.7128 | 396.0427 | 454.5379 | 696.3995 | 996.7563 | 0 | 0 | 0 | 1.4752 | 1.6211 | 2.6917 | 3.9083 | 416.887 | 478.4609 | 733.0521 | 1049.2172 | 0 | 0
|  |  |  | 223 | 1.4 | 1.5383 | 2.555 | 3.7099 | 397.4427 | 456.0762 | 698.9544 | 1000.4662 | 0 | 0 | 0 | 1.4737 | 1.6193 | 2.6894 | 3.9052 | 418.3607 | 480.0802 | 735.7415 | 1053.1223 | 0 | 0
|  |  |  | 224 | 1.3986 | 1.5365 | 2.5528 | 3.707 | 398.8413 | 457.6127 | 701.5072 | 1004.1732 | 0 | 0 | 0 | 1.4722 | 1.6174 | 2.6872 | 3.9021 | 419.8329 | 481.6976 | 738.4287 | 1057.0244 | 0 | 0
|  |  |  | 225 | 1.3973 | 1.5348 | 2.5507 | 3.7041 | 400.2386 | 459.1475 | 704.0579 | 1007.8773 | 0 | 0 | 0 | 1.4708 | 1.6156 | 2.6849 | 3.899 | 421.3037 | 483.3132 | 741.1136 | 1060.9235 | 0 | 0
|  |  |  | 226 | 1.3959 | 1.5331 | 2.5486 | 3.7012 | 401.6345 | 460.6806 | 706.6065 | 1011.5785 | 0 | 0 | 0 | 1.4694 | 1.6138 | 2.6827 | 3.896 | 422.7731 | 484.9269 | 743.7963 | 1064.8195 | 0 | 0
|  |  |  | 227 | 1.3945 | 1.5313 | 2.5464 | 3.6983 | 403.029 | 462.2119 | 709.1529 | 1015.2768 | 0 | 0 | 0 | 1.4679 | 1.6119 | 2.6805 | 3.893 | 424.2411 | 486.5389 | 746.4768 | 1068.7124 | 0 | 0
|  |  |  | 228 | 1.3932 | 1.5296 | 2.5443 | 3.6955 | 404.4222 | 463.7415 | 711.6972 | 1018.9723 | 0 | 0 | 0 | 1.4665 | 1.6101 | 2.6782 | 3.89 | 425.7076 | 488.149 | 749.155 | 1072.6024 | 0 | 0
|  |  |  | 229 | 1.3919 | 1.5279 | 2.5422 | 3.6926 | 405.8141 | 465.2695 | 714.2395 | 1022.6649 | 0 | 0 | 0 | 1.4651 | 1.6083 | 2.676 | 3.887 | 427.1727 | 489.7573 | 751.831 | 1076.4894 | 0 | 0
|  |  |  | 230 | 1.3905 | 1.5262 | 2.5402 | 3.6898 | 407.2046 | 466.7957 | 716.7797 | 1026.3547 | 0 | 0 | 0 | 1.4637 | 1.6066 | 2.6739 | 3.884 | 428.6364 | 491.3639 | 754.5049 | 1080.3734 | 0 | 0
|  |  |  | 231 | 1.3892 | 1.5245 | 2.5381 | 3.687 | 408.5938 | 468.3203 | 719.3178 | 1030.0417 | 0 | 0 | 0 | 1.4623 | 1.6048 | 2.6717 | 3.881 | 430.0987 | 492.9687 | 757.1766 | 1084.2545 | 0 | 0
|  |  |  | 232 | 1.3879 | 1.5229 | 2.536 | 3.6842 | 409.9816 | 469.8431 | 721.8538 | 1033.7259 | 0 | 0 | 0 | 1.4609 | 1.603 | 2.6695 | 3.8781 | 431.5596 | 494.5717 | 759.8461 | 1088.1326 | 0 | 0
|  |  |  | 233 | 1.3866 | 1.5212 | 2.534 | 3.6814 | 411.3682 | 471.3643 | 724.3878 | 1037.4074 | 0 | 0 | 0 | 1.4595 | 1.6013 | 2.6674 | 3.8752 | 433.0192 | 496.173 | 762.5135 | 1092.0077 | 0 | 0
|  |  |  | 234 | 1.3853 | 1.5195 | 2.532 | 3.6786 | 412.7535 | 472.8839 | 726.9197 | 1041.086 | 0 | 0 | 0 | 1.4582 | 1.5995 | 2.6652 | 3.8723 | 434.4773 | 497.7725 | 765.1787 | 1095.88 | 0 | 0
|  |  |  | 235 | 1.384 | 1.5179 | 2.5299 | 3.6759 | 414.1374 | 474.4018 | 729.4497 | 1044.7619 | 0 | 0 | 0 | 1.4568 | 1.5978 | 2.6631 | 3.8694 | 435.9341 | 499.3703 | 767.8417 | 1099.7494 | 0 | 0
|  |  |  | 236 | 1.3827 | 1.5163 | 2.5279 | 3.6731 | 415.5201 | 475.918 | 731.9776 | 1048.435 | 0 | 0 | 0 | 1.4554 | 1.5961 | 2.661 | 3.8665 | 437.3896 | 500.9663 | 770.5027 | 1103.6158 | 0 | 0
|  |  |  | 237 | 1.3814 | 1.5146 | 2.5259 | 3.6704 | 416.9015 | 477.4326 | 734.5035 | 1052.1055 | 0 | 0 | 0 | 1.4541 | 1.5943 | 2.6588 | 3.8636 | 438.8436 | 502.5607 | 773.1615 | 1107.4794 | 0 | 0
|  |  |  | 238 | 1.3801 | 1.513 | 2.5239 | 3.6677 | 418.2816 | 478.9456 | 737.0274 | 1055.7732 | 0 | 0 | 0 | 1.4527 | 1.5926 | 2.6567 | 3.8607 | 440.2964 | 504.1533 | 775.8183 | 1111.3402 | 0 | 0
|  |  |  | 239 | 1.3788 | 1.5114 | 2.5219 | 3.665 | 419.6604 | 480.457 | 739.5493 | 1059.4382 | 0 | 0 | 0 | 1.4514 | 1.5909 | 2.6546 | 3.8579 | 441.7478 | 505.7442 | 778.4729 | 1115.1981 | 0 | 0
|  |  |  | 240 | 1.3776 | 1.5098 | 2.5199 | 3.6623 | 421.038 | 481.9668 | 742.0692 | 1063.1005 | 0 | 0 | 0 | 1.4501 | 1.5892 | 2.6526 | 3.8551 | 443.1979 | 507.3334 | 781.1255 | 1119.0531 | 0 | 0
|  |  |  | 241 | 1.3763 | 1.5082 | 2.518 | 3.6596 | 422.4143 | 483.4749 | 744.5872 | 1066.7601 | 0 | 0 | 0 | 1.4487 | 1.5876 | 2.6505 | 3.8523 | 444.6466 | 508.921 | 783.776 | 1122.9054 | 0 | 0
|  |  |  | 242 | 1.375 | 1.5066 | 2.516 | 3.657 | 423.7893 | 484.9815 | 747.1032 | 1070.4171 | 0 | 0 | 0 | 1.4474 | 1.5859 | 2.6484 | 3.8495 | 446.094 | 510.5069 | 786.4244 | 1126.7548 | 0 | 0
|  |  |  | 243 | 1.3738 | 1.505 | 2.5141 | 3.6543 | 425.1631 | 486.4865 | 749.6173 | 1074.0714 | 0 | 0 | 0 | 1.4461 | 1.5842 | 2.6464 | 3.8467 | 447.5401 | 512.0911 | 789.0708 | 1130.6015 | 0 | 0
|  |  |  | 244 | 1.3726 | 1.5034 | 2.5121 | 3.6517 | 426.5357 | 487.99 | 752.1294 | 1077.7231 | 0 | 0 | 0 | 1.4448 | 1.5826 | 2.6443 | 3.8439 | 448.9849 | 513.6736 | 791.7152 | 1134.4454 | 0 | 0
|  |  |  | 245 | 1.3713 | 1.5019 | 2.5102 | 3.6491 | 427.907 | 489.4918 | 754.6396 | 1081.3722 | 0 | 0 | 0 | 1.4435 | 1.5809 | 2.6423 | 3.8411 | 450.4284 | 515.2546 | 794.3575 | 1138.2865 | 0 | 0
|  |  |  | 246 | 1.3701 | 1.5003 | 2.5083 | 3.6465 | 429.2771 | 490.9921 | 757.1479 | 1085.0186 | 0 | 0 | 0 | 1.4422 | 1.5793 | 2.6403 | 3.8384 | 451.8706 | 516.8338 | 796.9978 | 1142.1249 | 0 | 0
|  |  |  | 247 | 1.3689 | 1.4988 | 2.5064 | 3.6439 | 430.646 | 492.4909 | 759.6542 | 1088.6625 | 0 | 0 | 0 | 1.4409 | 1.5776 | 2.6383 | 3.8356 | 453.3116 | 518.4115 | 799.636 | 1145.9605 | 0 | 0
|  |  |  | 248 | 1.3677 | 1.4972 | 2.5045 | 3.6413 | 432.0136 | 493.9881 | 762.1587 | 1092.3038 | 0 | 0 | 0 | 1.4396 | 1.576 | 2.6363 | 3.8329 | 454.7512 | 519.9875 | 802.2723 | 1149.7935 | 0 | 0
|  |  |  | 249 | 1.3665 | 1.4957 | 2.5026 | 3.6387 | 433.3801 | 495.4838 | 764.6613 | 1095.9425 | 0 | 0 | 0 | 1.4384 | 1.5744 | 2.6343 | 3.8302 | 456.1896 | 521.5619 | 804.9066 | 1153.6237 | 0 | 0
|  |  |  | 250 | 1.3652 | 1.4942 | 2.5007 | 3.6361 | 434.7453 | 496.9779 | 767.162 | 1099.5786 | 0 | 0 | 0 | 1.4371 | 1.5728 | 2.6323 | 3.8275 | 457.6267 | 523.1347 | 807.5389 | 1157.4512 | 0 | 0
|  |  |  | 251 | 1.364 | 1.4926 | 2.4988 | 3.6336 | 436.1094 | 498.4706 | 769.6608 | 1103.2122 | 0 | 0 | 0 | 1.4358 | 1.5712 | 2.6303 | 3.8248 | 459.0625 | 524.7059 | 810.1693 | 1161.276 | 0 | 0
|  |  |  | 252 | 1.3629 | 1.4911 | 2.497 | 3.6311 | 437.4722 | 499.9617 | 772.1578 | 1106.8433 | 0 | 0 | 0 | 1.4346 | 1.5696 | 2.6284 | 3.8222 | 460.4971 | 526.2755 | 812.7976 | 1165.0982 | 0 | 0
|  |  |  | 253 | 1.3617 | 1.4896 | 2.4951 | 3.6285 | 438.8339 | 501.4513 | 774.6529 | 1110.4718 | 0 | 0 | 0 | 1.4333 | 1.568 | 2.6264 | 3.8195 | 461.9304 | 527.8435 | 815.4241 | 1168.9177 | 0 | 0
|  |  |  | 254 | 1.3605 | 1.4881 | 2.4933 | 3.626 | 440.1944 | 502.9394 | 777.1461 | 1114.0978 | 0 | 0 | 0 | 1.4321 | 1.5664 | 2.6245 | 3.8169 | 463.3625 | 529.4099 | 818.0485 | 1172.7346 | 0 | 0
|  |  |  | 255 | 1.3593 | 1.4866 | 2.4914 | 3.6235 | 441.5537 | 504.4261 | 779.6375 | 1117.7214 | 0 | 0 | 0 | 1.4309 | 1.5649 | 2.6225 | 3.8142 | 464.7934 | 530.9748 | 820.6711 | 1176.5488 | 0 | 0
|  |  |  | 256 | 1.3581 | 1.4852 | 2.4896 | 3.621 | 442.9119 | 505.9112 | 782.1271 | 1121.3424 | 0 | 0 | 0 | 1.4296 | 1.5633 | 2.6206 | 3.8116 | 466.223 | 532.5381 | 823.2917 | 1180.3604 | 0 | 0
|  |  |  | 257 | 1.357 | 1.4837 | 2.4878 | 3.6185 | 444.2688 | 507.3949 | 784.6149 | 1124.9609 | 0 | 0 | 0 | 1.4284 | 1.5618 | 2.6187 | 3.809 | 467.6514 | 534.0999 | 825.9104 | 1184.1694 | 0 | 0
|  |  |  | 258 | 1.3558 | 1.4822 | 2.486 | 3.6161 | 445.6246 | 508.8771 | 787.1008 | 1128.577 | 0 | 0 | 0 | 1.4272 | 1.5602 | 2.6168 | 3.8064 | 469.0786 | 535.6601 | 828.5272 | 1187.9758 | 0 | 0
|  |  |  | 259 | 1.3547 | 1.4807 | 2.4841 | 3.6136 | 446.9793 | 510.3578 | 789.585 | 1132.1906 | 0 | 0 | 0 | 1.426 | 1.5587 | 2.6149 | 3.8038 | 470.5045 | 537.2188 | 831.1421 | 1191.7796 | 0 | 0
|  |  |  | 260 | 1.3535 | 1.4793 | 2.4823 | 3.6112 | 448.3328 | 511.8371 | 792.0673 | 1135.8018 | 0 | 0 | 0 | 1.4248 | 1.5572 | 2.613 | 3.8012 | 471.9293 | 538.7759 | 833.7551 | 1195.5809 | 0 | 0
|  |  |  | 261 | 1.3524 | 1.4778 | 2.4806 | 3.6087 | 449.6852 | 513.315 | 794.5479 | 1139.4106 | 0 | 0 | 0 | 1.4236 | 1.5556 | 2.6111 | 3.7987 | 473.3528 | 540.3316 | 836.3662 | 1199.3796 | 0 | 0
|  |  |  | 262 | 1.3512 | 1.4764 | 2.4788 | 3.6063 | 451.0364 | 514.7914 | 797.0267 | 1143.0169 | 0 | 0 | 0 | 1.4224 | 1.5541 | 2.6092 | 3.7961 | 474.7752 | 541.8857 | 838.9754 | 1203.1757 | 0 | 0
|  |  |  | 263 | 1.3501 | 1.475 | 2.477 | 3.6039 | 452.3865 | 516.2664 | 799.5037 | 1146.6208 | 0 | 0 | 0 | 1.4212 | 1.5526 | 2.6074 | 3.7936 | 476.1964 | 543.4383 | 841.5828 | 1206.9693 | 0 | 0
|  |  |  | 264 | 1.349 | 1.4736 | 2.4752 | 3.6015 | 453.7355 | 517.7399 | 801.9789 | 1150.2223 | 0 | 0 | 0 | 1.42 | 1.5511 | 2.6055 | 3.7911 | 477.6163 | 544.9894 | 844.1883 | 1210.7603 | 0 | 0
|  |  |  | 265 | 1.3479 | 1.4721 | 2.4735 | 3.5991 | 455.0834 | 519.2121 | 804.4524 | 1153.8215 | 0 | 0 | 0 | 1.4188 | 1.5496 | 2.6037 | 3.7886 | 479.0351 | 546.539 | 846.792 | 1214.5489 | 0 | 0
|  |  |  | 266 | 1.3467 | 1.4707 | 2.4717 | 3.5967 | 456.4301 | 520.6828 | 806.9242 | 1157.4182 | 0 | 0 | 0 | 1.4176 | 1.5481 | 2.6018 | 3.786 | 480.4528 | 548.0871 | 849.3939 | 1218.3349 | 0 | 0
|  |  |  | 267 | 1.3456 | 1.4693 | 2.47 | 3.5944 | 457.7758 | 522.1521 | 809.3942 | 1161.0126 | 0 | 0 | 0 | 1.4165 | 1.5466 | 2.6 | 3.7836 | 481.8692 | 549.6338 | 851.9939 | 1222.1185 | 0 | 0
|  |  |  | 268 | 1.3445 | 1.4679 | 2.4683 | 3.592 | 459.1203 | 523.62 | 811.8624 | 1164.6046 | 0 | 0 | 0 | 1.4153 | 1.5452 | 2.5982 | 3.7811 | 483.2845 | 551.179 | 854.592 | 1225.8996 | 0 | 0
|  |  |  | 269 | 1.3434 | 1.4665 | 2.4665 | 3.5897 | 460.4637 | 525.0865 | 814.329 | 1168.1943 | 0 | 0 | 0 | 1.4141 | 1.5437 | 2.5964 | 3.7786 | 484.6986 | 552.7227 | 857.1884 | 1229.6782 | 0 | 0
|  |  |  | 270 | 1.3423 | 1.4651 | 2.4648 | 3.5873 | 461.806 | 526.5517 | 816.7938 | 1171.7816 | 0 | 0 | 0 | 1.413 | 1.5423 | 2.5946 | 3.7761 | 486.1116 | 554.2649 | 859.783 | 1233.4543 | 0 | 0
|  |  |  | 271 | 1.3412 | 1.4638 | 2.4631 | 3.585 | 463.1473 | 528.0154 | 819.2569 | 1175.3666 | 0 | 0 | 0 | 1.4118 | 1.5408 | 2.5928 | 3.7737 | 487.5234 | 555.8057 | 862.3757 | 1237.228 | 0 | 0
|  |  |  | 272 | 1.3401 | 1.4624 | 2.4614 | 3.5827 | 464.4874 | 529.4778 | 821.7183 | 1178.9493 | 0 | 0 | 0 | 1.4107 | 1.5394 | 2.591 | 3.7712 | 488.9341 | 557.3451 | 864.9667 | 1240.9992 | 0 | 0
|  |  |  | 273 | 1.3391 | 1.461 | 2.4597 | 3.5804 | 465.8265 | 530.9388 | 824.1781 | 1182.5297 | 0 | 0 | 0 | 1.4095 | 1.5379 | 2.5892 | 3.7688 | 490.3437 | 558.883 | 867.5559 | 1244.7681 | 0 | 0
|  |  |  | 274 | 1.338 | 1.4597 | 2.458 | 3.5781 | 467.1645 | 532.3985 | 826.6361 | 1186.1077 | 0 | 0 | 0 | 1.4084 | 1.5365 | 2.5874 | 3.7664 | 491.7521 | 560.4195 | 870.1433 | 1248.5345 | 0 | 0
|  |  |  | 275 | 1.3369 | 1.4583 | 2.4564 | 3.5758 | 468.5014 | 533.8568 | 829.0925 | 1189.6835 | 0 | 0 | 0 | 1.4073 | 1.5351 | 2.5856 | 3.764 | 493.1593 | 561.9545 | 872.7289 | 1252.2984 | 0 | 0
|  |  |  | 276 | 1.3359 | 1.457 | 2.4547 | 3.5735 | 469.8372 | 535.3138 | 831.5471 | 1193.257 | 0 | 0 | 0 | 1.4062 | 1.5336 | 2.5839 | 3.7616 | 494.5655 | 563.4882 | 875.3128 | 1256.06 | 0 | 0
|  |  |  | 277 | 1.3348 | 1.4556 | 2.453 | 3.5712 | 471.172 | 536.7694 | 834.0002 | 1196.8283 | 0 | 0 | 0 | 1.405 | 1.5322 | 2.5821 | 3.7592 | 495.9705 | 565.0204 | 877.8949 | 1259.8193 | 0 | 0
|  |  |  | 278 | 1.3337 | 1.4543 | 2.4514 | 3.569 | 472.5057 | 538.2237 | 836.4515 | 1200.3973 | 0 | 0 | 0 | 1.4039 | 1.5308 | 2.5804 | 3.7568 | 497.3745 | 566.5512 | 880.4753 | 1263.5761 | 0 | 0
|  |  |  | 279 | 1.3327 | 1.453 | 2.4497 | 3.5667 | 473.8384 | 539.6766 | 838.9012 | 1203.964 | 0 | 0 | 0 | 1.4028 | 1.5294 | 2.5786 | 3.7545 | 498.7773 | 568.0807 | 883.0539 | 1267.3305 | 0 | 0
|  |  |  | 280 | 1.3316 | 1.4516 | 2.4481 | 3.5645 | 475.17 | 541.1283 | 841.3493 | 1207.5285 | 0 | 0 | 0 | 1.4017 | 1.528 | 2.5769 | 3.7521 | 500.179 | 569.6087 | 885.6308 | 1271.0827 | 0 | 0
|  |  |  | 281 | 1.3306 | 1.4503 | 2.4464 | 3.5623 | 476.5006 | 542.5786 | 843.7957 | 1211.0908 | 0 | 0 | 0 | 1.4006 | 1.5266 | 2.5752 | 3.7498 | 501.5796 | 571.1353 | 888.206 | 1274.8324 | 0 | 0
|  |  |  | 282 | 1.3295 | 1.449 | 2.4448 | 3.5601 | 477.8302 | 544.0276 | 846.2405 | 1214.6508 | 0 | 0 | 0 | 1.3995 | 1.5253 | 2.5735 | 3.7474 | 502.9791 | 572.6606 | 890.7795 | 1278.5798 | 0 | 0
|  |  |  | 283 | 1.3285 | 1.4477 | 2.4432 | 3.5578 | 479.1587 | 545.4752 | 848.6837 | 1218.2087 | 0 | 0 | 0 | 1.3984 | 1.5239 | 2.5718 | 3.7451 | 504.3776 | 574.1845 | 893.3512 | 1282.3249 | 0 | 0
|  |  |  | 284 | 1.3275 | 1.4464 | 2.4416 | 3.5556 | 480.4862 | 546.9216 | 851.1252 | 1221.7643 | 0 | 0 | 0 | 1.3973 | 1.5225 | 2.5701 | 3.7428 | 505.7749 | 575.707 | 895.9213 | 1286.0677 | 0 | 0
|  |  |  | 285 | 1.3265 | 1.4451 | 2.4399 | 3.5534 | 481.8126 | 548.3667 | 853.5652 | 1225.3178 | 0 | 0 | 0 | 1.3963 | 1.5212 | 2.5684 | 3.7405 | 507.1712 | 577.2281 | 898.4897 | 1289.8082 | 0 | 0
|  |  |  | 286 | 1.3254 | 1.4438 | 2.4383 | 3.5513 | 483.1381 | 549.8105 | 856.0035 | 1228.869 | 0 | 0 | 0 | 1.3952 | 1.5198 | 2.5667 | 3.7382 | 508.5664 | 578.7479 | 901.0564 | 1293.5463 | 0 | 0
|  |  |  | 287 | 1.3244 | 1.4425 | 2.4368 | 3.5491 | 484.4625 | 551.2531 | 858.4403 | 1232.4181 | 0 | 0 | 0 | 1.3941 | 1.5184 | 2.565 | 3.7359 | 509.9605 | 580.2664 | 903.6214 | 1297.2822 | 0 | 0
|  |  |  | 288 | 1.3234 | 1.4412 | 2.4352 | 3.5469 | 485.7859 | 552.6943 | 860.8755 | 1235.965 | 0 | 0 | 0 | 1.3931 | 1.5171 | 2.5633 | 3.7336 | 511.3535 | 581.7835 | 906.1847 | 1301.0158 | 0 | 0
|  |  |  | 289 | 1.3224 | 1.44 | 2.4336 | 3.5448 | 487.1083 | 554.1343 | 863.309 | 1239.5098 | 0 | 0 | 0 | 1.392 | 1.5158 | 2.5617 | 3.7313 | 512.7455 | 583.2992 | 908.7463 | 1304.7472 | 0 | 0
|  |  |  | 290 | 1.3214 | 1.4387 | 2.432 | 3.5426 | 488.4296 | 555.573 | 865.741 | 1243.0524 | 0 | 0 | 0 | 1.3909 | 1.5144 | 2.56 | 3.7291 | 514.1365 | 584.8137 | 911.3064 | 1308.4762 | 0 | 0
|  |  |  | 291 | 1.3204 | 1.4374 | 2.4304 | 3.5405 | 489.75 | 557.0104 | 868.1715 | 1246.5929 | 0 | 0 | 0 | 1.3899 | 1.5131 | 2.5583 | 3.7268 | 515.5264 | 586.3268 | 913.8647 | 1312.203 | 0 | 0
|  |  |  | 292 | 1.3194 | 1.4362 | 2.4289 | 3.5383 | 491.0694 | 558.4466 | 870.6003 | 1250.1312 | 0 | 0 | 0 | 1.3888 | 1.5118 | 2.5567 | 3.7246 | 516.9152 | 587.8386 | 916.4214 | 1315.9276 | 0 | 0
|  |  |  | 293 | 1.3184 | 1.4349 | 2.4273 | 3.5362 | 492.3878 | 559.8816 | 873.0276 | 1253.6675 | 0 | 0 | 0 | 1.3878 | 1.5105 | 2.5551 | 3.7223 | 518.303 | 589.349 | 918.9765 | 1319.65 | 0 | 0
|  |  |  | 294 | 1.3174 | 1.4337 | 2.4258 | 3.5341 | 493.7052 | 561.3153 | 875.4534 | 1257.2016 | 0 | 0 | 0 | 1.3867 | 1.5092 | 2.5534 | 3.7201 | 519.6897 | 590.8582 | 921.5299 | 1323.3701 | 0 | 0
|  |  |  | 295 | 1.3164 | 1.4325 | 2.4242 | 3.532 | 495.0217 | 562.7477 | 877.8776 | 1260.7336 | 0 | 0 | 0 | 1.3857 | 1.5078 | 2.5518 | 3.7179 | 521.0754 | 592.366 | 924.0817 | 1327.088 | 0 | 0
|  |  |  | 296 | 1.3154 | 1.4312 | 2.4227 | 3.5299 | 496.3371 | 564.1789 | 880.3003 | 1264.2635 | 0 | 0 | 0 | 1.3847 | 1.5065 | 2.5502 | 3.7157 | 522.4601 | 593.8726 | 926.6319 | 1330.8037 | 0 | 0
|  |  |  | 297 | 1.3145 | 1.43 | 2.4211 | 3.5278 | 497.6516 | 565.6089 | 882.7214 | 1267.7913 | 0 | 0 | 0 | 1.3837 | 1.5053 | 2.5486 | 3.7135 | 523.8438 | 595.3778 | 929.1805 | 1334.5172 | 0 | 0
|  |  |  | 298 | 1.3135 | 1.4288 | 2.4196 | 3.5257 | 498.9651 | 567.0377 | 885.1411 | 1271.3171 | 0 | 0 | 0 | 1.3826 | 1.504 | 2.547 | 3.7113 | 525.2264 | 596.8818 | 931.7274 | 1338.2285 | 0 | 0
|  |  |  | 299 | 1.3125 | 1.4275 | 2.4181 | 3.5237 | 500.2776 | 568.4652 | 887.5592 | 1274.8407 | 0 | 0 | 0 | 1.3816 | 1.5027 | 2.5454 | 3.7091 | 526.608 | 598.3845 | 934.2728 | 1341.9376 | 0 | 0
|  |  |  | 300 | 1.3116 | 1.4263 | 2.4166 | 3.5216 | 501.5892 | 569.8916 | 889.9758 | 1278.3623 | 0 | 0 | 0 | 1.3806 | 1.5014 | 2.5438 | 3.707 | 527.9886 | 599.8859 | 936.8166 | 1345.6446 | 0 | 0
|  |  |  | 301 | 1.3106 | 1.4251 | 2.4151 | 3.5196 | 502.8998 | 571.3167 | 892.3908 | 1281.8819 | 0 | 0 | 0 | 1.3796 | 1.5001 | 2.5422 | 3.7048 | 529.3682 | 601.386 | 939.3588 | 1349.3493 | 0 | 0
|  |  |  | 302 | 1.3097 | 1.4239 | 2.4136 | 3.5175 | 504.2095 | 572.7406 | 894.8044 | 1285.3994 | 0 | 0 | 0 | 1.3786 | 1.4989 | 2.5406 | 3.7026 | 530.7468 | 602.8849 | 941.8994 | 1353.052 | 0 | 0
|  |  |  | 303 | 1.3087 | 1.4227 | 2.4121 | 3.5155 | 505.5182 | 574.1633 | 897.2165 | 1288.9148 | 0 | 0 | 0 | 1.3776 | 1.4976 | 2.539 | 3.7005 | 532.1244 | 604.3825 | 944.4384 | 1356.7525 | 0 | 0
|  |  |  | 304 | 1.3078 | 1.4215 | 2.4106 | 3.5134 | 506.8259 | 575.5849 | 899.6271 | 1292.4283 | 0 | 0 | 0 | 1.3766 | 1.4963 | 2.5375 | 3.6983 | 533.501 | 605.8788 | 946.9759 | 1360.4508 | 0 | 0
|  |  |  | 305 | 1.3068 | 1.4203 | 2.4091 | 3.5114 | 508.1327 | 577.0052 | 902.0362 | 1295.9397 | 0 | 0 | 0 | 1.3756 | 1.4951 | 2.5359 | 3.6962 | 534.8765 | 607.3739 | 949.5118 | 1364.147 | 0 | 0
|  |  |  | 306 | 1.3059 | 1.4192 | 2.4076 | 3.5094 | 509.4386 | 578.4244 | 904.4438 | 1299.4491 | 0 | 0 | 0 | 1.3746 | 1.4938 | 2.5343 | 3.6941 | 536.2511 | 608.8678 | 952.0461 | 1367.8411 | 0 | 0
|  |  |  | 307 | 1.3049 | 1.418 | 2.4062 | 3.5074 | 510.7435 | 579.8424 | 906.85 | 1302.9565 | 0 | 0 | 0 | 1.3736 | 1.4926 | 2.5328 | 3.692 | 537.6247 | 610.3604 | 954.5789 | 1371.5331 | 0 | 0
|  |  |  | 308 | 1.304 | 1.4168 | 2.4047 | 3.5054 | 512.0475 | 581.2592 | 909.2547 | 1306.4618 | 0 | 0 | 0 | 1.3726 | 1.4914 | 2.5313 | 3.6899 | 538.9974 | 611.8517 | 957.1102 | 1375.223 | 0 | 0
|  |  |  | 309 | 1.3031 | 1.4156 | 2.4032 | 3.5034 | 513.3506 | 582.6748 | 911.6579 | 1309.9652 | 0 | 0 | 0 | 1.3717 | 1.4901 | 2.5297 | 3.6878 | 540.369 | 613.3419 | 959.6399 | 1378.9108 | 0 | 0
|  |  |  | 310 | 1.3021 | 1.4145 | 2.4018 | 3.5014 | 514.6527 | 584.0893 | 914.0597 | 1313.4666 | 0 | 0 | 0 | 1.3707 | 1.4889 | 2.5282 | 3.6857 | 541.7397 | 614.8308 | 962.1681 | 1382.5965 | 0 | 0
|  |  |  | 311 | 1.3012 | 1.4133 | 2.4003 | 3.4994 | 515.9539 | 585.5026 | 916.46 | 1316.9661 | 0 | 0 | 0 | 1.3697 | 1.4877 | 2.5267 | 3.6836 | 543.1094 | 616.3185 | 964.6947 | 1386.2801 | 0 | 0
|  |  |  | 312 | 1.3003 | 1.4122 | 2.3989 | 3.4975 | 517.2542 | 586.9147 | 918.8589 | 1320.4635 | 0 | 0 | 0 | 1.3687 | 1.4865 | 2.5251 | 3.6815 | 544.4781 | 617.805 | 967.2199 | 1389.9616 | 0 | 0
|  |  |  | 313 | 1.2994 | 1.411 | 2.3974 | 3.4955 | 518.5536 | 588.3257 | 921.2563 | 1323.959 | 0 | 0 | 0 | 1.3678 | 1.4853 | 2.5236 | 3.6795 | 545.8459 | 619.2902 | 969.7435 | 1393.6411 | 0 | 0
|  |  |  | 314 | 1.2985 | 1.4099 | 2.396 | 3.4935 | 519.8521 | 589.7356 | 923.6523 | 1327.4526 | 0 | 0 | 0 | 1.3668 | 1.4841 | 2.5221 | 3.6774 | 547.2127 | 620.7743 | 972.2656 | 1397.3185 | 0 | 0
|  |  |  | 315 | 1.2976 | 1.4087 | 2.3946 | 3.4916 | 521.1497 | 591.1443 | 926.0469 | 1330.9442 | 0 | 0 | 0 | 1.3659 | 1.4829 | 2.5206 | 3.6754 | 548.5786 | 622.2571 | 974.7862 | 1400.9939 | 0 | 0
|  |  |  | 316 | 1.2967 | 1.4076 | 2.3932 | 3.4897 | 522.4463 | 592.5519 | 928.4401 | 1334.4338 | 0 | 0 | 0 | 1.3649 | 1.4817 | 2.5191 | 3.6733 | 549.9435 | 623.7388 | 977.3053 | 1404.6672 | 0 | 0
|  |  |  | 317 | 1.2958 | 1.4064 | 2.3917 | 3.4877 | 523.7421 | 593.9583 | 930.8318 | 1337.9215 | 0 | 0 | 0 | 1.364 | 1.4805 | 2.5176 | 3.6713 | 551.3075 | 625.2193 | 979.823 | 1408.3385 | 0 | 0
|  |  |  | 318 | 1.2949 | 1.4053 | 2.3903 | 3.4858 | 525.0369 | 595.3636 | 933.2221 | 1341.4073 | 0 | 0 | 0 | 1.363 | 1.4793 | 2.5161 | 3.6693 | 552.6705 | 626.6985 | 982.3391 | 1412.0077 | 0 | 0
|  |  |  | 319 | 1.294 | 1.4042 | 2.3889 | 3.4839 | 526.3309 | 596.7678 | 935.6111 | 1344.8912 | 0 | 0 | 0 | 1.3621 | 1.4781 | 2.5147 | 3.6672 | 554.0325 | 628.1766 | 984.8538 | 1415.675 | 0 | 0
|  |  |  | 320 | 1.2931 | 1.4031 | 2.3875 | 3.482 | 527.624 | 598.1709 | 937.9986 | 1348.3732 | 0 | 0 | 0 | 1.3611 | 1.4769 | 2.5132 | 3.6652 | 555.3937 | 629.6536 | 987.3669 | 1419.3402 | 0 | 0
|  |  |  | 321 | 1.2922 | 1.402 | 2.3861 | 3.4801 | 528.9162 | 599.5728 | 940.3847 | 1351.8532 | 0 | 0 | 0 | 1.3602 | 1.4757 | 2.5117 | 3.6632 | 556.7539 | 631.1293 | 989.8786 | 1423.0034 | 0 | 0
|  |  |  | 322 | 1.2913 | 1.4008 | 2.3847 | 3.4782 | 530.2075 | 600.9737 | 942.7694 | 1355.3314 | 0 | 0 | 0 | 1.3593 | 1.4746 | 2.5102 | 3.6612 | 558.1132 | 632.6039 | 992.3889 | 1426.6646 | 0 | 0
|  |  |  | 323 | 1.2904 | 1.3997 | 2.3833 | 3.4763 | 531.4979 | 602.3734 | 945.1528 | 1358.8077 | 0 | 0 | 0 | 1.3583 | 1.4734 | 2.5088 | 3.6592 | 559.4715 | 634.0773 | 994.8977 | 1430.3239 | 0 | 0
|  |  |  | 324 | 1.2895 | 1.3986 | 2.382 | 3.4744 | 532.7875 | 603.7721 | 947.5348 | 1362.2821 | 0 | 0 | 0 | 1.3574 | 1.4723 | 2.5073 | 3.6573 | 560.8289 | 635.5496 | 997.405 | 1433.9811 | 0 | 0
|  |  |  | 325 | 1.2887 | 1.3975 | 2.3806 | 3.4725 | 534.0761 | 605.1696 | 949.9154 | 1365.7546 | 0 | 0 | 0 | 1.3565 | 1.4711 | 2.5059 | 3.6553 | 562.1854 | 637.0206 | 999.9109 | 1437.6364 | 0 | 0
|  |  |  | 326 | 1.2878 | 1.3964 | 2.3792 | 3.4706 | 535.3639 | 606.5661 | 952.2946 | 1369.2252 | 0 | 0 | 0 | 1.3556 | 1.4699 | 2.5044 | 3.6533 | 563.541 | 638.4906 | 1002.4153 | 1441.2897 | 0 | 0
|  |  |  | 327 | 1.2869 | 1.3954 | 2.3779 | 3.4688 | 536.6509 | 607.9614 | 954.6724 | 1372.694 | 0 | 0 | 0 | 1.3547 | 1.4688 | 2.503 | 3.6513 | 564.8957 | 639.9594 | 1004.9184 | 1444.941 | 0 | 0
|  |  |  | 328 | 1.2861 | 1.3943 | 2.3765 | 3.4669 | 537.937 | 609.3557 | 957.0489 | 1376.1609 | 0 | 0 | 0 | 1.3538 | 1.4677 | 2.5016 | 3.6494 | 566.2494 | 641.427 | 1007.4199 | 1448.5904 | 0 | 0
|  |  |  | 329 | 1.2852 | 1.3932 | 2.3751 | 3.4651 | 539.2222 | 610.7489 | 959.4241 | 1379.626 | 0 | 0 | 0 | 1.3529 | 1.4665 | 2.5001 | 3.6474 | 567.6023 | 642.8936 | 1009.9201 | 1452.2379 | 0 | 0
|  |  |  | 330 | 1.2844 | 1.3921 | 2.3738 | 3.4632 | 540.5065 | 612.141 | 961.7979 | 1383.0892 | 0 | 0 | 0 | 1.352 | 1.4654 | 2.4987 | 3.6455 | 568.9542 | 644.359 | 1012.4188 | 1455.8834 | 0 | 0
|  |  |  | 331 | 1.2835 | 1.391 | 2.3724 | 3.4614 | 541.79 | 613.532 | 964.1703 | 1386.5506 | 0 | 0 | 0 | 1.3511 | 1.4643 | 2.4973 | 3.6436 | 570.3053 | 645.8232 | 1014.9161 | 1459.5269 | 0 | 0
|  |  |  | 332 | 1.2826 | 1.39 | 2.3711 | 3.4596 | 543.0727 | 614.922 | 966.5414 | 1390.0102 | 0 | 0 | 0 | 1.3502 | 1.4631 | 2.4959 | 3.6416 | 571.6554 | 647.2863 | 1017.412 | 1463.1686 | 0 | 0
|  |  |  | 333 | 1.2818 | 1.3889 | 2.3698 | 3.4577 | 544.3545 | 616.3109 | 968.9112 | 1393.4679 | 0 | 0 | 0 | 1.3493 | 1.462 | 2.4945 | 3.6397 | 573.0047 | 648.7484 | 1019.9065 | 1466.8083 | 0 | 0
|  |  |  | 334 | 1.281 | 1.3878 | 2.3684 | 3.4559 | 545.6354 | 617.6988 | 971.2796 | 1396.9238 | 0 | 0 | 0 | 1.3484 | 1.4609 | 2.4931 | 3.6378 | 574.3531 | 650.2092 | 1022.3996 | 1470.4461 | 0 | 0
|  |  |  | 335 | 1.2801 | 1.3868 | 2.3671 | 3.4541 | 546.9155 | 619.0856 | 973.6467 | 1400.3779 | 0 | 0 | 0 | 1.3475 | 1.4598 | 2.4917 | 3.6359 | 575.7006 | 651.669 | 1024.8913 | 1474.082 | 0 | 0
|  |  |  | 336 | 1.2793 | 1.3857 | 2.3658 | 3.4523 | 548.1948 | 620.4713 | 976.0125 | 1403.8302 | 0 | 0 | 0 | 1.3466 | 1.4587 | 2.4903 | 3.634 | 577.0472 | 653.1277 | 1027.3816 | 1477.716 | 0 | 0
|  |  |  | 337 | 1.2784 | 1.3847 | 2.3645 | 3.4505 | 549.4732 | 621.856 | 978.377 | 1407.2807 | 0 | 0 | 0 | 1.3457 | 1.4576 | 2.4889 | 3.6321 | 578.3929 | 654.5853 | 1029.8705 | 1481.3481 | 0 | 0
|  |  |  | 338 | 1.2776 | 1.3836 | 2.3632 | 3.4487 | 550.7509 | 623.2397 | 980.7402 | 1410.7295 | 0 | 0 | 0 | 1.3448 | 1.4565 | 2.4875 | 3.6302 | 579.7377 | 656.0417 | 1032.3581 | 1484.9784 | 0 | 0
|  |  |  | 339 | 1.2768 | 1.3826 | 2.3619 | 3.4469 | 552.0276 | 624.6223 | 983.102 | 1414.1764 | 0 | 0 | 0 | 1.344 | 1.4554 | 2.4862 | 3.6283 | 581.0817 | 657.4971 | 1034.8442 | 1488.6067 | 0 | 0
|  |  |  | 340 | 1.2759 | 1.3816 | 2.3605 | 3.4451 | 553.3036 | 626.0038 | 985.4626 | 1417.6215 | 0 | 0 | 0 | 1.3431 | 1.4543 | 2.4848 | 3.6265 | 582.4248 | 658.9514 | 1037.329 | 1492.2332 | 0 | 0
|  |  |  | 341 | 1.2751 | 1.3805 | 2.3592 | 3.4434 | 554.5787 | 627.3844 | 987.8218 | 1421.0649 | 0 | 0 | 0 | 1.3422 | 1.4532 | 2.4834 | 3.6246 | 583.767 | 660.4046 | 1039.8124 | 1495.8578 | 0 | 0
|  |  |  | 342 | 1.2743 | 1.3795 | 2.358 | 3.4416 | 555.853 | 628.7639 | 990.1798 | 1424.5065 | 0 | 0 | 0 | 1.3414 | 1.4521 | 2.4821 | 3.6227 | 585.1084 | 661.8567 | 1042.2945 | 1499.4805 | 0 | 0
|  |  |  | 343 | 1.2735 | 1.3785 | 2.3567 | 3.4398 | 557.1265 | 630.1423 | 992.5364 | 1427.9464 | 0 | 0 | 0 | 1.3405 | 1.451 | 2.4807 | 3.6209 | 586.4489 | 663.3077 | 1044.7752 | 1503.1014 | 0 | 0
|  |  |  | 344 | 1.2727 | 1.3775 | 2.3554 | 3.4381 | 558.3991 | 631.5198 | 994.8918 | 1431.3845 | 0 | 0 | 0 | 1.3397 | 1.45 | 2.4793 | 3.619 | 587.7886 | 664.7577 | 1047.2545 | 1506.7205 | 0 | 0
|  |  |  | 345 | 1.2719 | 1.3764 | 2.3541 | 3.4363 | 559.671 | 632.8962 | 997.2459 | 1434.8208 | 0 | 0 | 0 | 1.3388 | 1.4489 | 2.478 | 3.6172 | 589.1274 | 666.2066 | 1049.7325 | 1510.3377 | 0 | 0
|  |  |  | 346 | 1.271 | 1.3754 | 2.3528 | 3.4346 | 560.942 | 634.2717 | 999.5987 | 1438.2554 | 0 | 0 | 0 | 1.3379 | 1.4478 | 2.4767 | 3.6154 | 590.4653 | 667.6544 | 1052.2092 | 1513.9531 | 0 | 0
|  |  |  | 347 | 1.2702 | 1.3744 | 2.3516 | 3.4329 | 562.2123 | 635.6461 | 1001.9503 | 1441.6883 | 0 | 0 | 0 | 1.3371 | 1.4468 | 2.4753 | 3.6135 | 591.8024 | 669.1011 | 1054.6845 | 1517.5666 | 0 | 0
|  |  |  | 348 | 1.2694 | 1.3734 | 2.3503 | 3.4311 | 563.4817 | 637.0195 | 1004.3006 | 1445.1194 | 0 | 0 | 0 | 1.3362 | 1.4457 | 2.474 | 3.6117 | 593.1387 | 670.5468 | 1057.1585 | 1521.1783 | 0 | 0
|  |  |  | 349 | 1.2686 | 1.3724 | 2.349 | 3.4294 | 564.7504 | 638.3919 | 1006.6496 | 1448.5488 | 0 | 0 | 0 | 1.3354 | 1.4446 | 2.4727 | 3.6099 | 594.4741 | 671.9915 | 1059.6311 | 1524.7882 | 0 | 0
|  |  |  | 350 | 1.2678 | 1.3714 | 2.3478 | 3.4277 | 566.0182 | 639.7633 | 1008.9973 | 1451.9765 | 0 | 0 | 0 | 1.3346 | 1.4436 | 2.4713 | 3.6081 | 595.8086 | 673.435 | 1062.1025 | 1528.3963 | 0 | 0
|  |  |  | 351 | 1.267 | 1.3704 | 2.3465 | 3.426 | 567.2852 | 641.1337 | 1011.3439 | 1455.4025 | 0 | 0 | 0 | 1.3337 | 1.4425 | 2.47 | 3.6063 | 597.1423 | 674.8776 | 1064.5725 | 1532.0026 | 0 | 0
|  |  |  | 352 | 1.2662 | 1.3694 | 2.3453 | 3.4243 | 568.5515 | 642.5031 | 1013.6891 | 1458.8267 | 0 | 0 | 0 | 1.3329 | 1.4415 | 2.4687 | 3.6045 | 598.4752 | 676.3191 | 1067.0412 | 1535.6071 | 0 | 0
|  |  |  | 353 | 1.2655 | 1.3684 | 2.344 | 3.4226 | 569.8169 | 643.8715 | 1016.0331 | 1462.2493 | 0 | 0 | 0 | 1.3321 | 1.4404 | 2.4674 | 3.6027 | 599.8073 | 677.7595 | 1069.5085 | 1539.2098 | 0 | 0
|  |  |  | 354 | 1.2647 | 1.3674 | 2.3428 | 3.4209 | 571.0816 | 645.239 | 1018.3759 | 1465.6702 | 0 | 0 | 0 | 1.3312 | 1.4394 | 2.4661 | 3.6009 | 601.1385 | 679.1989 | 1071.9746 | 1542.8107 | 0 | 0
|  |  |  | 355 | 1.2639 | 1.3665 | 2.3415 | 3.4192 | 572.3455 | 646.6054 | 1020.7174 | 1469.0894 | 0 | 0 | 0 | 1.3304 | 1.4384 | 2.4648 | 3.5991 | 602.4689 | 680.6373 | 1074.4394 | 1546.4099 | 0 | 0
|  |  |  | 356 | 1.2631 | 1.3655 | 2.3403 | 3.4175 | 573.6086 | 647.9709 | 1023.0577 | 1472.5069 | 0 | 0 | 0 | 1.3296 | 1.4373 | 2.4635 | 3.5974 | 603.7985 | 682.0746 | 1076.9029 | 1550.0072 | 0 | 0
|  |  |  | 357 | 1.2623 | 1.3645 | 2.3391 | 3.4158 | 574.8709 | 649.3354 | 1025.3968 | 1475.9227 | 0 | 0 | 0 | 1.3288 | 1.4363 | 2.4622 | 3.5956 | 605.1273 | 683.5109 | 1079.365 | 1553.6028 | 0 | 0
|  |  |  | 358 | 1.2615 | 1.3635 | 2.3378 | 3.4141 | 576.1325 | 650.6989 | 1027.7346 | 1479.3368 | 0 | 0 | 0 | 1.3279 | 1.4353 | 2.4609 | 3.5938 | 606.4552 | 684.9462 | 1081.8259 | 1557.1966 | 0 | 0
|  |  |  | 359 | 1.2608 | 1.3626 | 2.3366 | 3.4125 | 577.3932 | 652.0615 | 1030.0713 | 1482.7493 | 0 | 0 | 0 | 1.3271 | 1.4343 | 2.4596 | 3.5921 | 607.7824 | 686.3805 | 1084.2855 | 1560.7887 | 0 | 0
|  |  |  | 360 | 1.26 | 1.3616 | 2.3354 | 3.4108 | 578.6532 | 653.4231 | 1032.4067 | 1486.1601 | 0 | 0 | 0 | 1.3263 | 1.4333 | 2.4583 | 3.5903 | 609.1087 | 687.8138 | 1086.7439 | 1564.379 | 0 | 0
|  |  |  | 361 | 1.2592 | 1.3606 | 2.3342 | 3.4092 | 579.9125 | 654.7837 | 1034.7409 | 1489.5692 | 0 | 0 | 0 | 1.3255 | 1.4322 | 2.457 | 3.5886 | 610.4342 | 689.246 | 1089.2009 | 1567.9676 | 0 | 0
|  |  |  | 362 | 1.2585 | 1.3597 | 2.333 | 3.4075 | 581.1709 | 656.1434 | 1037.0738 | 1492.9767 | 0 | 0 | 0 | 1.3247 | 1.4312 | 2.4558 | 3.5868 | 611.7589 | 690.6773 | 1091.6567 | 1571.5545 | 0 | 0
|  |  |  | 363 | 1.2577 | 1.3587 | 2.3318 | 3.4059 | 582.4286 | 657.5021 | 1039.4056 | 1496.3826 | 0 | 0 | 0 | 1.3239 | 1.4302 | 2.4545 | 3.5851 | 613.0828 | 692.1075 | 1094.1112 | 1575.1396 | 0 | 0
|  |  |  | 364 | 1.2569 | 1.3578 | 2.3306 | 3.4042 | 583.6856 | 658.8599 | 1041.7362 | 1499.7868 | 0 | 0 | 0 | 1.3231 | 1.4292 | 2.4532 | 3.5834 | 614.4059 | 693.5367 | 1096.5644 | 1578.723 | 0 | 0
|  |  |  | 365 | 1.2562 | 1.3568 | 2.3294 | 3.4026 | 584.9418 | 660.2167 | 1044.0656 | 1503.1894 | 0 | 0 | 0 | 1.3223 | 1.4282 | 2.452 | 3.5817 | 615.7282 | 694.9649 | 1099.0164 | 1582.3046 | 0 | 0
|  |  |  | 366 | 1.2554 | 1.3559 | 2.3282 | 3.4009 | 586.1972 | 661.5726 | 1046.3938 | 1506.5903 | 0 | 0 | 0 | 1.3215 | 1.4272 | 2.4507 | 3.5799 | 617.0497 | 696.3922 | 1101.4671 | 1585.8846 | 0 | 0
|  |  |  | 367 | 1.2547 | 1.3549 | 2.327 | 3.3993 | 587.4519 | 662.9275 | 1048.7208 | 1509.9896 | 0 | 0 | 0 | 1.3207 | 1.4262 | 2.4495 | 3.5782 | 618.3704 | 697.8184 | 1103.9166 | 1589.4628 | 0 | 0
|  |  |  | 368 | 1.2539 | 1.354 | 2.3258 | 3.3977 | 588.7058 | 664.2815 | 1051.0466 | 1513.3873 | 0 | 0 | 0 | 1.3199 | 1.4253 | 2.4482 | 3.5765 | 619.6903 | 699.2437 | 1106.3648 | 1593.0393 | 0 | 0
|  |  |  | 369 | 1.2532 | 1.3531 | 2.3246 | 3.3961 | 589.959 | 665.6345 | 1053.3712 | 1516.7834 | 0 | 0 | 0 | 1.3191 | 1.4243 | 2.447 | 3.5748 | 621.0094 | 700.6679 | 1108.8118 | 1596.6141 | 0 | 0
|  |  |  | 370 | 1.2524 | 1.3521 | 2.3235 | 3.3945 | 591.2114 | 666.9867 | 1055.6947 | 1520.1779 | 0 | 0 | 0 | 1.3183 | 1.4233 | 2.4457 | 3.5731 | 622.3278 | 702.0912 | 1111.2575 | 1600.1873 | 0 | 0
|  |  |  | 371 | 1.2517 | 1.3512 | 2.3223 | 3.3929 | 592.4631 | 668.3379 | 1058.0169 | 1523.5708 | 0 | 0 | 0 | 1.3176 | 1.4223 | 2.4445 | 3.5714 | 623.6454 | 703.5135 | 1113.702 | 1603.7587 | 0 | 0
|  |  |  | 372 | 1.2509 | 1.3503 | 2.3211 | 3.3913 | 593.714 | 669.6881 | 1060.338 | 1526.962 | 0 | 0 | 0 | 1.3168 | 1.4213 | 2.4433 | 3.5698 | 624.9621 | 704.9349 | 1116.1453 | 1607.3285 | 0 | 0
|  |  |  | 373 | 1.2502 | 1.3493 | 2.3199 | 3.3897 | 594.9642 | 671.0375 | 1062.658 | 1530.3517 | 0 | 0 | 0 | 1.316 | 1.4204 | 2.442 | 3.5681 | 626.2782 | 706.3552 | 1118.5873 | 1610.8965 | 0 | 0
|  |  |  | 374 | 1.2495 | 1.3484 | 2.3188 | 3.3881 | 596.2137 | 672.3859 | 1064.9768 | 1533.7398 | 0 | 0 | 0 | 1.3152 | 1.4194 | 2.4408 | 3.5664 | 627.5934 | 707.7746 | 1121.0282 | 1614.463 | 0 | 0
|  |  |  | 375 | 1.2487 | 1.3475 | 2.3176 | 3.3865 | 597.4625 | 673.7334 | 1067.2944 | 1537.1263 | 0 | 0 | 0 | 1.3145 | 1.4184 | 2.4396 | 3.5647 | 628.9078 | 709.1931 | 1123.4678 | 1618.0277 | 0 | 0
|  |  |  | 376 | 1.248 | 1.3466 | 2.3165 | 3.3849 | 598.7105 | 675.08 | 1069.6108 | 1540.5112 | 0 | 0 | 0 | 1.3137 | 1.4175 | 2.4384 | 3.5631 | 630.2215 | 710.6105 | 1125.9062 | 1621.5908 | 0 | 0
|  |  |  | 377 | 1.2473 | 1.3457 | 2.3153 | 3.3833 | 599.9577 | 676.4257 | 1071.9262 | 1543.8946 | 0 | 0 | 0 | 1.3129 | 1.4165 | 2.4372 | 3.5614 | 631.5345 | 712.027 | 1128.3433 | 1625.1522 | 0 | 0
|  |  |  | 378 | 1.2465 | 1.3448 | 2.3142 | 3.3818 | 601.2043 | 677.7705 | 1074.2403 | 1547.2764 | 0 | 0 | 0 | 1.3122 | 1.4156 | 2.436 | 3.5598 | 632.8466 | 713.4426 | 1130.7793 | 1628.712 | 0 | 0
|  |  |  | 379 | 1.2458 | 1.3439 | 2.313 | 3.3802 | 602.4501 | 679.1143 | 1076.5533 | 1550.6566 | 0 | 0 | 0 | 1.3114 | 1.4146 | 2.4348 | 3.5581 | 634.158 | 714.8572 | 1133.214 | 1632.2701 | 0 | 0
|  |  |  | 380 | 1.2451 | 1.343 | 2.3119 | 3.3787 | 603.6952 | 680.4573 | 1078.8652 | 1554.0352 | 0 | 0 | 0 | 1.3106 | 1.4136 | 2.4336 | 3.5565 | 635.4686 | 716.2708 | 1135.6476 | 1635.8265 | 0 | 0
|  |  |  | 381 | 1.2444 | 1.3421 | 2.3107 | 3.3771 | 604.9396 | 681.7994 | 1081.176 | 1557.4123 | 0 | 0 | 0 | 1.3099 | 1.4127 | 2.4324 | 3.5548 | 636.7785 | 717.6835 | 1138.08 | 1639.3814 | 0 | 0
|  |  |  | 382 | 1.2437 | 1.3412 | 2.3096 | 3.3755 | 606.1833 | 683.1405 | 1083.4856 | 1560.7879 | 0 | 0 | 0 | 1.3091 | 1.4118 | 2.4312 | 3.5532 | 638.0876 | 719.0953 | 1140.5111 | 1642.9346 | 0 | 0
|  |  |  | 383 | 1.243 | 1.3403 | 2.3085 | 3.374 | 607.4262 | 684.4808 | 1085.794 | 1564.1619 | 0 | 0 | 0 | 1.3084 | 1.4108 | 2.43 | 3.5516 | 639.396 | 720.5061 | 1142.9411 | 1646.4862 | 0 | 0
|  |  |  | 384 | 1.2422 | 1.3394 | 2.3074 | 3.3725 | 608.6685 | 685.8202 | 1088.1014 | 1567.5343 | 0 | 0 | 0 | 1.3076 | 1.4099 | 2.4288 | 3.55 | 640.7036 | 721.916 | 1145.3699 | 1650.0361 | 0 | 0
|  |  |  | 385 | 1.2415 | 1.3385 | 2.3062 | 3.3709 | 609.91 | 687.1587 | 1090.4076 | 1570.9053 | 0 | 0 | 0 | 1.3069 | 1.4089 | 2.4276 | 3.5483 | 642.0105 | 723.325 | 1147.7975 | 1653.5845 | 0 | 0
|  |  |  | 386 | 1.2408 | 1.3376 | 2.3051 | 3.3694 | 611.1508 | 688.4963 | 1092.7127 | 1574.2747 | 0 | 0 | 0 | 1.3061 | 1.408 | 2.4264 | 3.5467 | 643.3166 | 724.733 | 1150.2239 | 1657.1312 | 0 | 0
|  |  |  | 387 | 1.2401 | 1.3367 | 2.304 | 3.3679 | 612.3909 | 689.8331 | 1095.0167 | 1577.6425 | 0 | 0 | 0 | 1.3054 | 1.4071 | 2.4253 | 3.5451 | 644.622 | 726.1401 | 1152.6492 | 1660.6763 | 0 | 0
|  |  |  | 388 | 1.2394 | 1.3359 | 2.3029 | 3.3663 | 613.6303 | 691.1689 | 1097.3196 | 1581.0089 | 0 | 0 | 0 | 1.3046 | 1.4062 | 2.4241 | 3.5435 | 645.9267 | 727.5462 | 1155.0733 | 1664.2199 | 0 | 0
|  |  |  | 389 | 1.2387 | 1.335 | 2.3018 | 3.3648 | 614.869 | 692.5039 | 1099.6214 | 1584.3737 | 0 | 0 | 0 | 1.3039 | 1.4052 | 2.4229 | 3.5419 | 647.2306 | 728.9515 | 1157.4962 | 1667.7618 | 0 | 0
|  |  |  | 390 | 1.238 | 1.3341 | 2.3007 | 3.3633 | 616.107 | 693.838 | 1101.922 | 1587.737 | 0 | 0 | 0 | 1.3032 | 1.4043 | 2.4218 | 3.5403 | 648.5337 | 730.3558 | 1159.9179 | 1671.3021 | 0 | 0
|  |  |  | 391 | 1.2373 | 1.3332 | 2.2996 | 3.3618 | 617.3443 | 695.1712 | 1104.2216 | 1591.0988 | 0 | 0 | 0 | 1.3024 | 1.4034 | 2.4206 | 3.5387 | 649.8362 | 731.7592 | 1162.3385 | 1674.8409 | 0 | 0
|  |  |  | 392 | 1.2366 | 1.3324 | 2.2985 | 3.3603 | 618.581 | 696.5036 | 1106.52 | 1594.4591 | 0 | 0 | 0 | 1.3017 | 1.4025 | 2.4194 | 3.5372 | 651.1379 | 733.1617 | 1164.7579 | 1678.378 | 0 | 0
|  |  |  | 393 | 1.2359 | 1.3315 | 2.2974 | 3.3588 | 619.8169 | 697.8351 | 1108.8174 | 1597.8179 | 0 | 0 | 0 | 1.301 | 1.4016 | 2.4183 | 3.5356 | 652.4388 | 734.5633 | 1167.1762 | 1681.9136 | 0 | 0
|  |  |  | 394 | 1.2352 | 1.3306 | 2.2963 | 3.3573 | 621.0521 | 699.1658 | 1111.1137 | 1601.1752 | 0 | 0 | 0 | 1.3002 | 1.4007 | 2.4171 | 3.534 | 653.7391 | 735.964 | 1169.5934 | 1685.4476 | 0 | 0
|  |  |  | 395 | 1.2345 | 1.3298 | 2.2952 | 3.3558 | 622.2867 | 700.4956 | 1113.4089 | 1604.5311 | 0 | 0 | 0 | 1.2995 | 1.3998 | 2.416 | 3.5324 | 655.0386 | 737.3637 | 1172.0093 | 1688.9801 | 0 | 0
|  |  |  | 396 | 1.2339 | 1.3289 | 2.2941 | 3.3543 | 623.5205 | 701.8245 | 1115.703 | 1607.8854 | 0 | 0 | 0 | 1.2988 | 1.3989 | 2.4148 | 3.5309 | 656.3374 | 738.7626 | 1174.4242 | 1692.511 | 0 | 0
|  |  |  | 397 | 1.2332 | 1.3281 | 2.293 | 3.3529 | 624.7537 | 703.1526 | 1117.996 | 1611.2383 | 0 | 0 | 0 | 1.2981 | 1.398 | 2.4137 | 3.5293 | 657.6355 | 740.1606 | 1176.8379 | 1696.0403 | 0 | 0
|  |  |  | 398 | 1.2325 | 1.3272 | 2.2919 | 3.3514 | 625.9862 | 704.4798 | 1120.2879 | 1614.5896 | 0 | 0 | 0 | 1.2974 | 1.3971 | 2.4126 | 3.5278 | 658.9328 | 741.5577 | 1179.2504 | 1699.568 | 0 | 0
|  |  |  | 399 | 1.2318 | 1.3264 | 2.2909 | 3.3499 | 627.218 | 705.8062 | 1122.5788 | 1617.9395 | 0 | 0 | 0 | 1.2966 | 1.3962 | 2.4114 | 3.5262 | 660.2295 | 742.9539 | 1181.6619 | 1703.0943 | 0 | 0
|  |  |  | 400 | 1.2311 | 1.3255 | 2.2898 | 3.3484 | 628.4491 | 707.1317 | 1124.8686 | 1621.288 | 0 | 0 | 0 | 1.2959 | 1.3953 | 2.4103 | 3.5247 | 661.5254 | 744.3492 | 1184.0722 | 1706.6189 | 0 | 0
|  |  |  | 401 | 1.2305 | 1.3247 | 2.2887 | 3.347 | 629.6796 | 708.4564 | 1127.1573 | 1624.635 | 0 | 0 | 0 | 1.2952 | 1.3944 | 2.4092 | 3.5231 | 662.8206 | 745.7436 | 1186.4813 | 1710.1421 | 0 | 0
|  |  |  | 402 | 1.2298 | 1.3238 | 2.2876 | 3.3455 | 630.9094 | 709.7802 | 1129.4449 | 1627.9805 | 0 | 0 | 0 | 1.2945 | 1.3935 | 2.4081 | 3.5216 | 664.1151 | 747.1371 | 1188.8894 | 1713.6637 | 0 | 0
|  |  |  | 403 | 1.2291 | 1.323 | 2.2866 | 3.3441 | 632.1385 | 711.1032 | 1131.7315 | 1631.3245 | 0 | 0 | 0 | 1.2938 | 1.3926 | 2.4069 | 3.5201 | 665.4089 | 748.5297 | 1191.2963 | 1717.1837 | 0 | 0
|  |  |  | 404 | 1.2284 | 1.3222 | 2.2855 | 3.3426 | 633.3669 | 712.4254 | 1134.017 | 1634.6671 | 0 | 0 | 0 | 1.2931 | 1.3918 | 2.4058 | 3.5185 | 666.702 | 749.9215 | 1193.7021 | 1720.7023 | 0 | 0
|  |  |  | 405 | 1.2278 | 1.3213 | 2.2845 | 3.3412 | 634.5947 | 713.7468 | 1136.3015 | 1638.0083 | 0 | 0 | 0 | 1.2924 | 1.3909 | 2.4047 | 3.517 | 667.9944 | 751.3124 | 1196.1068 | 1724.2193 | 0 | 0
|  |  |  | 406 | 1.2271 | 1.3205 | 2.2834 | 3.3397 | 635.8218 | 715.0673 | 1138.5849 | 1641.348 | 0 | 0 | 0 | 1.2917 | 1.39 | 2.4036 | 3.5155 | 669.2861 | 752.7024 | 1198.5104 | 1727.7348 | 0 | 0
|  |  |  | 407 | 1.2264 | 1.3197 | 2.2824 | 3.3383 | 637.0482 | 716.387 | 1140.8673 | 1644.6863 | 0 | 0 | 0 | 1.291 | 1.3891 | 2.4025 | 3.514 | 670.5771 | 754.0915 | 1200.9129 | 1731.2487 | 0 | 0
|  |  |  | 408 | 1.2258 | 1.3189 | 2.2813 | 3.3368 | 638.274 | 717.7058 | 1143.1486 | 1648.0232 | 0 | 0 | 0 | 1.2903 | 1.3883 | 2.4014 | 3.5125 | 671.8674 | 755.4798 | 1203.3143 | 1734.7612 | 0 | 0
|  |  |  | 409 | 1.2251 | 1.318 | 2.2803 | 3.3354 | 639.4991 | 719.0239 | 1145.4289 | 1651.3586 | 0 | 0 | 0 | 1.2896 | 1.3874 | 2.4003 | 3.511 | 673.157 | 756.8672 | 1205.7146 | 1738.2722 | 0 | 0
|  |  |  | 410 | 1.2245 | 1.3172 | 2.2792 | 3.334 | 640.7236 | 720.3411 | 1147.7081 | 1654.6926 | 0 | 0 | 0 | 1.2889 | 1.3865 | 2.3992 | 3.5095 | 674.4459 | 758.2538 | 1208.1138 | 1741.7816 | 0 | 0
|  |  |  | 411 | 1.2238 | 1.3164 | 2.2782 | 3.3326 | 641.9474 | 721.6575 | 1149.9863 | 1658.0251 | 0 | 0 | 0 | 1.2882 | 1.3857 | 2.3981 | 3.508 | 675.7341 | 759.6395 | 1210.5119 | 1745.2896 | 0 | 0
|  |  |  | 412 | 1.2232 | 1.3156 | 2.2772 | 3.3312 | 643.1706 | 722.9731 | 1152.2634 | 1661.3563 | 0 | 0 | 0 | 1.2875 | 1.3848 | 2.397 | 3.5065 | 677.0216 | 761.0243 | 1212.9089 | 1748.7961 | 0 | 0
|  |  |  | 413 | 1.2225 | 1.3148 | 2.2761 | 3.3297 | 644.3931 | 724.2878 | 1154.5395 | 1664.686 | 0 | 0 | 0 | 1.2868 | 1.384 | 2.3959 | 3.505 | 678.3085 | 762.4083 | 1215.3048 | 1752.3011 | 0 | 0
|  |  |  | 414 | 1.2218 | 1.314 | 2.2751 | 3.3283 | 645.6149 | 725.6018 | 1156.8146 | 1668.0144 | 0 | 0 | 0 | 1.2862 | 1.3831 | 2.3948 | 3.5035 | 679.5946 | 763.7914 | 1217.6996 | 1755.8046 | 0 | 0
|  |  |  | 415 | 1.2212 | 1.3132 | 2.2741 | 3.3269 | 646.8361 | 726.915 | 1159.0887 | 1671.3413 | 0 | 0 | 0 | 1.2855 | 1.3823 | 2.3938 | 3.502 | 680.8801 | 765.1736 | 1220.0934 | 1759.3066 | 0 | 0
|  |  |  | 416 | 1.2206 | 1.3124 | 2.273 | 3.3255 | 648.0567 | 728.2273 | 1161.3617 | 1674.6668 | 0 | 0 | 0 | 1.2848 | 1.3814 | 2.3927 | 3.5006 | 682.1649 | 766.5551 | 1222.486 | 1762.8072 | 0 | 0
|  |  |  | 417 | 1.2199 | 1.3115 | 2.272 | 3.3241 | 649.2766 | 729.5389 | 1163.6338 | 1677.9909 | 0 | 0 | 0 | 1.2841 | 1.3806 | 2.3916 | 3.4991 | 683.449 | 767.9356 | 1224.8776 | 1766.3062 | 0 | 0
|  |  |  | 418 | 1.2193 | 1.3107 | 2.271 | 3.3227 | 650.4958 | 730.8496 | 1165.9048 | 1681.3137 | 0 | 0 | 0 | 1.2834 | 1.3797 | 2.3905 | 3.4976 | 684.7325 | 769.3154 | 1227.2682 | 1769.8039 | 0 | 0
|  |  |  | 419 | 1.2186 | 1.31 | 2.27 | 3.3213 | 651.7145 | 732.1596 | 1168.1747 | 1684.635 | 0 | 0 | 0 | 1.2828 | 1.3789 | 2.3895 | 3.4962 | 686.0152 | 770.6943 | 1229.6576 | 1773.3 | 0 | 0
|  |  |  | 420 | 1.218 | 1.3092 | 2.269 | 3.32 | 652.9325 | 733.4687 | 1170.4437 | 1687.955 | 0 | 0 | 0 | 1.2821 | 1.3781 | 2.3884 | 3.4947 | 687.2973 | 772.0723 | 1232.046 | 1776.7947 | 0 | 0
|  |  |  | 421 | 1.2174 | 1.3084 | 2.268 | 3.3186 | 654.1498 | 734.7771 | 1172.7117 | 1691.2735 | 0 | 0 | 0 | 1.2814 | 1.3772 | 2.3873 | 3.4932 | 688.5787 | 773.4496 | 1234.4333 | 1780.2879 | 0 | 0
|  |  |  | 422 | 1.2167 | 1.3076 | 2.267 | 3.3172 | 655.3665 | 736.0847 | 1174.9786 | 1694.5907 | 0 | 0 | 0 | 1.2808 | 1.3764 | 2.3863 | 3.4918 | 689.8595 | 774.826 | 1236.8196 | 1783.7797 | 0 | 0
|  |  |  | 423 | 1.2161 | 1.3068 | 2.266 | 3.3158 | 656.5826 | 737.3914 | 1177.2446 | 1697.9066 | 0 | 0 | 0 | 1.2801 | 1.3756 | 2.3852 | 3.4903 | 691.1396 | 776.2015 | 1239.2048 | 1787.2701 | 0 | 0
|  |  |  | 424 | 1.2155 | 1.306 | 2.265 | 3.3145 | 657.7981 | 738.6974 | 1179.5095 | 1701.221 | 0 | 0 | 0 | 1.2794 | 1.3747 | 2.3842 | 3.4889 | 692.419 | 777.5763 | 1241.589 | 1790.759 | 0 | 0
|  |  |  | 425 | 1.2148 | 1.3052 | 2.264 | 3.3131 | 659.0129 | 740.0027 | 1181.7735 | 1704.5341 | 0 | 0 | 0 | 1.2788 | 1.3739 | 2.3831 | 3.4875 | 693.6978 | 778.9502 | 1243.9721 | 1794.2464 | 0 | 0
|  |  |  | 426 | 1.2142 | 1.3044 | 2.263 | 3.3117 | 660.2271 | 741.3071 | 1184.0364 | 1707.8458 | 0 | 0 | 0 | 1.2781 | 1.3731 | 2.3821 | 3.486 | 694.9759 | 780.3232 | 1246.3542 | 1797.7324 | 0 | 0
|  |  |  | 427 | 1.2136 | 1.3037 | 2.262 | 3.3104 | 661.4406 | 742.6107 | 1186.2984 | 1711.1562 | 0 | 0 | 0 | 1.2774 | 1.3723 | 2.381 | 3.4846 | 696.2533 | 781.6955 | 1248.7352 | 1801.217 | 0 | 0
|  |  |  | 428 | 1.2129 | 1.3029 | 2.261 | 3.309 | 662.6536 | 743.9136 | 1188.5594 | 1714.4652 | 0 | 0 | 0 | 1.2768 | 1.3715 | 2.38 | 3.4832 | 697.5301 | 783.067 | 1251.1151 | 1804.7002 | 0 | 0
|  |  |  | 429 | 1.2123 | 1.3021 | 2.26 | 3.3077 | 663.8659 | 745.2157 | 1190.8194 | 1717.7729 | 0 | 0 | 0 | 1.2761 | 1.3706 | 2.3789 | 3.4817 | 698.8062 | 784.4376 | 1253.4941 | 1808.182 | 0 | 0
|  |  |  | 430 | 1.2117 | 1.3013 | 2.259 | 3.3063 | 665.0776 | 746.5171 | 1193.0784 | 1721.0792 | 0 | 0 | 0 | 1.2755 | 1.3698 | 2.3779 | 3.4803 | 700.0817 | 785.8074 | 1255.872 | 1811.6623 | 0 | 0
|  |  |  | 431 | 1.2111 | 1.3006 | 2.258 | 3.305 | 666.2887 | 747.8176 | 1195.3364 | 1724.3841 | 0 | 0 | 0 | 1.2748 | 1.369 | 2.3769 | 3.4789 | 701.3565 | 787.1764 | 1258.2489 | 1815.1412 | 0 | 0
|  |  |  | 432 | 1.2105 | 1.2998 | 2.257 | 3.3036 | 667.4991 | 749.1174 | 1197.5935 | 1727.6878 | 0 | 0 | 0 | 1.2742 | 1.3682 | 2.3758 | 3.4775 | 702.6307 | 788.5446 | 1260.6247 | 1818.6187 | 0 | 0
|  |  |  | 433 | 1.2098 | 1.299 | 2.2561 | 3.3023 | 668.709 | 750.4164 | 1199.8495 | 1730.9901 | 0 | 0 | 0 | 1.2735 | 1.3674 | 2.3748 | 3.4761 | 703.9042 | 789.912 | 1262.9995 | 1822.0948 | 0 | 0
|  |  |  | 434 | 1.2092 | 1.2983 | 2.2551 | 3.301 | 669.9182 | 751.7147 | 1202.1046 | 1734.291 | 0 | 0 | 0 | 1.2729 | 1.3666 | 2.3738 | 3.4747 | 705.1771 | 791.2786 | 1265.3733 | 1825.5695 | 0 | 0
|  |  |  | 435 | 1.2086 | 1.2975 | 2.2541 | 3.2996 | 671.1268 | 753.0122 | 1204.3587 | 1737.5906 | 0 | 0 | 0 | 1.2722 | 1.3658 | 2.3728 | 3.4733 | 706.4493 | 792.6444 | 1267.746 | 1829.0428 | 0 | 0
|  |  |  | 436 | 1.208 | 1.2967 | 2.2532 | 3.2983 | 672.3349 | 754.309 | 1206.6119 | 1740.889 | 0 | 0 | 0 | 1.2716 | 1.365 | 2.3717 | 3.4719 | 707.7209 | 794.0094 | 1270.1178 | 1832.5147 | 0 | 0
|  |  |  | 437 | 1.2074 | 1.296 | 2.2522 | 3.297 | 673.5423 | 755.6049 | 1208.8641 | 1744.1859 | 0 | 0 | 0 | 1.2709 | 1.3642 | 2.3707 | 3.4705 | 708.9918 | 795.3736 | 1272.4885 | 1835.9852 | 0 | 0
|  |  |  | 438 | 1.2068 | 1.2952 | 2.2512 | 3.2957 | 674.749 | 756.9002 | 1211.1153 | 1747.4816 | 0 | 0 | 0 | 1.2703 | 1.3634 | 2.3697 | 3.4691 | 710.2622 | 796.737 | 1274.8582 | 1839.4543 | 0 | 0
|  |  |  | 439 | 1.2062 | 1.2945 | 2.2503 | 3.2943 | 675.9552 | 758.1947 | 1213.3656 | 1750.7759 | 0 | 0 | 0 | 1.2697 | 1.3626 | 2.3687 | 3.4677 | 711.5318 | 798.0996 | 1277.2269 | 1842.922 | 0 | 0
|  |  |  | 440 | 1.2056 | 1.2937 | 2.2493 | 3.293 | 677.1608 | 759.4884 | 1215.6149 | 1754.069 | 0 | 0 | 0 | 1.269 | 1.3618 | 2.3677 | 3.4664 | 712.8009 | 799.4615 | 1279.5946 | 1846.3884 | 0 | 0
|  |  |  | 441 | 1.205 | 1.293 | 2.2484 | 3.2917 | 678.3658 | 760.7814 | 1217.8633 | 1757.3607 | 0 | 0 | 0 | 1.2684 | 1.361 | 2.3667 | 3.465 | 714.0693 | 800.8225 | 1281.9613 | 1849.8534 | 0 | 0
|  |  |  | 442 | 1.2044 | 1.2922 | 2.2474 | 3.2904 | 679.5702 | 762.0736 | 1220.1107 | 1760.6511 | 0 | 0 | 0 | 1.2678 | 1.3603 | 2.3657 | 3.4636 | 715.337 | 802.1827 | 1284.327 | 1853.317 | 0 | 0
|  |  |  | 443 | 1.2038 | 1.2915 | 2.2465 | 3.2891 | 680.774 | 763.3651 | 1222.3571 | 1763.9403 | 0 | 0 | 0 | 1.2671 | 1.3595 | 2.3647 | 3.4622 | 716.6042 | 803.5422 | 1286.6917 | 1856.7792 | 0 | 0
|  |  |  | 444 | 1.2032 | 1.2908 | 2.2455 | 3.2878 | 681.9772 | 764.6559 | 1224.6026 | 1767.2281 | 0 | 0 | 0 | 1.2665 | 1.3587 | 2.3637 | 3.4609 | 717.8707 | 804.9009 | 1289.0554 | 1860.2401 | 0 | 0
|  |  |  | 445 | 1.2026 | 1.29 | 2.2446 | 3.2865 | 683.1798 | 765.9459 | 1226.8472 | 1770.5146 | 0 | 0 | 0 | 1.2659 | 1.3579 | 2.3627 | 3.4595 | 719.1366 | 806.2588 | 1291.4181 | 1863.6996 | 0 | 0
|  |  |  | 446 | 1.202 | 1.2893 | 2.2436 | 3.2852 | 684.3818 | 767.2351 | 1229.0908 | 1773.7999 | 0 | 0 | 0 | 1.2653 | 1.3571 | 2.3617 | 3.4581 | 720.4018 | 807.6159 | 1293.7798 | 1867.1577 | 0 | 0
|  |  |  | 447 | 1.2014 | 1.2885 | 2.2427 | 3.284 | 685.5832 | 768.5237 | 1231.3335 | 1777.0838 | 0 | 0 | 0 | 1.2646 | 1.3564 | 2.3607 | 3.4568 | 721.6665 | 808.9723 | 1296.1405 | 1870.6145 | 0 | 0
|  |  |  | 448 | 1.2008 | 1.2878 | 2.2417 | 3.2827 | 686.784 | 769.8115 | 1233.5752 | 1780.3665 | 0 | 0 | 0 | 1.264 | 1.3556 | 2.3597 | 3.4554 | 722.9305 | 810.3279 | 1298.5002 | 1874.07 | 0 | 0
|  |  |  | 449 | 1.2002 | 1.2871 | 2.2408 | 3.2814 | 687.9842 | 771.0986 | 1235.816 | 1783.6479 | 0 | 0 | 0 | 1.2634 | 1.3548 | 2.3587 | 3.4541 | 724.1939 | 811.6827 | 1300.859 | 1877.5241 | 0 | 0
|  |  |  | 450 | 1.1996 | 1.2863 | 2.2399 | 3.2801 | 689.1838 | 772.3849 | 1238.0559 | 1786.928 | 0 | 0 | 0 | 1.2628 | 1.354 | 2.3578 | 3.4527 | 725.4567 | 813.0367 | 1303.2167 | 1880.9768 | 0 | 0
|  |  |  | 451 | 1.1991 | 1.2856 | 2.2389 | 3.2788 | 690.3829 | 773.6705 | 1240.2949 | 1790.2068 | 0 | 0 | 0 | 1.2622 | 1.3533 | 2.3568 | 3.4514 | 726.7188 | 814.39 | 1305.5735 | 1884.4282 | 0 | 0
|  |  |  | 452 | 1.1985 | 1.2849 | 2.238 | 3.2776 | 691.5814 | 774.9554 | 1242.5329 | 1793.4844 | 0 | 0 | 0 | 1.2615 | 1.3525 | 2.3558 | 3.4501 | 727.9804 | 815.7425 | 1307.9293 | 1887.8783 | 0 | 0
|  |  |  | 453 | 1.1979 | 1.2842 | 2.2371 | 3.2763 | 692.7793 | 776.2396 | 1244.77 | 1796.7607 | 0 | 0 | 0 | 1.2609 | 1.3518 | 2.3548 | 3.4487 | 729.2413 | 817.0943 | 1310.2842 | 1891.327 | 0 | 0
|  |  |  | 454 | 1.1973 | 1.2834 | 2.2362 | 3.275 | 693.9766 | 777.523 | 1247.0061 | 1800.0357 | 0 | 0 | 0 | 1.2603 | 1.351 | 2.3539 | 3.4474 | 730.5017 | 818.4453 | 1312.638 | 1894.7744 | 0 | 0
|  |  |  | 455 | 1.1967 | 1.2827 | 2.2353 | 3.2738 | 695.1733 | 778.8058 | 1249.2414 | 1803.3095 | 0 | 0 | 0 | 1.2597 | 1.3502 | 2.3529 | 3.4461 | 731.7614 | 819.7955 | 1314.9909 | 1898.2205 | 0 | 0
|  |  |  | 456 | 1.1961 | 1.282 | 2.2343 | 3.2725 | 696.3694 | 780.0878 | 1251.4757 | 1806.582 | 0 | 0 | 0 | 1.2591 | 1.3495 | 2.3519 | 3.4448 | 733.0205 | 821.145 | 1317.3429 | 1901.6653 | 0 | 0
|  |  |  | 457 | 1.1956 | 1.2813 | 2.2334 | 3.2713 | 697.565 | 781.3691 | 1253.7092 | 1809.8533 | 0 | 0 | 0 | 1.2585 | 1.3487 | 2.351 | 3.4434 | 734.279 | 822.4938 | 1319.6938 | 1905.1087 | 0 | 0
|  |  |  | 458 | 1.195 | 1.2806 | 2.2325 | 3.27 | 698.76 | 782.6497 | 1255.9417 | 1813.1233 | 0 | 0 | 0 | 1.2579 | 1.348 | 2.35 | 3.4421 | 735.5369 | 823.8417 | 1322.0439 | 1908.5508 | 0 | 0
|  |  |  | 459 | 1.1944 | 1.2799 | 2.2316 | 3.2688 | 699.9544 | 783.9295 | 1258.1733 | 1816.3921 | 0 | 0 | 0 | 1.2573 | 1.3472 | 2.349 | 3.4408 | 736.7942 | 825.189 | 1324.3929 | 1911.9917 | 0 | 0
|  |  |  | 460 | 1.1939 | 1.2792 | 2.2307 | 3.2675 | 701.1483 | 785.2087 | 1260.4039 | 1819.6596 | 0 | 0 | 0 | 1.2567 | 1.3465 | 2.3481 | 3.4395 | 738.0508 | 826.5355 | 1326.741 | 1915.4311 | 0 | 0
|  |  |  | 461 | 1.1933 | 1.2785 | 2.2298 | 3.2663 | 702.3416 | 786.4871 | 1262.6337 | 1822.9259 | 0 | 0 | 0 | 1.2561 | 1.3457 | 2.3471 | 3.4382 | 739.3069 | 827.8812 | 1329.0881 | 1918.8693 | 0 | 0
|  |  |  | 462 | 1.1927 | 1.2777 | 2.2289 | 3.265 | 703.5343 | 787.7649 | 1264.8626 | 1826.1909 | 0 | 0 | 0 | 1.2555 | 1.345 | 2.3462 | 3.4369 | 740.5624 | 829.2262 | 1331.4343 | 1922.3062 | 0 | 0
|  |  |  | 463 | 1.1921 | 1.277 | 2.228 | 3.2638 | 704.7264 | 789.0419 | 1267.0906 | 1829.4547 | 0 | 0 | 0 | 1.2549 | 1.3443 | 2.3452 | 3.4356 | 741.8173 | 830.5705 | 1333.7796 | 1925.7418 | 0 | 0
|  |  |  | 464 | 1.1916 | 1.2763 | 2.2271 | 3.2626 | 705.918 | 790.3183 | 1269.3177 | 1832.7173 | 0 | 0 | 0 | 1.2543 | 1.3435 | 2.3443 | 3.4343 | 743.0716 | 831.914 | 1336.1239 | 1929.1761 | 0 | 0
|  |  |  | 465 | 1.191 | 1.2756 | 2.2262 | 3.2613 | 707.109 | 791.5939 | 1271.5439 | 1835.9787 | 0 | 0 | 0 | 1.2537 | 1.3428 | 2.3434 | 3.433 | 744.3253 | 833.2568 | 1338.4672 | 1932.6091 | 0 | 0
|  |  |  | 466 | 1.1905 | 1.2749 | 2.2253 | 3.2601 | 708.2995 | 792.8689 | 1273.7691 | 1839.2388 | 0 | 0 | 0 | 1.2531 | 1.342 | 2.3424 | 3.4317 | 745.5784 | 834.5988 | 1340.8096 | 1936.0408 | 0 | 0
|  |  |  | 467 | 1.1899 | 1.2742 | 2.2244 | 3.2589 | 709.4894 | 794.1431 | 1275.9935 | 1842.4977 | 0 | 0 | 0 | 1.2525 | 1.3413 | 2.3415 | 3.4304 | 746.8309 | 835.9401 | 1343.1511 | 1939.4712 | 0 | 0
|  |  |  | 468 | 1.1893 | 1.2736 | 2.2235 | 3.2577 | 710.6787 | 795.4167 | 1278.217 | 1845.7554 | 0 | 0 | 0 | 1.2519 | 1.3406 | 2.3405 | 3.4291 | 748.0829 | 837.2807 | 1345.4916 | 1942.9004 | 0 | 0
|  |  |  | 469 | 1.1888 | 1.2729 | 2.2226 | 3.2565 | 711.8675 | 796.6895 | 1280.4397 | 1849.0118 | 0 | 0 | 0 | 1.2513 | 1.3399 | 2.3396 | 3.4279 | 749.3342 | 838.6206 | 1347.8312 | 1946.3282 | 0 | 0
|  |  |  | 470 | 1.1882 | 1.2722 | 2.2217 | 3.2553 | 713.0557 | 797.9617 | 1282.6614 | 1852.2671 | 0 | 0 | 0 | 1.2508 | 1.3391 | 2.3387 | 3.4266 | 750.585 | 839.9597 | 1350.1699 | 1949.7548 | 0 | 0
|  |  |  | 471 | 1.1877 | 1.2715 | 2.2209 | 3.254 | 714.2434 | 799.2332 | 1284.8823 | 1855.5211 | 0 | 0 | 0 | 1.2502 | 1.3384 | 2.3377 | 3.4253 | 751.8351 | 841.2981 | 1352.5076 | 1953.1801 | 0 | 0
|  |  |  | 472 | 1.1871 | 1.2708 | 2.22 | 3.2528 | 715.4305 | 800.504 | 1287.1022 | 1858.774 | 0 | 0 | 0 | 1.2496 | 1.3377 | 2.3368 | 3.424 | 753.0847 | 842.6358 | 1354.8445 | 1956.6042 | 0 | 0
|  |  |  | 473 | 1.1866 | 1.2701 | 2.2191 | 3.2516 | 716.617 | 801.7741 | 1289.3213 | 1862.0256 | 0 | 0 | 0 | 1.249 | 1.337 | 2.3359 | 3.4228 | 754.3337 | 843.9728 | 1357.1803 | 1960.027 | 0 | 0
|  |  |  | 474 | 1.186 | 1.2694 | 2.2182 | 3.2504 | 717.8031 | 803.0435 | 1291.5395 | 1865.276 | 0 | 0 | 0 | 1.2484 | 1.3362 | 2.335 | 3.4215 | 755.5822 | 845.309 | 1359.5153 | 1963.4485 | 0 | 0
|  |  |  | 475 | 1.1855 | 1.2687 | 2.2173 | 3.2492 | 718.9885 | 804.3123 | 1293.7569 | 1868.5253 | 0 | 0 | 0 | 1.2478 | 1.3355 | 2.334 | 3.4202 | 756.83 | 846.6445 | 1361.8494 | 1966.8687 | 0 | 0
|  |  |  | 476 | 1.1849 | 1.2681 | 2.2165 | 3.248 | 720.1734 | 805.5804 | 1295.9734 | 1871.7733 | 0 | 0 | 0 | 1.2473 | 1.3348 | 2.3331 | 3.419 | 758.0773 | 847.9793 | 1364.1825 | 1970.2877 | 0 | 0
|  |  |  | 477 | 1.1844 | 1.2674 | 2.2156 | 3.2468 | 721.3578 | 806.8477 | 1298.189 | 1875.0202 | 0 | 0 | 0 | 1.2467 | 1.3341 | 2.3322 | 3.4177 | 759.324 | 849.3134 | 1366.5147 | 1973.7054 | 0 | 0
|  |  |  | 478 | 1.1838 | 1.2667 | 2.2147 | 3.2457 | 722.5416 | 808.1145 | 1300.4037 | 1878.2658 | 0 | 0 | 0 | 1.2461 | 1.3334 | 2.3313 | 3.4165 | 760.5701 | 850.6468 | 1368.846 | 1977.1219 | 0 | 0
|  |  |  | 479 | 1.1833 | 1.266 | 2.2139 | 3.2445 | 723.7249 | 809.3805 | 1302.6176 | 1881.5103 | 0 | 0 | 0 | 1.2455 | 1.3327 | 2.3304 | 3.4152 | 761.8156 | 851.9795 | 1371.1764 | 1980.5371 | 0 | 0
|  |  |  | 480 | 1.1827 | 1.2654 | 2.213 | 3.2433 | 724.9076 | 810.6459 | 1304.8306 | 1884.7536 | 0 | 0 | 0 | 1.245 | 1.332 | 2.3295 | 3.414 | 763.0606 | 853.3114 | 1373.5059 | 1983.9511 | 0 | 0
|  |  |  | 481 | 1.1822 | 1.2647 | 2.2121 | 3.2421 | 726.0898 | 811.9106 | 1307.0427 | 1887.9957 | 0 | 0 | 0 | 1.2444 | 1.3313 | 2.3286 | 3.4127 | 764.305 | 854.6427 | 1375.8345 | 1987.3639 | 0 | 0
|  |  |  | 482 | 1.1816 | 1.264 | 2.2113 | 3.2409 | 727.2714 | 813.1746 | 1309.254 | 1891.2366 | 0 | 0 | 0 | 1.2438 | 1.3306 | 2.3277 | 3.4115 | 765.5489 | 855.9733 | 1378.1621 | 1990.7754 | 0 | 0
|  |  |  | 483 | 1.1811 | 1.2634 | 2.2104 | 3.2398 | 728.4525 | 814.438 | 1311.4645 | 1894.4764 | 0 | 0 | 0 | 1.2433 | 1.3299 | 2.3268 | 3.4103 | 766.7921 | 857.3031 | 1380.4889 | 1994.1857 | 0 | 0
|  |  |  | 484 | 1.1806 | 1.2627 | 2.2096 | 3.2386 | 729.6331 | 815.7006 | 1313.674 | 1897.715 | 0 | 0 | 0 | 1.2427 | 1.3292 | 2.3259 | 3.409 | 768.0348 | 858.6323 | 1382.8148 | 1997.5947 | 0 | 0
|  |  |  | 485 | 1.18 | 1.262 | 2.2087 | 3.2374 | 730.8131 | 816.9627 | 1315.8828 | 1900.9524 | 0 | 0 | 0 | 1.2421 | 1.3285 | 2.325 | 3.4078 | 769.277 | 859.9607 | 1385.1397 | 2001.0025 | 0 | 0
|  |  |  | 486 | 1.1795 | 1.2614 | 2.2079 | 3.2363 | 731.9926 | 818.224 | 1318.0906 | 1904.1886 | 0 | 0 | 0 | 1.2416 | 1.3278 | 2.3241 | 3.4066 | 770.5186 | 861.2885 | 1387.4638 | 2004.4091 | 0 | 0
|  |  |  | 487 | 1.179 | 1.2607 | 2.207 | 3.2351 | 733.1716 | 819.4848 | 1320.2977 | 1907.4237 | 0 | 0 | 0 | 1.241 | 1.3271 | 2.3232 | 3.4054 | 771.7596 | 862.6155 | 1389.787 | 2007.8144 | 0 | 0
|  |  |  | 488 | 1.1784 | 1.26 | 2.2062 | 3.2339 | 734.35 | 820.7448 | 1322.5038 | 1910.6576 | 0 | 0 | 0 | 1.2405 | 1.3264 | 2.3223 | 3.4041 | 773 | 863.9419 | 1392.1093 | 2011.2186 | 0 | 0
|  |  |  | 489 | 1.1779 | 1.2594 | 2.2053 | 3.2328 | 735.5279 | 822.0042 | 1324.7092 | 1913.8904 | 0 | 0 | 0 | 1.2399 | 1.3257 | 2.3214 | 3.4029 | 774.2399 | 865.2676 | 1394.4307 | 2014.6215 | 0 | 0
|  |  |  | 490 | 1.1774 | 1.2587 | 2.2045 | 3.2316 | 736.7053 | 823.2629 | 1326.9137 | 1917.122 | 0 | 0 | 0 | 1.2393 | 1.325 | 2.3205 | 3.4017 | 775.4793 | 866.5926 | 1396.7512 | 2018.0232 | 0 | 0
|  |  |  | 491 | 1.1768 | 1.2581 | 2.2037 | 3.2305 | 737.8822 | 824.521 | 1329.1173 | 1920.3525 | 0 | 0 | 0 | 1.2388 | 1.3243 | 2.3196 | 3.4005 | 776.7181 | 867.9169 | 1399.0709 | 2021.4237 | 0 | 0
|  |  |  | 492 | 1.1763 | 1.2574 | 2.2028 | 3.2293 | 739.0585 | 825.7785 | 1331.3201 | 1923.5818 | 0 | 0 | 0 | 1.2382 | 1.3236 | 2.3188 | 3.3993 | 777.9563 | 869.2405 | 1401.3896 | 2024.823 | 0 | 0
|  |  |  | 493 | 1.1758 | 1.2568 | 2.202 | 3.2282 | 740.2343 | 827.0352 | 1333.5221 | 1926.81 | 0 | 0 | 0 | 1.2377 | 1.3229 | 2.3179 | 3.3981 | 779.194 | 870.5634 | 1403.7075 | 2028.221 | 0 | 0
|  |  |  | 494 | 1.1753 | 1.2561 | 2.2011 | 3.227 | 741.4095 | 828.2914 | 1335.7233 | 1930.037 | 0 | 0 | 0 | 1.2371 | 1.3222 | 2.317 | 3.3969 | 780.4311 | 871.8856 | 1406.0245 | 2031.6179 | 0 | 0
|  |  |  | 495 | 1.1747 | 1.2555 | 2.2003 | 3.2259 | 742.5843 | 829.5469 | 1337.9236 | 1933.2629 | 0 | 0 | 0 | 1.2366 | 1.3216 | 2.3161 | 3.3957 | 781.6677 | 873.2072 | 1408.3406 | 2035.0136 | 0 | 0
|  |  |  | 496 | 1.1742 | 1.2548 | 2.1995 | 3.2247 | 743.7585 | 830.8017 | 1340.1231 | 1936.4876 | 0 | 0 | 0 | 1.236 | 1.3209 | 2.3152 | 3.3945 | 782.9037 | 874.5281 | 1410.6559 | 2038.408 | 0 | 0
|  |  |  | 497 | 1.1737 | 1.2542 | 2.1987 | 3.2236 | 744.9322 | 832.0559 | 1342.3217 | 1939.7112 | 0 | 0 | 0 | 1.2355 | 1.3202 | 2.3144 | 3.3933 | 784.1392 | 875.8483 | 1412.9702 | 2041.8013 | 0 | 0
|  |  |  | 498 | 1.1732 | 1.2536 | 2.1978 | 3.2225 | 746.1054 | 833.3094 | 1344.5196 | 1942.9337 | 0 | 0 | 0 | 1.2349 | 1.3195 | 2.3135 | 3.3921 | 785.3741 | 877.1678 | 1415.2838 | 2045.1934 | 0 | 0
|  |  |  | 499 | 1.1727 | 1.2529 | 2.197 | 3.2213 | 747.2781 | 834.5624 | 1346.7166 | 1946.1551 | 0 | 0 | 0 | 1.2344 | 1.3189 | 2.3126 | 3.3909 | 786.6085 | 878.4867 | 1417.5964 | 2048.5843 | 0 | 0
|  |  |  | 500 | 1.1722 | 1.2523 | 2.1962 | 3.2202 | 748.4502 | 835.8146 | 1348.9128 | 1949.3753 | 0 | 0 | 0 | 1.2338 | 1.3182 | 2.3118 | 3.3897 | 787.8424 | 879.8049 | 1419.9082 | 2051.974 | 0 | 0
|  |  |  | 501 | 1.1716 | 1.2516 | 2.1954 | 3.2191 | 749.6219 | 837.0663 | 1351.1081 | 1952.5944 | 0 | 0 | 0 | 1.2333 | 1.3175 | 2.3109 | 3.3885 | 789.0757 | 881.1224 | 1422.2191 | 2055.3625 | 0 | 0
|  |  |  | 502 | 1.1711 | 1.251 | 2.1945 | 3.218 | 750.793 | 838.3173 | 1353.3027 | 1955.8123 | 0 | 0 | 0 | 1.2328 | 1.3168 | 2.3101 | 3.3873 | 790.3084 | 882.4392 | 1424.5291 | 2058.7498 | 0 | 0
|  |  |  | 503 | 1.1706 | 1.2504 | 2.1937 | 3.2169 | 751.9636 | 839.5676 | 1355.4964 | 1959.0292 | 0 | 0 | 0 | 1.2322 | 1.3162 | 2.3092 | 3.3862 | 791.5406 | 883.7554 | 1426.8383 | 2062.136 | 0 | 0
|  |  |  | 504 | 1.1701 | 1.2497 | 2.1929 | 3.2157 | 753.1337 | 840.8174 | 1357.6893 | 1962.2449 | 0 | 0 | 0 | 1.2317 | 1.3155 | 2.3083 | 3.385 | 792.7723 | 885.0709 | 1429.1467 | 2065.521 | 0 | 0
|  |  |  | 505 | 1.1696 | 1.2491 | 2.1921 | 3.2146 | 754.3033 | 842.0665 | 1359.8814 | 1965.4596 | 0 | 0 | 0 | 1.2311 | 1.3148 | 2.3075 | 3.3838 | 794.0035 | 886.3858 | 1431.4541 | 2068.9048 | 0 | 0
|  |  |  | 506 | 1.1691 | 1.2485 | 2.1913 | 3.2135 | 755.4724 | 843.315 | 1362.0727 | 1968.6731 | 0 | 0 | 0 | 1.2306 | 1.3142 | 2.3066 | 3.3826 | 795.2341 | 887.7 | 1433.7608 | 2072.2874 | 0 | 0
|  |  |  | 507 | 1.1686 | 1.2478 | 2.1905 | 3.2124 | 756.641 | 844.5628 | 1364.2632 | 1971.8855 | 0 | 0 | 0 | 1.2301 | 1.3135 | 2.3058 | 3.3815 | 796.4642 | 889.0135 | 1436.0665 | 2075.6689 | 0 | 0
|  |  |  | 508 | 1.1681 | 1.2472 | 2.1897 | 3.2113 | 757.809 | 845.81 | 1366.4529 | 1975.0968 | 0 | 0 | 0 | 1.2295 | 1.3129 | 2.3049 | 3.3803 | 797.6937 | 890.3263 | 1438.3715 | 2079.0492 | 0 | 0
|  |  |  | 509 | 1.1676 | 1.2466 | 2.1889 | 3.2102 | 758.9766 | 847.0566 | 1368.6418 | 1978.307 | 0 | 0 | 0 | 1.229 | 1.3122 | 2.3041 | 3.3791 | 798.9227 | 891.6385 | 1440.6756 | 2082.4284 | 0 | 0
|  |  |  | 510 | 1.1671 | 1.246 | 2.1881 | 3.2091 | 760.1436 | 848.3026 | 1370.8298 | 1981.5161 | 0 | 0 | 0 | 1.2285 | 1.3116 | 2.3032 | 3.378 | 800.1512 | 892.9501 | 1442.9788 | 2085.8064 | 0 | 0
|  |  |  | 511 | 1.1666 | 1.2454 | 2.1873 | 3.208 | 761.3102 | 849.5479 | 1373.0171 | 1984.724 | 0 | 0 | 0 | 1.228 | 1.3109 | 2.3024 | 3.3768 | 801.3792 | 894.261 | 1445.2812 | 2089.1832 | 0 | 0
|  |  |  | 512 | 1.1661 | 1.2447 | 2.1865 | 3.2069 | 762.4763 | 850.7927 | 1375.2036 | 1987.9309 | 0 | 0 | 0 | 1.2274 | 1.3102 | 2.3016 | 3.3757 | 802.6066 | 895.5712 | 1447.5827 | 2092.5589 | 0 | 0
|  |  |  | 513 | 1.1656 | 1.2441 | 2.1857 | 3.2058 | 763.6418 | 852.0368 | 1377.3893 | 1991.1367 | 0 | 0 | 0 | 1.2269 | 1.3096 | 2.3007 | 3.3745 | 803.8335 | 896.8808 | 1449.8834 | 2095.9334 | 0 | 0
|  |  |  | 514 | 1.1651 | 1.2435 | 2.1849 | 3.2047 | 764.8069 | 853.2803 | 1379.5742 | 1994.3414 | 0 | 0 | 0 | 1.2264 | 1.3089 | 2.2999 | 3.3734 | 805.0599 | 898.1898 | 1452.1833 | 2099.3068 | 0 | 0
|  |  |  | 515 | 1.1646 | 1.2429 | 2.1841 | 3.2036 | 765.9714 | 854.5232 | 1381.7582 | 1997.5451 | 0 | 0 | 0 | 1.2258 | 1.3083 | 2.299 | 3.3722 | 806.2857 | 899.4981 | 1454.4824 | 2102.679 | 0 | 0
|  |  |  | 516 | 1.1641 | 1.2423 | 2.1833 | 3.2025 | 767.1355 | 855.7654 | 1383.9415 | 2000.7476 | 0 | 0 | 0 | 1.2253 | 1.3076 | 2.2982 | 3.3711 | 807.511 | 900.8057 | 1456.7806 | 2106.0501 | 0 | 0
|  |  |  | 517 | 1.1636 | 1.2417 | 2.1825 | 3.2015 | 768.299 | 857.0071 | 1386.124 | 2003.9491 | 0 | 0 | 0 | 1.2248 | 1.307 | 2.2974 | 3.3699 | 808.7358 | 902.1127 | 1459.0779 | 2109.4201 | 0 | 0
|  |  |  | 518 | 1.1631 | 1.241 | 2.1817 | 3.2004 | 769.4621 | 858.2481 | 1388.3058 | 2007.1494 | 0 | 0 | 0 | 1.2243 | 1.3064 | 2.2965 | 3.3688 | 809.9601 | 903.4191 | 1461.3745 | 2112.7889 | 0 | 0
|  |  |  | 519 | 1.1626 | 1.2404 | 2.1809 | 3.1993 | 770.6247 | 859.4886 | 1390.4867 | 2010.3487 | 0 | 0 | 0 | 1.2238 | 1.3057 | 2.2957 | 3.3677 | 811.1839 | 904.7248 | 1463.6702 | 2116.1565 | 0 | 0
|  |  |  | 520 | 1.1621 | 1.2398 | 2.1801 | 3.1982 | 771.7868 | 860.7284 | 1392.6668 | 2013.5469 | 0 | 0 | 0 | 1.2232 | 1.3051 | 2.2949 | 3.3665 | 812.4071 | 906.0299 | 1465.9651 | 2119.5231 | 0 | 0
|  |  |  | 521 | 1.1616 | 1.2392 | 2.1794 | 3.1971 | 772.9484 | 861.9676 | 1394.8462 | 2016.7441 | 0 | 0 | 0 | 1.2227 | 1.3044 | 2.2941 | 3.3654 | 813.6298 | 907.3343 | 1468.2592 | 2122.8885 | 0 | 0
|  |  |  | 522 | 1.1611 | 1.2386 | 2.1786 | 3.1961 | 774.1095 | 863.2062 | 1397.0248 | 2019.9401 | 0 | 0 | 0 | 1.2222 | 1.3038 | 2.2932 | 3.3643 | 814.8521 | 908.6381 | 1470.5524 | 2126.2528 | 0 | 0
|  |  |  | 523 | 1.1606 | 1.238 | 2.1778 | 3.195 | 775.2701 | 864.4442 | 1399.2026 | 2023.1351 | 0 | 0 | 0 | 1.2217 | 1.3032 | 2.2924 | 3.3632 | 816.0738 | 909.9413 | 1472.8449 | 2129.6159 | 0 | 0
|  |  |  | 524 | 1.1601 | 1.2374 | 2.177 | 3.1939 | 776.4302 | 865.6816 | 1401.3796 | 2026.3291 | 0 | 0 | 0 | 1.2212 | 1.3025 | 2.2916 | 3.362 | 817.2949 | 911.2438 | 1475.1365 | 2132.978 | 0 | 0
|  |  |  | 525 | 1.1596 | 1.2368 | 2.1763 | 3.1929 | 777.5898 | 866.9184 | 1403.5559 | 2029.522 | 0 | 0 | 0 | 1.2207 | 1.3019 | 2.2908 | 3.3609 | 818.5156 | 912.5457 | 1477.4273 | 2136.3389 | 0 | 0
|  |  |  | 526 | 1.1592 | 1.2362 | 2.1755 | 3.1918 | 778.749 | 868.1546 | 1405.7314 | 2032.7138 | 0 | 0 | 0 | 1.2202 | 1.3013 | 2.29 | 3.3598 | 819.7358 | 913.847 | 1479.7172 | 2139.6987 | 0 | 0
|  |  |  | 527 | 1.1587 | 1.2356 | 2.1747 | 3.1907 | 779.9077 | 869.3902 | 1407.9061 | 2035.9045 | 0 | 0 | 0 | 1.2197 | 1.3006 | 2.2892 | 3.3587 | 820.9554 | 915.1476 | 1482.0064 | 2143.0574 | 0 | 0
|  |  |  | 528 | 1.1582 | 1.235 | 2.1739 | 3.1897 | 781.0658 | 870.6253 | 1410.08 | 2039.0942 | 0 | 0 | 0 | 1.2191 | 1.3 | 2.2884 | 3.3576 | 822.1746 | 916.4476 | 1484.2948 | 2146.415 | 0 | 0
|  |  |  | 529 | 1.1577 | 1.2344 | 2.1732 | 3.1886 | 782.2235 | 871.8597 | 1412.2532 | 2042.2828 | 0 | 0 | 0 | 1.2186 | 1.2994 | 2.2875 | 3.3565 | 823.3932 | 917.747 | 1486.5823 | 2149.7714 | 0 | 0
|  |  |  | 530 | 1.1572 | 1.2338 | 2.1724 | 3.1876 | 783.3808 | 873.0935 | 1414.4256 | 2045.4704 | 0 | 0 | 0 | 1.2181 | 1.2988 | 2.2867 | 3.3554 | 824.6113 | 919.0458 | 1488.869 | 2153.1268 | 0 | 0
|  |  |  | 531 | 1.1567 | 1.2332 | 2.1716 | 3.1865 | 784.5375 | 874.3267 | 1416.5972 | 2048.657 | 0 | 0 | 0 | 1.2176 | 1.2981 | 2.2859 | 3.3542 | 825.829 | 920.3439 | 1491.155 | 2156.481 | 0 | 0
|  |  |  | 532 | 1.1563 | 1.2326 | 2.1709 | 3.1855 | 785.6938 | 875.5594 | 1418.7681 | 2051.8424 | 0 | 0 | 0 | 1.2171 | 1.2975 | 2.2851 | 3.3531 | 827.0461 | 921.6414 | 1493.4401 | 2159.8342 | 0 | 0
|  |  |  | 533 | 1.1558 | 1.232 | 2.1701 | 3.1844 | 786.8496 | 876.7914 | 1420.9382 | 2055.0269 | 0 | 0 | 0 | 1.2166 | 1.2969 | 2.2843 | 3.352 | 828.2627 | 922.9383 | 1495.7244 | 2163.1862 | 0 | 0
|  |  |  | 534 | 1.1553 | 1.2315 | 2.1694 | 3.1834 | 788.0049 | 878.0229 | 1423.1076 | 2058.2103 | 0 | 0 | 0 | 1.2161 | 1.2963 | 2.2835 | 3.3509 | 829.4788 | 924.2346 | 1498.008 | 2166.5371 | 0 | 0
|  |  |  | 535 | 1.1548 | 1.2309 | 2.1686 | 3.1824 | 789.1597 | 879.2537 | 1425.2762 | 2061.3926 | 0 | 0 | 0 | 1.2156 | 1.2957 | 2.2827 | 3.3499 | 830.6944 | 925.5303 | 1500.2907 | 2169.887 | 0 | 0
|  |  |  | 536 | 1.1544 | 1.2303 | 2.1678 | 3.1813 | 790.3141 | 880.484 | 1427.444 | 2064.574 | 0 | 0 | 0 | 1.2151 | 1.295 | 2.2819 | 3.3488 | 831.9095 | 926.8253 | 1502.5727 | 2173.2358 | 0 | 0
|  |  |  | 537 | 1.1539 | 1.2297 | 2.1671 | 3.1803 | 791.468 | 881.7137 | 1429.6111 | 2067.7543 | 0 | 0 | 0 | 1.2146 | 1.2944 | 2.2811 | 3.3477 | 833.1242 | 928.1197 | 1504.8538 | 2176.5834 | 0 | 0
|  |  |  | 538 | 1.1534 | 1.2291 | 2.1663 | 3.1792 | 792.6214 | 882.9429 | 1431.7774 | 2070.9335 | 0 | 0 | 0 | 1.2141 | 1.2938 | 2.2804 | 3.3466 | 834.3383 | 929.4135 | 1507.1341 | 2179.93 | 0 | 0
|  |  |  | 539 | 1.1529 | 1.2285 | 2.1656 | 3.1782 | 793.7743 | 884.1714 | 1433.943 | 2074.1117 | 0 | 0 | 0 | 1.2136 | 1.2932 | 2.2796 | 3.3455 | 835.5519 | 930.7067 | 1509.4137 | 2183.2755 | 0 | 0
|  |  |  | 540 | 1.1525 | 1.228 | 2.1648 | 3.1772 | 794.9268 | 885.3994 | 1436.1079 | 2077.2889 | 0 | 0 | 0 | 1.2131 | 1.2926 | 2.2788 | 3.3444 | 836.765 | 931.9993 | 1511.6925 | 2186.6199 | 0 | 0
|  |  |  | 541 | 1.152 | 1.2274 | 2.1641 | 3.1762 | 796.0788 | 886.6267 | 1438.2719 | 2080.4651 | 0 | 0 | 0 | 1.2126 | 1.292 | 2.278 | 3.3433 | 837.9777 | 933.2913 | 1513.9705 | 2189.9632 | 0 | 0
|  |  |  | 542 | 1.1515 | 1.2268 | 2.1633 | 3.1751 | 797.2303 | 887.8535 | 1440.4353 | 2083.6402 | 0 | 0 | 0 | 1.2121 | 1.2914 | 2.2772 | 3.3422 | 839.1898 | 934.5827 | 1516.2477 | 2193.3055 | 0 | 0
|  |  |  | 543 | 1.1511 | 1.2262 | 2.1626 | 3.1741 | 798.3814 | 889.0798 | 1442.5979 | 2086.8143 | 0 | 0 | 0 | 1.2117 | 1.2908 | 2.2764 | 3.3412 | 840.4015 | 935.8734 | 1518.5241 | 2196.6467 | 0 | 0
|  |  |  | 544 | 1.1506 | 1.2257 | 2.1618 | 3.1731 | 799.532 | 890.3054 | 1444.7597 | 2089.9874 | 0 | 0 | 0 | 1.2112 | 1.2902 | 2.2756 | 3.3401 | 841.6126 | 937.1636 | 1520.7997 | 2199.9868 | 0 | 0
|  |  |  | 545 | 1.1501 | 1.2251 | 2.1611 | 3.1721 | 800.6821 | 891.5305 | 1446.9208 | 2093.1595 | 0 | 0 | 0 | 1.2107 | 1.2896 | 2.2749 | 3.339 | 842.8233 | 938.4532 | 1523.0745 | 2203.3258 | 0 | 0
|  |  |  | 546 | 1.1497 | 1.2245 | 2.1604 | 3.1711 | 801.8318 | 892.755 | 1449.0812 | 2096.3306 | 0 | 0 | 0 | 1.2102 | 1.289 | 2.2741 | 3.338 | 844.0335 | 939.7421 | 1525.3486 | 2206.6637 | 0 | 0
|  |  |  | 547 | 1.1492 | 1.2239 | 2.1596 | 3.17 | 802.981 | 893.9789 | 1451.2408 | 2099.5006 | 0 | 0 | 0 | 1.2097 | 1.2884 | 2.2733 | 3.3369 | 845.2432 | 941.0305 | 1527.6219 | 2210.0006 | 0 | 0
|  |  |  | 548 | 1.1488 | 1.2234 | 2.1589 | 3.169 | 804.1298 | 895.2023 | 1453.3997 | 2102.6696 | 0 | 0 | 0 | 1.2092 | 1.2878 | 2.2725 | 3.3358 | 846.4524 | 942.3182 | 1529.8944 | 2213.3365 | 0 | 0
|  |  |  | 549 | 1.1483 | 1.2228 | 2.1582 | 3.168 | 805.2781 | 896.4251 | 1455.5579 | 2105.8377 | 0 | 0 | 0 | 1.2087 | 1.2872 | 2.2717 | 3.3348 | 847.6611 | 943.6054 | 1532.1662 | 2216.6712 | 0 | 0
|  |  |  | 550 | 1.1478 | 1.2222 | 2.1574 | 3.167 | 806.4259 | 897.6473 | 1457.7153 | 2109.0047 | 0 | 0 | 0 | 1.2082 | 1.2866 | 2.271 | 3.3337 | 848.8694 | 944.8919 | 1534.4372 | 2220.0049 | 0 | 0
|  |  |  | 551 | 1.1474 | 1.2217 | 2.1567 | 3.166 | 807.5733 | 898.869 | 1459.872 | 2112.1707 | 0 | 0 | 0 | 1.2078 | 1.286 | 2.2702 | 3.3326 | 850.0771 | 946.1779 | 1536.7074 | 2223.3376 | 0 | 0
|  |  |  | 552 | 1.1469 | 1.2211 | 2.156 | 3.165 | 808.7202 | 900.0901 | 1462.0279 | 2115.3357 | 0 | 0 | 0 | 1.2073 | 1.2854 | 2.2694 | 3.3316 | 851.2844 | 947.4633 | 1538.9768 | 2226.6692 | 0 | 0
|  |  |  | 553 | 1.1465 | 1.2205 | 2.1552 | 3.164 | 809.8667 | 901.3107 | 1464.1832 | 2118.4997 | 0 | 0 | 0 | 1.2068 | 1.2848 | 2.2687 | 3.3305 | 852.4912 | 948.7481 | 1541.2455 | 2229.9997 | 0 | 0
|  |  |  | 554 | 1.146 | 1.22 | 2.1545 | 3.163 | 811.0127 | 902.5306 | 1466.3377 | 2121.6627 | 0 | 0 | 0 | 1.2063 | 1.2842 | 2.2679 | 3.3295 | 853.6975 | 950.0322 | 1543.5134 | 2233.3292 | 0 | 0
|  |  |  | 555 | 1.1455 | 1.2194 | 2.1538 | 3.162 | 812.1582 | 903.7501 | 1468.4915 | 2124.8247 | 0 | 0 | 0 | 1.2058 | 1.2836 | 2.2671 | 3.3284 | 854.9034 | 951.3158 | 1545.7805 | 2236.6576 | 0 | 0
|  |  |  | 556 | 1.1451 | 1.2189 | 2.1531 | 3.161 | 813.3033 | 904.9689 | 1470.6445 | 2127.9858 | 0 | 0 | 0 | 1.2054 | 1.283 | 2.2664 | 3.3274 | 856.1087 | 952.5989 | 1548.0469 | 2239.985 | 0 | 0
|  |  |  | 557 | 1.1446 | 1.2183 | 2.1523 | 3.16 | 814.4479 | 906.1872 | 1472.7969 | 2131.1458 | 0 | 0 | 0 | 1.2049 | 1.2824 | 2.2656 | 3.3263 | 857.3136 | 953.8813 | 1550.3125 | 2243.3113 | 0 | 0
|  |  |  | 558 | 1.1442 | 1.2177 | 2.1516 | 3.159 | 815.5921 | 907.405 | 1474.9485 | 2134.3048 | 0 | 0 | 0 | 1.2044 | 1.2818 | 2.2649 | 3.3253 | 858.518 | 955.1631 | 1552.5773 | 2246.6367 | 0 | 0
|  |  |  | 559 | 1.1437 | 1.2172 | 2.1509 | 3.158 | 816.7359 | 908.6221 | 1477.0994 | 2137.4629 | 0 | 0 | 0 | 1.2039 | 1.2813 | 2.2641 | 3.3243 | 859.722 | 956.4444 | 1554.8414 | 2249.9609 | 0 | 0
|  |  |  | 560 | 1.1433 | 1.2166 | 2.1502 | 3.1571 | 817.8792 | 909.8388 | 1479.2495 | 2140.6199 | 0 | 0 | 0 | 1.2035 | 1.2807 | 2.2633 | 3.3232 | 860.9254 | 957.725 | 1557.1048 | 2253.2841 | 0 | 0
|  |  |  | 561 | 1.1428 | 1.2161 | 2.1495 | 3.1561 | 819.022 | 911.0549 | 1481.399 | 2143.776 | 0 | 0 | 0 | 1.203 | 1.2801 | 2.2626 | 3.3222 | 862.1284 | 959.0051 | 1559.3674 | 2256.6063 | 0 | 0
|  |  |  | 562 | 1.1424 | 1.2155 | 2.1487 | 3.1551 | 820.1644 | 912.2704 | 1483.5478 | 2146.9311 | 0 | 0 | 0 | 1.2025 | 1.2795 | 2.2618 | 3.3212 | 863.3309 | 960.2846 | 1561.6292 | 2259.9275 | 0 | 0
|  |  |  | 563 | 1.1419 | 1.215 | 2.148 | 3.1541 | 821.3063 | 913.4854 | 1485.6958 | 2150.0852 | 0 | 0 | 0 | 1.202 | 1.2789 | 2.2611 | 3.3201 | 864.533 | 961.5636 | 1563.8903 | 2263.2476 | 0 | 0
|  |  |  | 564 | 1.1415 | 1.2144 | 2.1473 | 3.1531 | 822.4478 | 914.6998 | 1487.8431 | 2153.2384 | 0 | 0 | 0 | 1.2016 | 1.2783 | 2.2603 | 3.3191 | 865.7346 | 962.8419 | 1566.1506 | 2266.5667 | 0 | 0
|  |  |  | 565 | 1.1411 | 1.2139 | 2.1466 | 3.1522 | 823.5889 | 915.9137 | 1489.9897 | 2156.3905 | 0 | 0 | 0 | 1.2011 | 1.2778 | 2.2596 | 3.3181 | 866.9357 | 964.1197 | 1568.4102 | 2269.8848 | 0 | 0
|  |  |  | 566 | 1.1406 | 1.2133 | 2.1459 | 3.1512 | 824.7295 | 917.127 | 1492.1356 | 2159.5417 | 0 | 0 | 0 | 1.2006 | 1.2772 | 2.2588 | 3.317 | 868.1363 | 965.3969 | 1570.6691 | 2273.2018 | 0 | 0
|  |  |  | 567 | 1.1402 | 1.2128 | 2.1452 | 3.1502 | 825.8697 | 918.3398 | 1494.2808 | 2162.6919 | 0 | 0 | 0 | 1.2002 | 1.2766 | 2.2581 | 3.316 | 869.3365 | 966.6735 | 1572.9272 | 2276.5178 | 0 | 0
|  |  |  | 568 | 1.1397 | 1.2122 | 2.1445 | 3.1492 | 827.0094 | 919.5521 | 1496.4253 | 2165.8412 | 0 | 0 | 0 | 1.1997 | 1.276 | 2.2574 | 3.315 | 870.5362 | 967.9495 | 1575.1845 | 2279.8328 | 0 | 0
|  |  |  | 569 | 1.1393 | 1.2117 | 2.1438 | 3.1483 | 828.1487 | 920.7638 | 1498.5691 | 2168.9895 | 0 | 0 | 0 | 1.1992 | 1.2755 | 2.2566 | 3.314 | 871.7355 | 969.225 | 1577.4411 | 2283.1468 | 0 | 0
|  |  |  | 570 | 1.1388 | 1.2112 | 2.1431 | 3.1473 | 829.2876 | 921.9749 | 1500.7122 | 2172.1368 | 0 | 0 | 0 | 1.1988 | 1.2749 | 2.2559 | 3.313 | 872.9343 | 970.4999 | 1579.697 | 2286.4598 | 0 | 0
|  |  |  | 571 | 1.1384 | 1.2106 | 2.1424 | 3.1464 | 830.426 | 923.1855 | 1502.8545 | 2175.2831 | 0 | 0 | 0 | 1.1983 | 1.2743 | 2.2551 | 3.312 | 874.1326 | 971.7743 | 1581.9522 | 2289.7717 | 0 | 0
|  |  |  | 572 | 1.138 | 1.2101 | 2.1417 | 3.1454 | 831.5639 | 924.3956 | 1504.9962 | 2178.4285 | 0 | 0 | 0 | 1.1979 | 1.2738 | 2.2544 | 3.3109 | 875.3305 | 973.048 | 1584.2066 | 2293.0827 | 0 | 0
|  |  |  | 573 | 1.1375 | 1.2095 | 2.141 | 3.1444 | 832.7015 | 925.6052 | 1507.1372 | 2181.573 | 0 | 0 | 0 | 1.1974 | 1.2732 | 2.2537 | 3.3099 | 876.5279 | 974.3212 | 1586.4602 | 2296.3926 | 0 | 0
|  |  |  | 574 | 1.1371 | 1.209 | 2.1403 | 3.1435 | 833.8386 | 926.8142 | 1509.2775 | 2184.7164 | 0 | 0 | 0 | 1.1969 | 1.2726 | 2.2529 | 3.3089 | 877.7248 | 975.5939 | 1588.7132 | 2299.7015 | 0 | 0
|  |  |  | 575 | 1.1367 | 1.2085 | 2.1396 | 3.1425 | 834.9752 | 928.0226 | 1511.4171 | 2187.859 | 0 | 0 | 0 | 1.1965 | 1.2721 | 2.2522 | 3.3079 | 878.9213 | 976.8659 | 1590.9654 | 2303.0094 | 0 | 0
|  |  |  | 576 | 1.1362 | 1.2079 | 2.1389 | 3.1416 | 836.1114 | 929.2306 | 1513.556 | 2191.0005 | 0 | 0 | 0 | 1.196 | 1.2715 | 2.2515 | 3.3069 | 880.1173 | 978.1374 | 1593.2168 | 2306.3163 | 0 | 0
|  |  |  | 577 | 1.1358 | 1.2074 | 2.1382 | 3.1406 | 837.2472 | 930.438 | 1515.6942 | 2194.1411 | 0 | 0 | 0 | 1.1956 | 1.2709 | 2.2507 | 3.3059 | 881.3129 | 979.4084 | 1595.4676 | 2309.6222 | 0 | 0
|  |  |  | 578 | 1.1354 | 1.2069 | 2.1375 | 3.1397 | 838.3826 | 931.6448 | 1517.8317 | 2197.2808 | 0 | 0 | 0 | 1.1951 | 1.2704 | 2.25 | 3.3049 | 882.508 | 980.6788 | 1597.7176 | 2312.9272 | 0 | 0
|  |  |  | 579 | 1.1349 | 1.2063 | 2.1368 | 3.1387 | 839.5175 | 932.8512 | 1519.9685 | 2200.4195 | 0 | 0 | 0 | 1.1947 | 1.2698 | 2.2493 | 3.3039 | 883.7027 | 981.9486 | 1599.9669 | 2316.2311 | 0 | 0
|  |  |  | 580 | 1.1345 | 1.2058 | 2.1361 | 3.1378 | 840.652 | 934.057 | 1522.1047 | 2203.5573 | 0 | 0 | 0 | 1.1942 | 1.2693 | 2.2486 | 3.3029 | 884.8969 | 983.2179 | 1602.2154 | 2319.534 | 0 | 0
|  |  |  | 581 | 1.1341 | 1.2053 | 2.1354 | 3.1368 | 841.7861 | 935.2623 | 1524.2401 | 2206.6941 | 0 | 0 | 0 | 1.1938 | 1.2687 | 2.2478 | 3.3019 | 886.0906 | 984.4866 | 1604.4633 | 2322.8359 | 0 | 0
|  |  |  | 582 | 1.1336 | 1.2047 | 2.1348 | 3.1359 | 842.9197 | 936.467 | 1526.3749 | 2209.83 | 0 | 0 | 0 | 1.1933 | 1.2682 | 2.2471 | 3.3009 | 887.2839 | 985.7547 | 1606.7104 | 2326.1368 | 0 | 0
|  |  |  | 583 | 1.1332 | 1.2042 | 2.1341 | 3.1349 | 844.0529 | 937.6712 | 1528.5089 | 2212.9649 | 0 | 0 | 0 | 1.1929 | 1.2676 | 2.2464 | 3.2999 | 888.4768 | 987.0223 | 1608.9568 | 2329.4368 | 0 | 0
|  |  |  | 584 | 1.1328 | 1.2037 | 2.1334 | 3.134 | 845.1857 | 938.8749 | 1530.6423 | 2216.0989 | 0 | 0 | 0 | 1.1924 | 1.267 | 2.2457 | 3.299 | 889.6692 | 988.2894 | 1611.2025 | 2332.7357 | 0 | 0
|  |  |  | 585 | 1.1324 | 1.2032 | 2.1327 | 3.1331 | 846.3181 | 940.0781 | 1532.775 | 2219.232 | 0 | 0 | 0 | 1.192 | 1.2665 | 2.245 | 3.298 | 890.8611 | 989.5559 | 1613.4474 | 2336.0337 | 0 | 0
|  |  |  | 586 | 1.1319 | 1.2026 | 2.132 | 3.1321 | 847.45 | 941.2807 | 1534.9071 | 2222.3641 | 0 | 0 | 0 | 1.1915 | 1.2659 | 2.2442 | 3.297 | 892.0526 | 990.8218 | 1615.6917 | 2339.3307 | 0 | 0
|  |  |  | 587 | 1.1315 | 1.2021 | 2.1314 | 3.1312 | 848.5815 | 942.4829 | 1537.0384 | 2225.4953 | 0 | 0 | 0 | 1.1911 | 1.2654 | 2.2435 | 3.296 | 893.2437 | 992.0872 | 1617.9352 | 2342.6267 | 0 | 0
|  |  |  | 588 | 1.1311 | 1.2016 | 2.1307 | 3.1303 | 849.7126 | 943.6845 | 1539.1691 | 2228.6256 | 0 | 0 | 0 | 1.1906 | 1.2648 | 2.2428 | 3.295 | 894.4343 | 993.3521 | 1620.178 | 2345.9217 | 0 | 0
|  |  |  | 589 | 1.1307 | 1.2011 | 2.13 | 3.1293 | 850.8433 | 944.8856 | 1541.2991 | 2231.7549 | 0 | 0 | 0 | 1.1902 | 1.2643 | 2.2421 | 3.294 | 895.6245 | 994.6164 | 1622.4201 | 2349.2157 | 0 | 0
|  |  |  | 590 | 1.1302 | 1.2006 | 2.1293 | 3.1284 | 851.9735 | 946.0861 | 1543.4284 | 2234.8834 | 0 | 0 | 0 | 1.1897 | 1.2638 | 2.2414 | 3.2931 | 896.8142 | 995.8801 | 1624.6615 | 2352.5088 | 0 | 0
|  |  |  | 591 | 1.1298 | 1.2 | 2.1287 | 3.1275 | 853.1033 | 947.2862 | 1545.5571 | 2238.0109 | 0 | 0 | 0 | 1.1893 | 1.2632 | 2.2407 | 3.2921 | 898.0035 | 997.1433 | 1626.9022 | 2355.8009 | 0 | 0
|  |  |  | 592 | 1.1294 | 1.1995 | 2.128 | 3.1266 | 854.2327 | 948.4857 | 1547.6851 | 2241.1374 | 0 | 0 | 0 | 1.1888 | 1.2627 | 2.24 | 3.2911 | 899.1923 | 998.406 | 1629.1422 | 2359.092 | 0 | 0
|  |  |  | 593 | 1.129 | 1.199 | 2.1273 | 3.1256 | 855.3617 | 949.6847 | 1549.8124 | 2244.2631 | 0 | 0 | 0 | 1.1884 | 1.2621 | 2.2393 | 3.2902 | 900.3807 | 999.6681 | 1631.3815 | 2362.3822 | 0 | 0
|  |  |  | 594 | 1.1286 | 1.1985 | 2.1266 | 3.1247 | 856.4903 | 950.8832 | 1551.939 | 2247.3878 | 0 | 0 | 0 | 1.188 | 1.2616 | 2.2386 | 3.2892 | 901.5687 | 1000.9297 | 1633.62 | 2365.6714 | 0 | 0
|  |  |  | 595 | 1.1281 | 1.198 | 2.126 | 3.1238 | 857.6184 | 952.0812 | 1554.065 | 2250.5116 | 0 | 0 | 0 | 1.1875 | 1.261 | 2.2379 | 3.2882 | 902.7562 | 1002.1908 | 1635.8579 | 2368.9596 | 0 | 0
|  |  |  | 596 | 1.1277 | 1.1975 | 2.1253 | 3.1229 | 858.7461 | 953.2787 | 1556.1903 | 2253.6345 | 0 | 0 | 0 | 1.1871 | 1.2605 | 2.2372 | 3.2873 | 903.9433 | 1003.4513 | 1638.0951 | 2372.2468 | 0 | 0
|  |  |  | 597 | 1.1273 | 1.197 | 2.1246 | 3.122 | 859.8734 | 954.4757 | 1558.315 | 2256.7565 | 0 | 0 | 0 | 1.1866 | 1.26 | 2.2365 | 3.2863 | 905.1299 | 1004.7112 | 1640.3315 | 2375.5331 | 0 | 0
|  |  |  | 598 | 1.1269 | 1.1965 | 2.124 | 3.1211 | 861.0003 | 955.6721 | 1560.4389 | 2259.8775 | 0 | 0 | 0 | 1.1862 | 1.2594 | 2.2358 | 3.2853 | 906.3161 | 1005.9706 | 1642.5673 | 2378.8185 | 0 | 0
|  |  |  | 599 | 1.1265 | 1.1959 | 2.1233 | 3.1202 | 862.1268 | 956.868 | 1562.5623 | 2262.9977 | 0 | 0 | 0 | 1.1858 | 1.2589 | 2.2351 | 3.2844 | 907.5019 | 1007.2295 | 1644.8024 | 2382.1028 | 0 | 0
|  |  |  | 600 | 1.1261 | 1.1954 | 2.1227 | 3.1192 | 863.2529 | 958.0635 | 1564.6849 | 2266.1169 | 0 | 0 | 0 | 1.1853 | 1.2584 | 2.2344 | 3.2834 | 908.6872 | 1008.4879 | 1647.0367 | 2385.3862 | 0 | 0
|  |  |  | 601 | 1.1257 | 1.1949 | 2.122 | 3.1183 | 864.3785 | 959.2584 | 1566.8069 | 2269.2353 | 0 | 0 | 0 | 1.1849 | 1.2578 | 2.2337 | 3.2825 | 909.8721 | 1009.7457 | 1649.2704 | 2388.6687 | 0 | 0
|  |  |  | 602 | 1.1252 | 1.1944 | 2.1213 | 3.1174 | 865.5038 | 960.4528 | 1568.9282 | 2272.3527 | 0 | 0 | 0 | 1.1845 | 1.2573 | 2.233 | 3.2815 | 911.0566 | 1011.003 | 1651.5034 | 2391.9502 | 0 | 0
|  |  |  | 603 | 1.1248 | 1.1939 | 2.1207 | 3.1165 | 866.6286 | 961.6468 | 1571.0489 | 2275.4692 | 0 | 0 | 0 | 1.184 | 1.2568 | 2.2323 | 3.2806 | 912.2407 | 1012.2597 | 1653.7357 | 2395.2308 | 0 | 0
|  |  |  | 604 | 1.1244 | 1.1934 | 2.12 | 3.1156 | 867.753 | 962.8402 | 1573.1689 | 2278.5849 | 0 | 0 | 0 | 1.1836 | 1.2562 | 2.2316 | 3.2796 | 913.4243 | 1013.516 | 1655.9673 | 2398.5104 | 0 | 0
|  |  |  | 605 | 1.124 | 1.1929 | 2.1194 | 3.1147 | 868.8771 | 964.0331 | 1575.2883 | 2281.6996 | 0 | 0 | 0 | 1.1832 | 1.2557 | 2.2309 | 3.2787 | 914.6074 | 1014.7717 | 1658.1982 | 2401.789 | 0 | 0
|  |  |  | 606 | 1.1236 | 1.1924 | 2.1187 | 3.1138 | 870.0007 | 965.2255 | 1577.407 | 2284.8134 | 0 | 0 | 0 | 1.1827 | 1.2552 | 2.2302 | 3.2777 | 915.7902 | 1016.0268 | 1660.4285 | 2405.0668 | 0 | 0
|  |  |  | 607 | 1.1232 | 1.1919 | 2.1181 | 3.1129 | 871.1239 | 966.4174 | 1579.5251 | 2287.9264 | 0 | 0 | 0 | 1.1823 | 1.2546 | 2.2295 | 3.2768 | 916.9725 | 1017.2815 | 1662.658 | 2408.3435 | 0 | 0
|  |  |  | 608 | 1.1228 | 1.1914 | 2.1174 | 3.112 | 872.2466 | 967.6088 | 1581.6425 | 2291.0384 | 0 | 0 | 0 | 1.1819 | 1.2541 | 2.2289 | 3.2758 | 918.1544 | 1018.5356 | 1664.8869 | 2411.6194 | 0 | 0
|  |  |  | 609 | 1.1224 | 1.1909 | 2.1168 | 3.1111 | 873.369 | 968.7997 | 1583.7593 | 2294.1495 | 0 | 0 | 0 | 1.1815 | 1.2536 | 2.2282 | 3.2749 | 919.3358 | 1019.7892 | 1667.115 | 2414.8942 | 0 | 0
|  |  |  | 610 | 1.122 | 1.1904 | 2.1161 | 3.1103 | 874.491 | 969.9901 | 1585.8754 | 2297.2598 | 0 | 0 | 0 | 1.181 | 1.2531 | 2.2275 | 3.274 | 920.5169 | 1021.0422 | 1669.3425 | 2418.1682 | 0 | 0
|  |  |  | 611 | 1.1216 | 1.1899 | 2.1155 | 3.1094 | 875.6126 | 971.18 | 1587.9909 | 2300.3692 | 0 | 0 | 0 | 1.1806 | 1.2525 | 2.2268 | 3.273 | 921.6975 | 1022.2948 | 1671.5693 | 2421.4412 | 0 | 0
|  |  |  | 612 | 1.1212 | 1.1894 | 2.1148 | 3.1085 | 876.7338 | 972.3695 | 1590.1057 | 2303.4776 | 0 | 0 | 0 | 1.1802 | 1.252 | 2.2261 | 3.2721 | 922.8776 | 1023.5468 | 1673.7955 | 2424.7133 | 0 | 0
|  |  |  | 613 | 1.1208 | 1.1889 | 2.1142 | 3.1076 | 877.8545 | 973.5584 | 1592.2199 | 2306.5852 | 0 | 0 | 0 | 1.1798 | 1.2515 | 2.2255 | 3.2711 | 924.0574 | 1024.7983 | 1676.0209 | 2427.9844 | 0 | 0
|  |  |  | 614 | 1.1204 | 1.1884 | 2.1135 | 3.1067 | 878.9749 | 974.7468 | 1594.3334 | 2309.6919 | 0 | 0 | 0 | 1.1793 | 1.251 | 2.2248 | 3.2702 | 925.2367 | 1026.0493 | 1678.2457 | 2431.2547 | 0 | 0
|  |  |  | 615 | 1.12 | 1.1879 | 2.1129 | 3.1058 | 880.0949 | 975.9348 | 1596.4463 | 2312.7978 | 0 | 0 | 0 | 1.1789 | 1.2505 | 2.2241 | 3.2693 | 926.4157 | 1027.2997 | 1680.4698 | 2434.524 | 0 | 0
|  |  |  | 616 | 1.1196 | 1.1874 | 2.1123 | 3.1049 | 881.2144 | 977.1222 | 1598.5586 | 2315.9027 | 0 | 0 | 0 | 1.1785 | 1.2499 | 2.2234 | 3.2684 | 927.5941 | 1028.5497 | 1682.6932 | 2437.7923 | 0 | 0
|  |  |  | 617 | 1.1192 | 1.187 | 2.1116 | 3.1041 | 882.3336 | 978.3092 | 1600.6702 | 2319.0068 | 0 | 0 | 0 | 1.1781 | 1.2494 | 2.2228 | 3.2674 | 928.7722 | 1029.7991 | 1684.916 | 2441.0598 | 0 | 0
|  |  |  | 618 | 1.1188 | 1.1865 | 2.111 | 3.1032 | 883.4524 | 979.4956 | 1602.7812 | 2322.11 | 0 | 0 | 0 | 1.1777 | 1.2489 | 2.2221 | 3.2665 | 929.9499 | 1031.048 | 1687.1381 | 2444.3263 | 0 | 0
|  |  |  | 619 | 1.1184 | 1.186 | 2.1103 | 3.1023 | 884.5707 | 980.6816 | 1604.8915 | 2325.2123 | 0 | 0 | 0 | 1.1772 | 1.2484 | 2.2214 | 3.2656 | 931.1271 | 1032.2964 | 1689.3595 | 2447.5919 | 0 | 0
|  |  |  | 620 | 1.118 | 1.1855 | 2.1097 | 3.1014 | 885.6887 | 981.8671 | 1607.0012 | 2328.3137 | 0 | 0 | 0 | 1.1768 | 1.2479 | 2.2207 | 3.2647 | 932.3039 | 1033.5443 | 1691.5802 | 2450.8565 | 0 | 0
|  |  |  | 621 | 1.1176 | 1.185 | 2.1091 | 3.1006 | 886.8063 | 983.0521 | 1609.1103 | 2331.4143 | 0 | 0 | 0 | 1.1764 | 1.2474 | 2.2201 | 3.2638 | 933.4803 | 1034.7917 | 1693.8003 | 2454.1203 | 0 | 0
|  |  |  | 622 | 1.1172 | 1.1845 | 2.1084 | 3.0997 | 887.9235 | 984.2366 | 1611.2187 | 2334.514 | 0 | 0 | 0 | 1.176 | 1.2469 | 2.2194 | 3.2628 | 934.6563 | 1036.0386 | 1696.0197 | 2457.3831 | 0 | 0
|  |  |  | 623 | 1.1168 | 1.184 | 2.1078 | 3.0988 | 889.0403 | 985.4207 | 1613.3265 | 2337.6128 | 0 | 0 | 0 | 1.1756 | 1.2464 | 2.2187 | 3.2619 | 935.8319 | 1037.2849 | 1698.2384 | 2460.645 | 0 | 0
|  |  |  | 624 | 1.1164 | 1.1836 | 2.1072 | 3.098 | 890.1567 | 986.6042 | 1615.4337 | 2340.7107 | 0 | 0 | 0 | 1.1752 | 1.2458 | 2.2181 | 3.261 | 937.007 | 1038.5307 | 1700.4565 | 2463.906 | 0 | 0
|  |  |  | 625 | 1.116 | 1.1831 | 2.1065 | 3.0971 | 891.2727 | 987.7873 | 1617.5402 | 2343.8078 | 0 | 0 | 0 | 1.1747 | 1.2453 | 2.2174 | 3.2601 | 938.1817 | 1039.7761 | 1702.6739 | 2467.1661 | 0 | 0
|  |  |  | 626 | 1.1156 | 1.1826 | 2.1059 | 3.0962 | 892.3883 | 988.9699 | 1619.6462 | 2346.9041 | 0 | 0 | 0 | 1.1743 | 1.2448 | 2.2168 | 3.2592 | 939.3561 | 1041.0209 | 1704.8907 | 2470.4253 | 0 | 0
|  |  |  | 627 | 1.1152 | 1.1821 | 2.1053 | 3.0954 | 893.5035 | 990.152 | 1621.7515 | 2349.9994 | 0 | 0 | 0 | 1.1739 | 1.2443 | 2.2161 | 3.2583 | 940.53 | 1042.2652 | 1707.1068 | 2473.6836 | 0 | 0
|  |  |  | 628 | 1.1148 | 1.1816 | 2.1047 | 3.0945 | 894.6183 | 991.3336 | 1623.8561 | 2353.0939 | 0 | 0 | 0 | 1.1735 | 1.2438 | 2.2154 | 3.2574 | 941.7035 | 1043.509 | 1709.3222 | 2476.941 | 0 | 0
|  |  |  | 629 | 1.1144 | 1.1811 | 2.104 | 3.0936 | 895.7327 | 992.5147 | 1625.9602 | 2356.1876 | 0 | 0 | 0 | 1.1731 | 1.2433 | 2.2148 | 3.2565 | 942.8766 | 1044.7524 | 1711.537 | 2480.1974 | 0 | 0
|  |  |  | 630 | 1.114 | 1.1807 | 2.1034 | 3.0928 | 896.8468 | 993.6954 | 1628.0636 | 2359.2804 | 0 | 0 | 0 | 1.1727 | 1.2428 | 2.2141 | 3.2556 | 944.0493 | 1045.9952 | 1713.7511 | 2483.453 | 0 | 0
|  |  |  | 631 | 1.1137 | 1.1802 | 2.1028 | 3.0919 | 897.9604 | 994.8756 | 1630.1664 | 2362.3723 | 0 | 0 | 0 | 1.1723 | 1.2423 | 2.2135 | 3.2547 | 945.2215 | 1047.2375 | 1715.9646 | 2486.7077 | 0 | 0
|  |  |  | 632 | 1.1133 | 1.1797 | 2.1022 | 3.0911 | 899.0737 | 996.0553 | 1632.2685 | 2365.4634 | 0 | 0 | 0 | 1.1719 | 1.2418 | 2.2128 | 3.2538 | 946.3934 | 1048.4793 | 1718.1774 | 2489.9614 | 0 | 0
|  |  |  | 633 | 1.1129 | 1.1792 | 2.1016 | 3.0902 | 900.1866 | 997.2346 | 1634.3701 | 2368.5536 | 0 | 0 | 0 | 1.1715 | 1.2413 | 2.2122 | 3.2529 | 947.5648 | 1049.7206 | 1720.3896 | 2493.2143 | 0 | 0
|  |  |  | 634 | 1.1125 | 1.1788 | 2.1009 | 3.0894 | 901.2991 | 998.4133 | 1636.471 | 2371.643 | 0 | 0 | 0 | 1.171 | 1.2408 | 2.2115 | 3.252 | 948.7359 | 1050.9614 | 1722.6011 | 2496.4663 | 0 | 0
|  |  |  | 635 | 1.1121 | 1.1783 | 2.1003 | 3.0885 | 902.4112 | 999.5916 | 1638.5713 | 2374.7315 | 0 | 0 | 0 | 1.1706 | 1.2403 | 2.2109 | 3.2511 | 949.9065 | 1052.2017 | 1724.8119 | 2499.7173 | 0 | 0
|  |  |  | 636 | 1.1117 | 1.1778 | 2.0997 | 3.0877 | 903.5229 | 1000.7694 | 1640.671 | 2377.8191 | 0 | 0 | 0 | 1.1702 | 1.2398 | 2.2102 | 3.2502 | 951.0768 | 1053.4415 | 1727.0221 | 2502.9675 | 0 | 0
|  |  |  | 637 | 1.1113 | 1.1773 | 2.0991 | 3.0868 | 904.6343 | 1001.9468 | 1642.7701 | 2380.906 | 0 | 0 | 0 | 1.1698 | 1.2393 | 2.2096 | 3.2493 | 952.2466 | 1054.6808 | 1729.2317 | 2506.2168 | 0 | 0
|  |  |  | 638 | 1.111 | 1.1769 | 2.0985 | 3.086 | 905.7452 | 1003.1237 | 1644.8686 | 2383.992 | 0 | 0 | 0 | 1.1694 | 1.2388 | 2.2089 | 3.2484 | 953.416 | 1055.9196 | 1731.4406 | 2509.4652 | 0 | 0
|  |  |  | 639 | 1.1106 | 1.1764 | 2.0979 | 3.0851 | 906.8558 | 1004.3001 | 1646.9664 | 2387.0771 | 0 | 0 | 0 | 1.169 | 1.2383 | 2.2083 | 3.2475 | 954.585 | 1057.158 | 1733.6489 | 2512.7127 | 0 | 0
|  |  |  | 640 | 1.1102 | 1.1759 | 2.0972 | 3.0843 | 907.966 | 1005.476 | 1649.0637 | 2390.1614 | 0 | 0 | 0 | 1.1686 | 1.2378 | 2.2076 | 3.2466 | 955.7537 | 1058.3958 | 1735.8565 | 2515.9594 | 0 | 0
|  |  |  | 641 | 1.1098 | 1.1755 | 2.0966 | 3.0835 | 909.0758 | 1006.6515 | 1651.1603 | 2393.2448 | 0 | 0 | 0 | 1.1682 | 1.2373 | 2.207 | 3.2457 | 956.9219 | 1059.6331 | 1738.0635 | 2519.2051 | 0 | 0
|  |  |  | 642 | 1.1094 | 1.175 | 2.096 | 3.0826 | 910.1852 | 1007.8265 | 1653.2563 | 2396.3275 | 0 | 0 | 0 | 1.1678 | 1.2368 | 2.2063 | 3.2449 | 958.0897 | 1060.87 | 1740.2698 | 2522.45 | 0 | 0
|  |  |  | 643 | 1.1091 | 1.1745 | 2.0954 | 3.0818 | 911.2943 | 1009.001 | 1655.3518 | 2399.4092 | 0 | 0 | 0 | 1.1674 | 1.2364 | 2.2057 | 3.244 | 959.2571 | 1062.1063 | 1742.4755 | 2525.6939 | 0 | 0
|  |  |  | 644 | 1.1087 | 1.1741 | 2.0948 | 3.0809 | 912.403 | 1010.1751 | 1657.4466 | 2402.4902 | 0 | 0 | 0 | 1.167 | 1.2359 | 2.2051 | 3.2431 | 960.4242 | 1063.3422 | 1744.6806 | 2528.937 | 0 | 0
|  |  |  | 645 | 1.1083 | 1.1736 | 2.0942 | 3.0801 | 913.5112 | 1011.3487 | 1659.5408 | 2405.5703 | 0 | 0 | 0 | 1.1666 | 1.2354 | 2.2044 | 3.2422 | 961.5908 | 1064.5776 | 1746.885 | 2532.1792 | 0 | 0
|  |  |  | 646 | 1.1079 | 1.1731 | 2.0936 | 3.0793 | 914.6192 | 1012.5219 | 1661.6344 | 2408.6496 | 0 | 0 | 0 | 1.1662 | 1.2349 | 2.2038 | 3.2413 | 962.757 | 1065.8125 | 1749.0888 | 2535.4206 | 0 | 0
|  |  |  | 647 | 1.1075 | 1.1727 | 2.093 | 3.0784 | 915.7267 | 1013.6945 | 1663.7274 | 2411.728 | 0 | 0 | 0 | 1.1658 | 1.2344 | 2.2031 | 3.2405 | 963.9228 | 1067.0469 | 1751.292 | 2538.6611 | 0 | 0
|  |  |  | 648 | 1.1072 | 1.1722 | 2.0924 | 3.0776 | 916.8339 | 1014.8668 | 1665.8197 | 2414.8056 | 0 | 0 | 0 | 1.1654 | 1.2339 | 2.2025 | 3.2396 | 965.0883 | 1068.2808 | 1753.4945 | 2541.9007 | 0 | 0
|  |  |  | 649 | 1.1068 | 1.1718 | 2.0918 | 3.0768 | 917.9406 | 1016.0385 | 1667.9115 | 2417.8824 | 0 | 0 | 0 | 1.165 | 1.2334 | 2.2019 | 3.2387 | 966.2533 | 1069.5142 | 1755.6963 | 2545.1394 | 0 | 0
|  |  |  | 650 | 1.1064 | 1.1713 | 2.0912 | 3.076 | 919.0471 | 1017.2098 | 1670.0027 | 2420.9584 | 0 | 0 | 0 | 1.1646 | 1.233 | 2.2012 | 3.2379 | 967.418 | 1070.7472 | 1757.8976 | 2548.3772 | 0 | 0
|  |  |  | 651 | 1.106 | 1.1708 | 2.0906 | 3.0751 | 920.1531 | 1018.3807 | 1672.0933 | 2424.0335 | 0 | 0 | 0 | 1.1643 | 1.2325 | 2.2006 | 3.237 | 968.5822 | 1071.9797 | 1760.0982 | 2551.6142 | 0 | 0
|  |  |  | 652 | 1.1057 | 1.1704 | 2.09 | 3.0743 | 921.2588 | 1019.5511 | 1674.1833 | 2427.1078 | 0 | 0 | 0 | 1.1639 | 1.232 | 2.2 | 3.2361 | 969.7461 | 1073.2117 | 1762.2982 | 2554.8503 | 0 | 0
|  |  |  | 653 | 1.1053 | 1.1699 | 2.0894 | 3.0735 | 922.3641 | 1020.721 | 1676.2727 | 2430.1813 | 0 | 0 | 0 | 1.1635 | 1.2315 | 2.1994 | 3.2353 | 970.9095 | 1074.4432 | 1764.4976 | 2558.0856 | 0 | 0
|  |  |  | 654 | 1.1049 | 1.1695 | 2.0888 | 3.0727 | 923.469 | 1021.8905 | 1678.3615 | 2433.254 | 0 | 0 | 0 | 1.1631 | 1.231 | 2.1987 | 3.2344 | 972.0726 | 1075.6742 | 1766.6963 | 2561.32 | 0 | 0
|  |  |  | 655 | 1.1045 | 1.169 | 2.0882 | 3.0718 | 924.5735 | 1023.0595 | 1680.4497 | 2436.3258 | 0 | 0 | 0 | 1.1627 | 1.2305 | 2.1981 | 3.2335 | 973.2353 | 1076.9047 | 1768.8944 | 2564.5535 | 0 | 0
|  |  |  | 656 | 1.1042 | 1.1686 | 2.0876 | 3.071 | 925.6777 | 1024.2281 | 1682.5373 | 2439.3968 | 0 | 0 | 0 | 1.1623 | 1.2301 | 2.1975 | 3.2327 | 974.3976 | 1078.1348 | 1771.0919 | 2567.7862 | 0 | 0
|  |  |  | 657 | 1.1038 | 1.1681 | 2.087 | 3.0702 | 926.7815 | 1025.3962 | 1684.6243 | 2442.4671 | 0 | 0 | 0 | 1.1619 | 1.2296 | 2.1969 | 3.2318 | 975.5595 | 1079.3644 | 1773.2887 | 2571.018 | 0 | 0
|  |  |  | 658 | 1.1034 | 1.1677 | 2.0864 | 3.0694 | 927.8849 | 1026.5638 | 1686.7107 | 2445.5365 | 0 | 0 | 0 | 1.1615 | 1.2291 | 2.1962 | 3.2309 | 976.721 | 1080.5935 | 1775.485 | 2574.2489 | 0 | 0
|  |  |  | 659 | 1.1031 | 1.1672 | 2.0858 | 3.0686 | 928.988 | 1027.731 | 1688.7965 | 2448.605 | 0 | 0 | 0 | 1.1611 | 1.2286 | 2.1956 | 3.2301 | 977.8821 | 1081.8222 | 1777.6806 | 2577.479 | 0 | 0
|  |  |  | 660 | 1.1027 | 1.1668 | 2.0852 | 3.0678 | 930.0907 | 1028.8978 | 1690.8818 | 2451.6728 | 0 | 0 | 0 | 1.1607 | 1.2282 | 2.195 | 3.2292 | 979.0429 | 1083.0503 | 1779.8755 | 2580.7082 | 0 | 0
|  |  |  | 661 | 1.1023 | 1.1663 | 2.0846 | 3.067 | 931.1931 | 1030.0641 | 1692.9664 | 2454.7398 | 0 | 0 | 0 | 1.1604 | 1.2277 | 2.1944 | 3.2284 | 980.2032 | 1084.278 | 1782.0699 | 2583.9366 | 0 | 0
|  |  |  | 662 | 1.102 | 1.1659 | 2.0841 | 3.0662 | 932.295 | 1031.23 | 1695.0505 | 2457.8059 | 0 | 0 | 0 | 1.16 | 1.2272 | 2.1937 | 3.2275 | 981.3632 | 1085.5052 | 1784.2637 | 2587.1641 | 0 | 0
|  |  |  | 663 | 1.1016 | 1.1654 | 2.0835 | 3.0653 | 933.3966 | 1032.3954 | 1697.134 | 2460.8713 | 0 | 0 | 0 | 1.1596 | 1.2267 | 2.1931 | 3.2267 | 982.5228 | 1086.732 | 1786.4568 | 2590.3908 | 0 | 0
|  |  |  | 664 | 1.1012 | 1.165 | 2.0829 | 3.0645 | 934.4979 | 1033.5603 | 1699.2168 | 2463.9358 | 0 | 0 | 0 | 1.1592 | 1.2263 | 2.1925 | 3.2258 | 983.682 | 1087.9583 | 1788.6493 | 2593.6167 | 0 | 0
|  |  |  | 665 | 1.1009 | 1.1645 | 2.0823 | 3.0637 | 935.5987 | 1034.7249 | 1701.2991 | 2466.9996 | 0 | 0 | 0 | 1.1588 | 1.2258 | 2.1919 | 3.225 | 984.8408 | 1089.1841 | 1790.8412 | 2596.8416 | 0 | 0
|  |  |  | 666 | 1.1005 | 1.1641 | 2.0817 | 3.0629 | 936.6992 | 1035.8889 | 1703.3809 | 2470.0625 | 0 | 0 | 0 | 1.1584 | 1.2253 | 2.1913 | 3.2241 | 985.9992 | 1090.4094 | 1793.0325 | 2600.0658 | 0 | 0
|  |  |  | 667 | 1.1001 | 1.1636 | 2.0811 | 3.0621 | 937.7994 | 1037.0526 | 1705.462 | 2473.1246 | 0 | 0 | 0 | 1.158 | 1.2249 | 2.1907 | 3.2233 | 987.1573 | 1091.6343 | 1795.2232 | 2603.2891 | 0 | 0
|  |  |  | 668 | 1.0998 | 1.1632 | 2.0806 | 3.0613 | 938.8992 | 1038.2157 | 1707.5426 | 2476.186 | 0 | 0 | 0 | 1.1577 | 1.2244 | 2.1901 | 3.2225 | 988.3149 | 1092.8587 | 1797.4132 | 2606.5115 | 0 | 0
|  |  |  | 669 | 1.0994 | 1.1627 | 2.08 | 3.0605 | 939.9986 | 1039.3785 | 1709.6225 | 2479.2465 | 0 | 0 | 0 | 1.1573 | 1.2239 | 2.1894 | 3.2216 | 989.4722 | 1094.0826 | 1799.6027 | 2609.7331 | 0 | 0
|  |  |  | 670 | 1.0991 | 1.1623 | 2.0794 | 3.0597 | 941.0977 | 1040.5408 | 1711.7019 | 2482.3062 | 0 | 0 | 0 | 1.1569 | 1.2235 | 2.1888 | 3.2208 | 990.6291 | 1095.3061 | 1801.7915 | 2612.9539 | 0 | 0
|  |  |  | 671 | 1.0987 | 1.1619 | 2.0788 | 3.0589 | 942.1964 | 1041.7026 | 1713.7808 | 2485.3652 | 0 | 0 | 0 | 1.1565 | 1.223 | 2.1882 | 3.2199 | 991.7856 | 1096.5291 | 1803.9797 | 2616.1739 | 0 | 0
|  |  |  | 672 | 1.0983 | 1.1614 | 2.0782 | 3.0581 | 943.2947 | 1042.864 | 1715.859 | 2488.4233 | 0 | 0 | 0 | 1.1561 | 1.2225 | 2.1876 | 3.2191 | 992.9418 | 1097.7516 | 1806.1674 | 2619.393 | 0 | 0
|  |  |  | 673 | 1.098 | 1.161 | 2.0777 | 3.0573 | 944.3927 | 1044.025 | 1717.9367 | 2491.4807 | 0 | 0 | 0 | 1.1558 | 1.2221 | 2.187 | 3.2183 | 994.0976 | 1098.9737 | 1808.3544 | 2622.6112 | 0 | 0
|  |  |  | 674 | 1.0976 | 1.1605 | 2.0771 | 3.0566 | 945.4903 | 1045.1855 | 1720.0138 | 2494.5372 | 0 | 0 | 0 | 1.1554 | 1.2216 | 2.1864 | 3.2174 | 995.2529 | 1100.1953 | 1810.5408 | 2625.8286 | 0 | 0
|  |  |  | 675 | 1.0973 | 1.1601 | 2.0765 | 3.0558 | 946.5876 | 1046.3456 | 1722.0903 | 2497.593 | 0 | 0 | 0 | 1.155 | 1.2212 | 2.1858 | 3.2166 | 996.408 | 1101.4165 | 1812.7266 | 2629.0452 | 0 | 0
|  |  |  | 676 | 1.0969 | 1.1597 | 2.0759 | 3.055 | 947.6845 | 1047.5053 | 1724.1662 | 2500.648 | 0 | 0 | 0 | 1.1546 | 1.2207 | 2.1852 | 3.2158 | 997.5626 | 1102.6372 | 1814.9118 | 2632.261 | 0 | 0
|  |  |  | 677 | 1.0965 | 1.1592 | 2.0754 | 3.0542 | 948.781 | 1048.6645 | 1726.2416 | 2503.7021 | 0 | 0 | 0 | 1.1543 | 1.2202 | 2.1846 | 3.2149 | 998.7169 | 1103.8574 | 1817.0964 | 2635.4759 | 0 | 0
|  |  |  | 678 | 1.0962 | 1.1588 | 2.0748 | 3.0534 | 949.8772 | 1049.8233 | 1728.3164 | 2506.7555 | 0 | 0 | 0 | 1.1539 | 1.2198 | 2.184 | 3.2141 | 999.8707 | 1105.0772 | 1819.2804 | 2638.6901 | 0 | 0
|  |  |  | 679 | 1.0958 | 1.1584 | 2.0742 | 3.0526 | 950.973 | 1050.9817 | 1730.3906 | 2509.8082 | 0 | 0 | 0 | 1.1535 | 1.2193 | 2.1834 | 3.2133 | 1001.0243 | 1106.2965 | 1821.4638 | 2641.9033 | 0 | 0
|  |  |  | 680 | 1.0955 | 1.1579 | 2.0737 | 3.0518 | 952.0685 | 1052.1396 | 1732.4643 | 2512.86 | 0 | 0 | 0 | 1.1531 | 1.2189 | 2.1828 | 3.2125 | 1002.1774 | 1107.5153 | 1823.6466 | 2645.1158 | 0 | 0
|  |  |  | 681 | 1.0951 | 1.1575 | 2.0731 | 3.0511 | 953.1637 | 1053.2971 | 1734.5374 | 2515.9111 | 0 | 0 | 0 | 1.1528 | 1.2184 | 2.1822 | 3.2116 | 1003.3302 | 1108.7337 | 1825.8288 | 2648.3274 | 0 | 0
|  |  |  | 682 | 1.0948 | 1.1571 | 2.0725 | 3.0503 | 954.2584 | 1054.4541 | 1736.6099 | 2518.9613 | 0 | 0 | 0 | 1.1524 | 1.2179 | 2.1816 | 3.2108 | 1004.4826 | 1109.9517 | 1828.0104 | 2651.5382 | 0 | 0
|  |  |  | 683 | 1.0944 | 1.1566 | 2.072 | 3.0495 | 955.3529 | 1055.6107 | 1738.6818 | 2522.0108 | 0 | 0 | 0 | 1.152 | 1.2175 | 2.181 | 3.21 | 1005.6346 | 1111.1692 | 1830.1914 | 2654.7482 | 0 | 0
|  |  |  | 684 | 1.0941 | 1.1562 | 2.0714 | 3.0487 | 956.4469 | 1056.7669 | 1740.7532 | 2525.0595 | 0 | 0 | 0 | 1.1517 | 1.217 | 2.1804 | 3.2092 | 1006.7862 | 1112.3862 | 1832.3718 | 2657.9574 | 0 | 0
|  |  |  | 685 | 1.0937 | 1.1558 | 2.0708 | 3.0479 | 957.5406 | 1057.9227 | 1742.8241 | 2528.1075 | 0 | 0 | 0 | 1.1513 | 1.2166 | 2.1798 | 3.2084 | 1007.9375 | 1113.6028 | 1834.5516 | 2661.1658 | 0 | 0
|  |  |  | 686 | 1.0934 | 1.1553 | 2.0703 | 3.0472 | 958.634 | 1059.078 | 1744.8943 | 2531.1546 | 0 | 0 | 0 | 1.1509 | 1.2161 | 2.1792 | 3.2075 | 1009.0884 | 1114.819 | 1836.7309 | 2664.3733 | 0 | 0
|  |  |  | 687 | 1.093 | 1.1549 | 2.0697 | 3.0464 | 959.727 | 1060.2329 | 1746.964 | 2534.201 | 0 | 0 | 0 | 1.1505 | 1.2157 | 2.1786 | 3.2067 | 1010.239 | 1116.0346 | 1838.9095 | 2667.58 | 0 | 0
|  |  |  | 688 | 1.0927 | 1.1545 | 2.0691 | 3.0456 | 960.8197 | 1061.3874 | 1749.0332 | 2537.2466 | 0 | 0 | 0 | 1.1502 | 1.2152 | 2.178 | 3.2059 | 1011.3892 | 1117.2499 | 1841.0875 | 2670.7859 | 0 | 0
|  |  |  | 689 | 1.0923 | 1.154 | 2.0686 | 3.0448 | 961.912 | 1062.5414 | 1751.1017 | 2540.2915 | 0 | 0 | 0 | 1.1498 | 1.2148 | 2.1775 | 3.2051 | 1012.539 | 1118.4647 | 1843.265 | 2673.991 | 0 | 0
|  |  |  | 690 | 1.092 | 1.1536 | 2.068 | 3.0441 | 963.004 | 1063.695 | 1753.1698 | 2543.3355 | 0 | 0 | 0 | 1.1494 | 1.2143 | 2.1769 | 3.2043 | 1013.6884 | 1119.679 | 1845.4419 | 2677.1953 | 0 | 0
|  |  |  | 691 | 1.0916 | 1.1532 | 2.0675 | 3.0433 | 964.0956 | 1064.8482 | 1755.2372 | 2546.3788 | 0 | 0 | 0 | 1.1491 | 1.2139 | 2.1763 | 3.2035 | 1014.8375 | 1120.8929 | 1847.6181 | 2680.3988 | 0 | 0
|  |  |  | 692 | 1.0913 | 1.1528 | 2.0669 | 3.0425 | 965.1869 | 1066.001 | 1757.3041 | 2549.4214 | 0 | 0 | 0 | 1.1487 | 1.2134 | 2.1757 | 3.2027 | 1015.9862 | 1122.1063 | 1849.7938 | 2683.6014 | 0 | 0
|  |  |  | 693 | 1.0909 | 1.1523 | 2.0663 | 3.0418 | 966.2778 | 1067.1533 | 1759.3705 | 2552.4631 | 0 | 0 | 0 | 1.1483 | 1.213 | 2.1751 | 3.2019 | 1017.1345 | 1123.3193 | 1851.9689 | 2686.8033 | 0 | 0
|  |  |  | 694 | 1.0906 | 1.1519 | 2.0658 | 3.041 | 967.3684 | 1068.3053 | 1761.4363 | 2555.5041 | 0 | 0 | 0 | 1.148 | 1.2125 | 2.1745 | 3.2011 | 1018.2825 | 1124.5319 | 1854.1434 | 2690.0044 | 0 | 0
|  |  |  | 695 | 1.0902 | 1.1515 | 2.0652 | 3.0402 | 968.4586 | 1069.4568 | 1763.5015 | 2558.5444 | 0 | 0 | 0 | 1.1476 | 1.2121 | 2.1739 | 3.2003 | 1019.4301 | 1125.744 | 1856.3174 | 2693.2046 | 0 | 0
|  |  |  | 696 | 1.0899 | 1.1511 | 2.0647 | 3.0395 | 969.5485 | 1070.6078 | 1765.5662 | 2561.5839 | 0 | 0 | 0 | 1.1473 | 1.2117 | 2.1734 | 3.1994 | 1020.5774 | 1126.9556 | 1858.4907 | 2696.4041 | 0 | 0
|  |  |  | 697 | 1.0895 | 1.1507 | 2.0641 | 3.0387 | 970.6381 | 1071.7585 | 1767.6303 | 2564.6226 | 0 | 0 | 0 | 1.1469 | 1.2112 | 2.1728 | 3.1986 | 1021.7243 | 1128.1668 | 1860.6635 | 2699.6027 | 0 | 0
|  |  |  | 698 | 1.0892 | 1.1502 | 2.0636 | 3.038 | 971.7273 | 1072.9087 | 1769.6939 | 2567.6605 | 0 | 0 | 0 | 1.1465 | 1.2108 | 2.1722 | 3.1978 | 1022.8708 | 1129.3776 | 1862.8357 | 2702.8005 | 0 | 0
|  |  |  | 699 | 1.0889 | 1.1498 | 2.063 | 3.0372 | 972.8162 | 1074.0585 | 1771.7569 | 2570.6977 | 0 | 0 | 0 | 1.1462 | 1.2103 | 2.1716 | 3.197 | 1024.017 | 1130.5879 | 1865.0073 | 2705.9976 | 0 | 0
|  |  |  | 700 | 1.0885 | 1.1494 | 2.0625 | 3.0364 | 973.9047 | 1075.2079 | 1773.8194 | 2573.7342 | 0 | 0 | 0 | 1.1458 | 1.2099 | 2.171 | 3.1963 | 1025.1628 | 1131.7978 | 1867.1783 | 2709.1938 | 0 | 0
|  |  |  | 701 | 1.0882 | 1.149 | 2.0619 | 3.0357 | 974.9928 | 1076.3569 | 1775.8813 | 2576.7698 | 0 | 0 | 0 | 1.1455 | 1.2095 | 2.1705 | 3.1955 | 1026.3083 | 1133.0073 | 1869.3488 | 2712.3893 | 0 | 0
|  |  |  | 702 | 1.0878 | 1.1486 | 2.0614 | 3.0349 | 976.0807 | 1077.5055 | 1777.9427 | 2579.8048 | 0 | 0 | 0 | 1.1451 | 1.209 | 2.1699 | 3.1947 | 1027.4534 | 1134.2163 | 1871.5187 | 2715.584 | 0 | 0
|  |  |  | 703 | 1.0875 | 1.1481 | 2.0608 | 3.0342 | 977.1682 | 1078.6536 | 1780.0036 | 2582.8389 | 0 | 0 | 0 | 1.1447 | 1.2086 | 2.1693 | 3.1939 | 1028.5981 | 1135.4249 | 1873.688 | 2718.7778 | 0 | 0
|  |  |  | 704 | 1.0872 | 1.1477 | 2.0603 | 3.0334 | 978.2553 | 1079.8014 | 1782.0639 | 2585.8724 | 0 | 0 | 0 | 1.1444 | 1.2081 | 2.1687 | 3.1931 | 1029.7425 | 1136.633 | 1875.8567 | 2721.9709 | 0 | 0
|  |  |  | 705 | 1.0868 | 1.1473 | 2.0597 | 3.0327 | 979.3422 | 1080.9487 | 1784.1236 | 2588.905 | 0 | 0 | 0 | 1.144 | 1.2077 | 2.1682 | 3.1923 | 1030.8865 | 1137.8407 | 1878.0248 | 2725.1632 | 0 | 0
|  |  |  | 706 | 1.0865 | 1.1469 | 2.0592 | 3.0319 | 980.4286 | 1082.0956 | 1786.1828 | 2591.937 | 0 | 0 | 0 | 1.1437 | 1.2073 | 2.1676 | 3.1915 | 1032.0301 | 1139.048 | 1880.1924 | 2728.3547 | 0 | 0
|  |  |  | 707 | 1.0861 | 1.1465 | 2.0587 | 3.0312 | 981.5148 | 1083.2421 | 1788.2414 | 2594.9681 | 0 | 0 | 0 | 1.1433 | 1.2068 | 2.167 | 3.1907 | 1033.1734 | 1140.2548 | 1882.3594 | 2731.5454 | 0 | 0
|  |  |  | 708 | 1.0858 | 1.1461 | 2.0581 | 3.0304 | 982.6006 | 1084.3881 | 1790.2996 | 2597.9986 | 0 | 0 | 0 | 1.1429 | 1.2064 | 2.1664 | 3.1899 | 1034.3164 | 1141.4612 | 1884.5259 | 2734.7353 | 0 | 0
|  |  |  | 709 | 1.0855 | 1.1457 | 2.0576 | 3.0297 | 983.686 | 1085.5338 | 1792.3571 | 2601.0282 | 0 | 0 | 0 | 1.1426 | 1.206 | 2.1659 | 3.1891 | 1035.459 | 1142.6671 | 1886.6917 | 2737.9245 | 0 | 0
|  |  |  | 710 | 1.0851 | 1.1453 | 2.057 | 3.0289 | 984.7712 | 1086.679 | 1794.4142 | 2604.0572 | 0 | 0 | 0 | 1.1422 | 1.2055 | 2.1653 | 3.1884 | 1036.6012 | 1143.8727 | 1888.857 | 2741.1128 | 0 | 0
|  |  |  | 711 | 1.0848 | 1.1448 | 2.0565 | 3.0282 | 985.856 | 1087.8239 | 1796.4707 | 2607.0854 | 0 | 0 | 0 | 1.1419 | 1.2051 | 2.1647 | 3.1876 | 1037.7431 | 1145.0778 | 1891.0217 | 2744.3004 | 0 | 0
|  |  |  | 712 | 1.0845 | 1.1444 | 2.056 | 3.0274 | 986.9404 | 1088.9683 | 1798.5266 | 2610.1128 | 0 | 0 | 0 | 1.1415 | 1.2047 | 2.1642 | 3.1868 | 1038.8846 | 1146.2824 | 1893.1859 | 2747.4872 | 0 | 0
|  |  |  | 713 | 1.0841 | 1.144 | 2.0554 | 3.0267 | 988.0245 | 1090.1123 | 1800.582 | 2613.1395 | 0 | 0 | 0 | 1.1412 | 1.2042 | 2.1636 | 3.186 | 1040.0258 | 1147.4867 | 1895.3495 | 2750.6732 | 0 | 0
|  |  |  | 714 | 1.0838 | 1.1436 | 2.0549 | 3.026 | 989.1083 | 1091.2559 | 1802.6369 | 2616.1655 | 0 | 0 | 0 | 1.1408 | 1.2038 | 2.163 | 3.1852 | 1041.1667 | 1148.6905 | 1897.5125 | 2753.8584 | 0 | 0
|  |  |  | 715 | 1.0835 | 1.1432 | 2.0543 | 3.0252 | 990.1918 | 1092.3991 | 1804.6912 | 2619.1907 | 0 | 0 | 0 | 1.1405 | 1.2034 | 2.1625 | 3.1845 | 1042.3071 | 1149.8938 | 1899.675 | 2757.0429 | 0 | 0
|  |  |  | 716 | 1.0831 | 1.1428 | 2.0538 | 3.0245 | 991.2749 | 1093.5419 | 1806.7451 | 2622.2152 | 0 | 0 | 0 | 1.1401 | 1.2029 | 2.1619 | 3.1837 | 1043.4473 | 1151.0968 | 1901.8369 | 2760.2265 | 0 | 0
|  |  |  | 717 | 1.0828 | 1.1424 | 2.0533 | 3.0238 | 992.3577 | 1094.6843 | 1808.7983 | 2625.239 | 0 | 0 | 0 | 1.1398 | 1.2025 | 2.1613 | 3.1829 | 1044.587 | 1152.2993 | 1903.9982 | 2763.4094 | 0 | 0
|  |  |  | 718 | 1.0825 | 1.142 | 2.0527 | 3.023 | 993.4401 | 1095.8263 | 1810.8511 | 2628.262 | 0 | 0 | 0 | 1.1394 | 1.2021 | 2.1608 | 3.1821 | 1045.7265 | 1153.5014 | 1906.159 | 2766.5916 | 0 | 0
|  |  |  | 719 | 1.0821 | 1.1416 | 2.0522 | 3.0223 | 994.5223 | 1096.9679 | 1812.9033 | 2631.2843 | 0 | 0 | 0 | 1.1391 | 1.2017 | 2.1602 | 3.1814 | 1046.8655 | 1154.7031 | 1908.3192 | 2769.7729 | 0 | 0
|  |  |  | 720 | 1.0818 | 1.1412 | 2.0517 | 3.0216 | 995.6041 | 1098.1091 | 1814.9549 | 2634.3058 | 0 | 0 | 0 | 1.1387 | 1.2012 | 2.1597 | 3.1806 | 1048.0043 | 1155.9043 | 1910.4789 | 2772.9535 | 0 | 0
|  |  |  | 721 | 1.0815 | 1.1408 | 2.0511 | 3.0208 | 996.6855 | 1099.2499 | 1817.0061 | 2637.3266 | 0 | 0 | 0 | 1.1384 | 1.2008 | 2.1591 | 3.1798 | 1049.1427 | 1157.1051 | 1912.638 | 2776.1333 | 0 | 0
|  |  |  | 722 | 1.0811 | 1.1404 | 2.0506 | 3.0201 | 997.7667 | 1100.3902 | 1819.0567 | 2640.3467 | 0 | 0 | 0 | 1.138 | 1.2004 | 2.1585 | 3.179 | 1050.2807 | 1158.3055 | 1914.7965 | 2779.3124 | 0 | 0
|  |  |  | 723 | 1.0808 | 1.14 | 2.0501 | 3.0194 | 998.8475 | 1101.5302 | 1821.1068 | 2643.3661 | 0 | 0 | 0 | 1.1377 | 1.2 | 2.158 | 3.1783 | 1051.4184 | 1159.5055 | 1916.9545 | 2782.4906 | 0 | 0
|  |  |  | 724 | 1.0805 | 1.1396 | 2.0496 | 3.0186 | 999.9279 | 1102.6698 | 1823.1563 | 2646.3847 | 0 | 0 | 0 | 1.1373 | 1.1995 | 2.1574 | 3.1775 | 1052.5557 | 1160.705 | 1919.1119 | 2785.6681 | 0 | 0
|  |  |  | 725 | 1.0801 | 1.1392 | 2.049 | 3.0179 | 1001.0081 | 1103.8089 | 1825.2054 | 2649.4026 | 0 | 0 | 0 | 1.137 | 1.1991 | 2.1569 | 3.1767 | 1053.6927 | 1161.9041 | 1921.2688 | 2788.8449 | 0 | 0
|  |  |  | 726 | 1.0798 | 1.1388 | 2.0485 | 3.0172 | 1002.0879 | 1104.9477 | 1827.2539 | 2652.4198 | 0 | 0 | 0 | 1.1367 | 1.1987 | 2.1563 | 3.176 | 1054.8294 | 1163.1028 | 1923.4251 | 2792.0209 | 0 | 0
|  |  |  | 727 | 1.0795 | 1.1384 | 2.048 | 3.0165 | 1003.1674 | 1106.0861 | 1829.3018 | 2655.4363 | 0 | 0 | 0 | 1.1363 | 1.1983 | 2.1558 | 3.1752 | 1055.9657 | 1164.3011 | 1925.5809 | 2795.1961 | 0 | 0
|  |  |  | 728 | 1.0792 | 1.138 | 2.0475 | 3.0157 | 1004.2466 | 1107.224 | 1831.3493 | 2658.452 | 0 | 0 | 0 | 1.136 | 1.1979 | 2.1552 | 3.1745 | 1057.1017 | 1165.499 | 1927.7361 | 2798.3706 | 0 | 0
|  |  |  | 729 | 1.0788 | 1.1376 | 2.0469 | 3.015 | 1005.3254 | 1108.3616 | 1833.3962 | 2661.467 | 0 | 0 | 0 | 1.1356 | 1.1974 | 2.1547 | 3.1737 | 1058.2373 | 1166.6964 | 1929.8908 | 2801.5443 | 0 | 0
|  |  |  | 730 | 1.0785 | 1.1372 | 2.0464 | 3.0143 | 1006.4039 | 1109.4988 | 1835.4426 | 2664.4813 | 0 | 0 | 0 | 1.1353 | 1.197 | 2.1541 | 3.1729 | 1059.3726 | 1167.8934 | 1932.0449 | 2804.7172 | 0 | 0
|  |  |  | 731 | 1.0782 | 1.1368 | 2.0459 | 3.0136 | 1007.4821 | 1110.6356 | 1837.4885 | 2667.4949 | 0 | 0 | 0 | 1.1349 | 1.1966 | 2.1536 | 3.1722 | 1060.5075 | 1169.0901 | 1934.1984 | 2807.8894 | 0 | 0
|  |  |  | 732 | 1.0779 | 1.1364 | 2.0454 | 3.0129 | 1008.56 | 1111.7719 | 1839.5339 | 2670.5078 | 0 | 0 | 0 | 1.1346 | 1.1962 | 2.153 | 3.1714 | 1061.6421 | 1170.2862 | 1936.3515 | 2811.0608 | 0 | 0
|  |  |  | 733 | 1.0775 | 1.136 | 2.0448 | 3.0121 | 1009.6375 | 1112.9079 | 1841.5787 | 2673.5199 | 0 | 0 | 0 | 1.1343 | 1.1958 | 2.1525 | 3.1707 | 1062.7764 | 1171.482 | 1938.5039 | 2814.2315 | 0 | 0
|  |  |  | 734 | 1.0772 | 1.1356 | 2.0443 | 3.0114 | 1010.7148 | 1114.0435 | 1843.623 | 2676.5313 | 0 | 0 | 0 | 1.1339 | 1.1954 | 2.1519 | 3.1699 | 1063.9103 | 1172.6774 | 1940.6558 | 2817.4014 | 0 | 0
|  |  |  | 735 | 1.0769 | 1.1352 | 2.0438 | 3.0107 | 1011.7917 | 1115.1787 | 1845.6668 | 2679.542 | 0 | 0 | 0 | 1.1336 | 1.1949 | 2.1514 | 3.1692 | 1065.0438 | 1173.8723 | 1942.8072 | 2820.5706 | 0 | 0
|  |  |  | 736 | 1.0766 | 1.1348 | 2.0433 | 3.01 | 1012.8682 | 1116.3135 | 1847.7101 | 2682.552 | 0 | 0 | 0 | 1.1332 | 1.1945 | 2.1508 | 3.1684 | 1066.1771 | 1175.0669 | 1944.958 | 2823.739 | 0 | 0
|  |  |  | 737 | 1.0763 | 1.1344 | 2.0428 | 3.0093 | 1013.9445 | 1117.4479 | 1849.7529 | 2685.5613 | 0 | 0 | 0 | 1.1329 | 1.1941 | 2.1503 | 3.1677 | 1067.31 | 1176.261 | 1947.1083 | 2826.9066 | 0 | 0
|  |  |  | 738 | 1.0759 | 1.134 | 2.0423 | 3.0086 | 1015.0204 | 1118.5819 | 1851.7951 | 2688.5699 | 0 | 0 | 0 | 1.1326 | 1.1937 | 2.1497 | 3.1669 | 1068.4425 | 1177.4547 | 1949.2581 | 2830.0736 | 0 | 0
|  |  |  | 739 | 1.0756 | 1.1336 | 2.0417 | 3.0079 | 1016.096 | 1119.7156 | 1853.8369 | 2691.5777 | 0 | 0 | 0 | 1.1322 | 1.1933 | 2.1492 | 3.1662 | 1069.5748 | 1178.648 | 1951.4072 | 2833.2397 | 0 | 0
|  |  |  | 740 | 1.0753 | 1.1332 | 2.0412 | 3.0072 | 1017.1713 | 1120.8488 | 1855.8781 | 2694.5849 | 0 | 0 | 0 | 1.1319 | 1.1929 | 2.1487 | 3.1654 | 1070.7067 | 1179.8409 | 1953.5559 | 2836.4051 | 0 | 0
|  |  |  | 741 | 1.075 | 1.1328 | 2.0407 | 3.0064 | 1018.2463 | 1121.9817 | 1857.9188 | 2697.5913 | 0 | 0 | 0 | 1.1316 | 1.1925 | 2.1481 | 3.1647 | 1071.8382 | 1181.0333 | 1955.704 | 2839.5698 | 0 | 0
|  |  |  | 742 | 1.0747 | 1.1325 | 2.0402 | 3.0057 | 1019.321 | 1123.1141 | 1859.959 | 2700.5971 | 0 | 0 | 0 | 1.1312 | 1.1921 | 2.1476 | 3.1639 | 1072.9694 | 1182.2254 | 1957.8516 | 2842.7338 | 0 | 0
|  |  |  | 743 | 1.0743 | 1.1321 | 2.0397 | 3.005 | 1020.3953 | 1124.2462 | 1861.9987 | 2703.6021 | 0 | 0 | 0 | 1.1309 | 1.1917 | 2.147 | 3.1632 | 1074.1003 | 1183.417 | 1959.9986 | 2845.8969 | 0 | 0
|  |  |  | 744 | 1.074 | 1.1317 | 2.0392 | 3.0043 | 1021.4693 | 1125.3779 | 1864.0379 | 2706.6064 | 0 | 0 | 0 | 1.1305 | 1.1912 | 2.1465 | 3.1624 | 1075.2309 | 1184.6083 | 1962.1451 | 2849.0594 | 0 | 0
|  |  |  | 745 | 1.0737 | 1.1313 | 2.0387 | 3.0036 | 1022.543 | 1126.5092 | 1866.0765 | 2709.61 | 0 | 0 | 0 | 1.1302 | 1.1908 | 2.146 | 3.1617 | 1076.3611 | 1185.7991 | 1964.2911 | 2852.2211 | 0 | 0
|  |  |  | 746 | 1.0734 | 1.1309 | 2.0382 | 3.0029 | 1023.6164 | 1127.6401 | 1868.1147 | 2712.613 | 0 | 0 | 0 | 1.1299 | 1.1904 | 2.1454 | 3.161 | 1077.4909 | 1186.9896 | 1966.4365 | 2855.3821 | 0 | 0
|  |  |  | 747 | 1.0731 | 1.1305 | 2.0376 | 3.0022 | 1024.6895 | 1128.7706 | 1870.1523 | 2715.6152 | 0 | 0 | 0 | 1.1295 | 1.19 | 2.1449 | 3.1602 | 1078.6205 | 1188.1796 | 1968.5814 | 2858.5423 | 0 | 0
|  |  |  | 748 | 1.0728 | 1.1301 | 2.0371 | 3.0015 | 1025.7622 | 1129.9007 | 1872.1895 | 2718.6167 | 0 | 0 | 0 | 1.1292 | 1.1896 | 2.1444 | 3.1595 | 1079.7497 | 1189.3692 | 1970.7257 | 2861.7018 | 0 | 0
|  |  |  | 749 | 1.0724 | 1.1298 | 2.0366 | 3.0008 | 1026.8347 | 1131.0305 | 1874.2261 | 2721.6175 | 0 | 0 | 0 | 1.1289 | 1.1892 | 2.1438 | 3.1588 | 1080.8786 | 1190.5584 | 1972.8696 | 2864.8605 | 0 | 0
|  |  |  | 750 | 1.0721 | 1.1294 | 2.0361 | 3.0001 | 1027.9068 | 1132.1599 | 1876.2622 | 2724.6176 | 0 | 0 | 0 | 1.1285 | 1.1888 | 2.1433 | 3.158 | 1082.0071 | 1191.7472 | 1975.0128 | 2868.0186 | 0 | 0
|  |  |  | 751 | 1.0718 | 1.129 | 2.0356 | 2.9994 | 1028.9786 | 1133.2889 | 1878.2978 | 2727.6171 | 0 | 0 | 0 | 1.1282 | 1.1884 | 2.1428 | 3.1573 | 1083.1353 | 1192.9356 | 1977.1556 | 2871.1758 | 0 | 0
|  |  |  | 752 | 1.0715 | 1.1286 | 2.0351 | 2.9987 | 1030.0501 | 1134.4175 | 1880.3329 | 2730.6158 | 0 | 0 | 0 | 1.1279 | 1.188 | 2.1422 | 3.1566 | 1084.2632 | 1194.1236 | 1979.2978 | 2874.3324 | 0 | 0
|  |  |  | 753 | 1.0712 | 1.1282 | 2.0346 | 2.998 | 1031.1213 | 1135.5457 | 1882.3675 | 2733.6138 | 0 | 0 | 0 | 1.1276 | 1.1876 | 2.1417 | 3.1558 | 1085.3908 | 1195.3112 | 1981.4395 | 2877.4882 | 0 | 0
|  |  |  | 754 | 1.0709 | 1.1278 | 2.0341 | 2.9973 | 1032.1921 | 1136.6735 | 1884.4016 | 2736.6112 | 0 | 0 | 0 | 1.1272 | 1.1872 | 2.1412 | 3.1551 | 1086.518 | 1196.4984 | 1983.5807 | 2880.6433 | 0 | 0
|  |  |  | 755 | 1.0706 | 1.1275 | 2.0336 | 2.9966 | 1033.2627 | 1137.801 | 1886.4352 | 2739.6078 | 0 | 0 | 0 | 1.1269 | 1.1868 | 2.1406 | 3.1544 | 1087.6449 | 1197.6852 | 1985.7213 | 2883.7977 | 0 | 0
|  |  |  | 756 | 1.0702 | 1.1271 | 2.0331 | 2.996 | 1034.3329 | 1138.9281 | 1888.4683 | 2742.6038 | 0 | 0 | 0 | 1.1266 | 1.1864 | 2.1401 | 3.1536 | 1088.7715 | 1198.8716 | 1987.8614 | 2886.9513 | 0 | 0
|  |  |  | 757 | 1.0699 | 1.1267 | 2.0326 | 2.9953 | 1035.4029 | 1140.0548 | 1890.5009 | 2745.599 | 0 | 0 | 0 | 1.1262 | 1.186 | 2.1396 | 3.1529 | 1089.8977 | 1200.0576 | 1990.001 | 2890.1042 | 0 | 0
|  |  |  | 758 | 1.0696 | 1.1263 | 2.0321 | 2.9946 | 1036.4725 | 1141.1811 | 1892.533 | 2748.5936 | 0 | 0 | 0 | 1.1259 | 1.1856 | 2.1391 | 3.1522 | 1091.0237 | 1201.2432 | 1992.14 | 2893.2564 | 0 | 0
|  |  |  | 759 | 1.0693 | 1.1259 | 2.0316 | 2.9939 | 1037.5418 | 1142.307 | 1894.5646 | 2751.5875 | 0 | 0 | 0 | 1.1256 | 1.1852 | 2.1385 | 3.1515 | 1092.1493 | 1202.4284 | 1994.2786 | 2896.4079 | 0 | 0
|  |  |  | 760 | 1.069 | 1.1256 | 2.0311 | 2.9932 | 1038.6108 | 1143.4326 | 1896.5957 | 2754.5807 | 0 | 0 | 0 | 1.1253 | 1.1848 | 2.138 | 3.1507 | 1093.2745 | 1203.6132 | 1996.4166 | 2899.5586 | 0 | 0
|  |  |  | 761 | 1.0687 | 1.1252 | 2.0306 | 2.9925 | 1039.6795 | 1144.5578 | 1898.6263 | 2757.5732 | 0 | 0 | 0 | 1.1249 | 1.1844 | 2.1375 | 3.15 | 1094.3995 | 1204.7977 | 1998.554 | 2902.7086 | 0 | 0
|  |  |  | 762 | 1.0684 | 1.1248 | 2.0301 | 2.9918 | 1040.7479 | 1145.6826 | 1900.6564 | 2760.565 | 0 | 0 | 0 | 1.1246 | 1.184 | 2.137 | 3.1493 | 1095.5241 | 1205.9817 | 2000.691 | 2905.8579 | 0 | 0
|  |  |  | 763 | 1.0681 | 1.1244 | 2.0296 | 2.9911 | 1041.816 | 1146.807 | 1902.6861 | 2763.5562 | 0 | 0 | 0 | 1.1243 | 1.1836 | 2.1364 | 3.1486 | 1096.6484 | 1207.1653 | 2002.8274 | 2909.0065 | 0 | 0
|  |  |  | 764 | 1.0678 | 1.1241 | 2.0291 | 2.9905 | 1042.8837 | 1147.9311 | 1904.7152 | 2766.5466 | 0 | 0 | 0 | 1.124 | 1.1832 | 2.1359 | 3.1479 | 1097.7723 | 1208.3485 | 2004.9633 | 2912.1543 | 0 | 0
|  |  |  | 765 | 1.0675 | 1.1237 | 2.0286 | 2.9898 | 1043.9512 | 1149.0548 | 1906.7438 | 2769.5364 | 0 | 0 | 0 | 1.1236 | 1.1828 | 2.1354 | 3.1471 | 1098.896 | 1209.5313 | 2007.0987 | 2915.3015 | 0 | 0
|  |  |  | 766 | 1.0672 | 1.1233 | 2.0281 | 2.9891 | 1045.0183 | 1150.1781 | 1908.7719 | 2772.5255 | 0 | 0 | 0 | 1.1233 | 1.1824 | 2.1349 | 3.1464 | 1100.0193 | 1210.7138 | 2009.2336 | 2918.4479 | 0 | 0
|  |  |  | 767 | 1.0668 | 1.1229 | 2.0276 | 2.9884 | 1046.0852 | 1151.301 | 1910.7996 | 2775.5139 | 0 | 0 | 0 | 1.123 | 1.182 | 2.1344 | 3.1457 | 1101.1423 | 1211.8958 | 2011.3679 | 2921.5936 | 0 | 0
|  |  |  | 768 | 1.0665 | 1.1226 | 2.0271 | 2.9877 | 1047.1517 | 1152.4236 | 1912.8267 | 2778.5017 | 0 | 0 | 0 | 1.1227 | 1.1816 | 2.1338 | 3.145 | 1102.265 | 1213.0775 | 2013.5018 | 2924.7386 | 0 | 0
|  |  |  | 769 | 1.0662 | 1.1222 | 2.0266 | 2.9871 | 1048.218 | 1153.5458 | 1914.8533 | 2781.4887 | 0 | 0 | 0 | 1.1224 | 1.1813 | 2.1333 | 3.1443 | 1103.3873 | 1214.2587 | 2015.6351 | 2927.8829 | 0 | 0
|  |  |  | 770 | 1.0659 | 1.1218 | 2.0262 | 2.9864 | 1049.2839 | 1154.6676 | 1916.8795 | 2784.4751 | 0 | 0 | 0 | 1.122 | 1.1809 | 2.1328 | 3.1436 | 1104.5094 | 1215.4396 | 2017.7679 | 2931.0264 | 0 | 0
|  |  |  | 771 | 1.0656 | 1.1215 | 2.0257 | 2.9857 | 1050.3495 | 1155.789 | 1918.9052 | 2787.4608 | 0 | 0 | 0 | 1.1217 | 1.1805 | 2.1323 | 3.1429 | 1105.6311 | 1216.6201 | 2019.9002 | 2934.1693 | 0 | 0
|  |  |  | 772 | 1.0653 | 1.1211 | 2.0252 | 2.985 | 1051.4149 | 1156.9101 | 1920.9303 | 2790.4458 | 0 | 0 | 0 | 1.1214 | 1.1801 | 2.1318 | 3.1421 | 1106.7525 | 1217.8001 | 2022.0319 | 2937.3114 | 0 | 0
|  |  |  | 773 | 1.065 | 1.1207 | 2.0247 | 2.9844 | 1052.4799 | 1158.0308 | 1922.955 | 2793.4302 | 0 | 0 | 0 | 1.1211 | 1.1797 | 2.1313 | 3.1414 | 1107.8736 | 1218.9798 | 2024.1632 | 2940.4528 | 0 | 0
|  |  |  | 774 | 1.0647 | 1.1203 | 2.0242 | 2.9837 | 1053.5446 | 1159.1512 | 1924.9792 | 2796.4139 | 0 | 0 | 0 | 1.1208 | 1.1793 | 2.1307 | 3.1407 | 1108.9943 | 1220.1591 | 2026.2939 | 2943.5936 | 0 | 0
|  |  |  | 775 | 1.0644 | 1.12 | 2.0237 | 2.983 | 1054.609 | 1160.2712 | 1927.003 | 2799.3969 | 0 | 0 | 0 | 1.1204 | 1.1789 | 2.1302 | 3.14 | 1110.1147 | 1221.3381 | 2028.4242 | 2946.7336 | 0 | 0
|  |  |  | 776 | 1.0641 | 1.1196 | 2.0232 | 2.9823 | 1055.6731 | 1161.3908 | 1929.0262 | 2802.3793 | 0 | 0 | 0 | 1.1201 | 1.1785 | 2.1297 | 3.1393 | 1111.2349 | 1222.5166 | 2030.5539 | 2949.8729 | 0 | 0
|  |  |  | 777 | 1.0638 | 1.1192 | 2.0227 | 2.9817 | 1056.7369 | 1162.51 | 1931.0489 | 2805.3609 | 0 | 0 | 0 | 1.1198 | 1.1781 | 2.1292 | 3.1386 | 1112.3547 | 1223.6947 | 2032.6831 | 2953.0115 | 0 | 0
|  |  |  | 778 | 1.0635 | 1.1189 | 2.0223 | 2.981 | 1057.8004 | 1163.6289 | 1933.0712 | 2808.3419 | 0 | 0 | 0 | 1.1195 | 1.1778 | 2.1287 | 3.1379 | 1113.4742 | 1224.8725 | 2034.8118 | 2956.1494 | 0 | 0
|  |  |  | 779 | 1.0632 | 1.1185 | 2.0218 | 2.9803 | 1058.8637 | 1164.7474 | 1935.093 | 2811.3223 | 0 | 0 | 0 | 1.1192 | 1.1774 | 2.1282 | 3.1372 | 1114.5933 | 1226.0499 | 2036.94 | 2959.2866 | 0 | 0
|  |  |  | 780 | 1.0629 | 1.1181 | 2.0213 | 2.9797 | 1059.9266 | 1165.8655 | 1937.1143 | 2814.302 | 0 | 0 | 0 | 1.1189 | 1.177 | 2.1277 | 3.1365 | 1115.7122 | 1227.2269 | 2039.0676 | 2962.4231 | 0 | 0
|  |  |  | 781 | 1.0626 | 1.1178 | 2.0208 | 2.979 | 1060.9892 | 1166.9833 | 1939.1351 | 2817.281 | 0 | 0 | 0 | 1.1185 | 1.1766 | 2.1272 | 3.1358 | 1116.8307 | 1228.4035 | 2041.1948 | 2965.5589 | 0 | 0
|  |  |  | 782 | 1.0623 | 1.1174 | 2.0203 | 2.9783 | 1062.0515 | 1168.1007 | 1941.1554 | 2820.2593 | 0 | 0 | 0 | 1.1182 | 1.1762 | 2.1267 | 3.1351 | 1117.9489 | 1229.5797 | 2043.3215 | 2968.694 | 0 | 0
|  |  |  | 783 | 1.062 | 1.117 | 2.0198 | 2.9777 | 1063.1135 | 1169.2178 | 1943.1753 | 2823.237 | 0 | 0 | 0 | 1.1179 | 1.1758 | 2.1262 | 3.1344 | 1119.0669 | 1230.7555 | 2045.4476 | 2971.8284 | 0 | 0
|  |  |  | 784 | 1.0617 | 1.1167 | 2.0194 | 2.977 | 1064.1752 | 1170.3344 | 1945.1946 | 2826.214 | 0 | 0 | 0 | 1.1176 | 1.1755 | 2.1256 | 3.1337 | 1120.1844 | 1231.931 | 2047.5733 | 2974.9621 | 0 | 0
|  |  |  | 785 | 1.0614 | 1.1163 | 2.0189 | 2.9764 | 1065.2366 | 1171.4508 | 1947.2135 | 2829.1904 | 0 | 0 | 0 | 1.1173 | 1.1751 | 2.1251 | 3.133 | 1121.3017 | 1233.1061 | 2049.6984 | 2978.0951 | 0 | 0
|  |  |  | 786 | 1.0611 | 1.116 | 2.0184 | 2.9757 | 1066.2978 | 1172.5667 | 1949.2319 | 2832.1661 | 0 | 0 | 0 | 1.117 | 1.1747 | 2.1246 | 3.1323 | 1122.4187 | 1234.2808 | 2051.8231 | 2981.2274 | 0 | 0
|  |  |  | 787 | 1.0608 | 1.1156 | 2.0179 | 2.975 | 1067.3586 | 1173.6823 | 1951.2498 | 2835.1411 | 0 | 0 | 0 | 1.1167 | 1.1743 | 2.1241 | 3.1316 | 1123.5354 | 1235.4551 | 2053.9472 | 2984.3591 | 0 | 0
|  |  |  | 788 | 1.0605 | 1.1152 | 2.0175 | 2.9744 | 1068.4191 | 1174.7976 | 1953.2673 | 2838.1155 | 0 | 0 | 0 | 1.1163 | 1.1739 | 2.1236 | 3.1309 | 1124.6517 | 1236.629 | 2056.0708 | 2987.49 | 0 | 0
|  |  |  | 789 | 1.0602 | 1.1149 | 2.017 | 2.9737 | 1069.4793 | 1175.9124 | 1955.2843 | 2841.0892 | 0 | 0 | 0 | 1.116 | 1.1736 | 2.1231 | 3.1302 | 1125.7677 | 1237.8026 | 2058.194 | 2990.6202 | 0 | 0
|  |  |  | 790 | 1.0599 | 1.1145 | 2.0165 | 2.9731 | 1070.5393 | 1177.027 | 1957.3008 | 2844.0623 | 0 | 0 | 0 | 1.1157 | 1.1732 | 2.1226 | 3.1295 | 1126.8835 | 1238.9757 | 2060.3166 | 2993.7498 | 0 | 0
|  |  |  | 791 | 1.0596 | 1.1142 | 2.016 | 2.9724 | 1071.5989 | 1178.1411 | 1959.3168 | 2847.0347 | 0 | 0 | 0 | 1.1154 | 1.1728 | 2.1221 | 3.1289 | 1127.9989 | 1240.1485 | 2062.4387 | 2996.8786 | 0 | 0
|  |  |  | 792 | 1.0593 | 1.1138 | 2.0156 | 2.9718 | 1072.6583 | 1179.2549 | 1961.3324 | 2850.0064 | 0 | 0 | 0 | 1.1151 | 1.1724 | 2.1216 | 3.1282 | 1129.114 | 1241.321 | 2064.5604 | 3000.0068 | 0 | 0
|  |  |  | 793 | 1.0591 | 1.1134 | 2.0151 | 2.9711 | 1073.7173 | 1180.3684 | 1963.3474 | 2852.9775 | 0 | 0 | 0 | 1.1148 | 1.172 | 2.1211 | 3.1275 | 1130.2288 | 1242.493 | 2066.6815 | 3003.1342 | 0 | 0
|  |  |  | 794 | 1.0588 | 1.1131 | 2.0146 | 2.9704 | 1074.7761 | 1181.4814 | 1965.362 | 2855.948 | 0 | 0 | 0 | 1.1145 | 1.1717 | 2.1206 | 3.1268 | 1131.3432 | 1243.6647 | 2068.8021 | 3006.261 | 0 | 0
|  |  |  | 795 | 1.0585 | 1.1127 | 2.0141 | 2.9698 | 1075.8346 | 1182.5942 | 1967.3762 | 2858.9178 | 0 | 0 | 0 | 1.1142 | 1.1713 | 2.1201 | 3.1261 | 1132.4574 | 1244.836 | 2070.9223 | 3009.3871 | 0 | 0
|  |  |  | 796 | 1.0582 | 1.1124 | 2.0137 | 2.9691 | 1076.8927 | 1183.7065 | 1969.3898 | 2861.8869 | 0 | 0 | 0 | 1.1139 | 1.1709 | 2.1196 | 3.1254 | 1133.5713 | 1246.0069 | 2073.0419 | 3012.5126 | 0 | 0
|  |  |  | 797 | 1.0579 | 1.112 | 2.0132 | 2.9685 | 1077.9506 | 1184.8186 | 1971.403 | 2864.8554 | 0 | 0 | 0 | 1.1136 | 1.1705 | 2.1191 | 3.1247 | 1134.6849 | 1247.1774 | 2075.1611 | 3015.6373 | 0 | 0
|  |  |  | 798 | 1.0576 | 1.1117 | 2.0127 | 2.9678 | 1079.0082 | 1185.9302 | 1973.4157 | 2867.8233 | 0 | 0 | 0 | 1.1133 | 1.1702 | 2.1187 | 3.1241 | 1135.7981 | 1248.3476 | 2077.2797 | 3018.7613 | 0 | 0
|  |  |  | 799 | 1.0573 | 1.1113 | 2.0122 | 2.9672 | 1080.0655 | 1187.0415 | 1975.428 | 2870.7905 | 0 | 0 | 0 | 1.1129 | 1.1698 | 2.1182 | 3.1234 | 1136.911 | 1249.5174 | 2079.3979 | 3021.8847 | 0 | 0
|  |  |  | 800 | 1.057 | 1.111 | 2.0118 | 2.9666 | 1081.1225 | 1188.1525 | 1977.4398 | 2873.757 | 0 | 0 | 0 | 1.1126 | 1.1694 | 2.1177 | 3.1227 | 1138.0237 | 1250.6868 | 2081.5155 | 3025.0074 | 0 | 0
|  |  |  | 801 | 1.0567 | 1.1106 | 2.0113 | 2.9659 | 1082.1792 | 1189.2631 | 1979.4511 | 2876.7229 | 0 | 0 | 0 | 1.1123 | 1.1691 | 2.1172 | 3.122 | 1139.136 | 1251.8559 | 2083.6327 | 3028.1294 | 0 | 0
|  |  |  | 802 | 1.0564 | 1.1102 | 2.0108 | 2.9653 | 1083.2356 | 1190.3733 | 1981.4619 | 2879.6882 | 0 | 0 | 0 | 1.112 | 1.1687 | 2.1167 | 3.1213 | 1140.2481 | 1253.0245 | 2085.7494 | 3031.2507 | 0 | 0
|  |  |  | 803 | 1.0561 | 1.1099 | 2.0104 | 2.9646 | 1084.2918 | 1191.4832 | 1983.4723 | 2882.6528 | 0 | 0 | 0 | 1.1117 | 1.1683 | 2.1162 | 3.1207 | 1141.3598 | 1254.1928 | 2087.8656 | 3034.3714 | 0 | 0
|  |  |  | 804 | 1.0558 | 1.1095 | 2.0099 | 2.964 | 1085.3476 | 1192.5927 | 1985.4822 | 2885.6168 | 0 | 0 | 0 | 1.1114 | 1.1679 | 2.1157 | 3.12 | 1142.4712 | 1255.3608 | 2089.9813 | 3037.4914 | 0 | 0
|  |  |  | 805 | 1.0556 | 1.1092 | 2.0094 | 2.9633 | 1086.4032 | 1193.7019 | 1987.4917 | 2888.5801 | 0 | 0 | 0 | 1.1111 | 1.1676 | 2.1152 | 3.1193 | 1143.5823 | 1256.5284 | 2092.0965 | 3040.6107 | 0 | 0
|  |  |  | 806 | 1.0553 | 1.1088 | 2.009 | 2.9627 | 1087.4585 | 1194.8108 | 1989.5006 | 2891.5428 | 0 | 0 | 0 | 1.1108 | 1.1672 | 2.1147 | 3.1186 | 1144.6931 | 1257.6956 | 2094.2112 | 3043.7293 | 0 | 0
|  |  |  | 807 | 1.055 | 1.1085 | 2.0085 | 2.9621 | 1088.5134 | 1195.9193 | 1991.5092 | 2894.5049 | 0 | 0 | 0 | 1.1105 | 1.1668 | 2.1142 | 3.1179 | 1145.8036 | 1258.8624 | 2096.3254 | 3046.8472 | 0 | 0
|  |  |  | 808 | 1.0547 | 1.1081 | 2.0081 | 2.9614 | 1089.5681 | 1197.0274 | 1993.5172 | 2897.4663 | 0 | 0 | 0 | 1.1102 | 1.1665 | 2.1137 | 3.1173 | 1146.9138 | 1260.0288 | 2098.4392 | 3049.9645 | 0 | 0
|  |  |  | 809 | 1.0544 | 1.1078 | 2.0076 | 2.9608 | 1090.6226 | 1198.1352 | 1995.5248 | 2900.4271 | 0 | 0 | 0 | 1.1099 | 1.1661 | 2.1133 | 3.1166 | 1148.0237 | 1261.1949 | 2100.5524 | 3053.0811 | 0 | 0
|  |  |  | 810 | 1.0541 | 1.1074 | 2.0071 | 2.9601 | 1091.6767 | 1199.2426 | 1997.5319 | 2903.3872 | 0 | 0 | 0 | 1.1096 | 1.1657 | 2.1128 | 3.1159 | 1149.1333 | 1262.3607 | 2102.6652 | 3056.197 | 0 | 0
|  |  |  | 811 | 1.0538 | 1.1071 | 2.0067 | 2.9595 | 1092.7305 | 1200.3497 | 1999.5386 | 2906.3467 | 0 | 0 | 0 | 1.1093 | 1.1654 | 2.1123 | 3.1153 | 1150.2426 | 1263.526 | 2104.7775 | 3059.3123 | 0 | 0
|  |  |  | 812 | 1.0536 | 1.1067 | 2.0062 | 2.9589 | 1093.7841 | 1201.4565 | 2001.5448 | 2909.3056 | 0 | 0 | 0 | 1.109 | 1.165 | 2.1118 | 3.1146 | 1151.3516 | 1264.691 | 2106.8893 | 3062.4269 | 0 | 0
|  |  |  | 813 | 1.0533 | 1.1064 | 2.0057 | 2.9582 | 1094.8373 | 1202.5629 | 2003.5506 | 2912.2638 | 0 | 0 | 0 | 1.1087 | 1.1646 | 2.1113 | 3.1139 | 1152.4603 | 1265.8557 | 2109.0006 | 3065.5408 | 0 | 0
|  |  |  | 814 | 1.053 | 1.1061 | 2.0053 | 2.9576 | 1095.8903 | 1203.6689 | 2005.5558 | 2915.2214 | 0 | 0 | 0 | 1.1084 | 1.1643 | 2.1108 | 3.1133 | 1153.5687 | 1267.0199 | 2111.1114 | 3068.6541 | 0 | 0
|  |  |  | 815 | 1.0527 | 1.1057 | 2.0048 | 2.957 | 1096.943 | 1204.7746 | 2007.5607 | 2918.1784 | 0 | 0 | 0 | 1.1081 | 1.1639 | 2.1103 | 3.1126 | 1154.6768 | 1268.1838 | 2113.2218 | 3071.7667 | 0 | 0
|  |  |  | 816 | 1.0524 | 1.1054 | 2.0044 | 2.9563 | 1097.9954 | 1205.88 | 2009.5651 | 2921.1347 | 0 | 0 | 0 | 1.1078 | 1.1635 | 2.1099 | 3.1119 | 1155.7847 | 1269.3474 | 2115.3316 | 3074.8786 | 0 | 0
|  |  |  | 817 | 1.0521 | 1.105 | 2.0039 | 2.9557 | 1099.0475 | 1206.985 | 2011.569 | 2924.0904 | 0 | 0 | 0 | 1.1075 | 1.1632 | 2.1094 | 3.1113 | 1156.8922 | 1270.5105 | 2117.441 | 3077.9899 | 0 | 0
|  |  |  | 818 | 1.0518 | 1.1047 | 2.0035 | 2.9551 | 1100.0994 | 1208.0897 | 2013.5724 | 2927.0455 | 0 | 0 | 0 | 1.1072 | 1.1628 | 2.1089 | 3.1106 | 1157.9994 | 1271.6733 | 2119.5499 | 3081.1005 | 0 | 0
|  |  |  | 819 | 1.0516 | 1.1043 | 2.003 | 2.9544 | 1101.151 | 1209.194 | 2015.5754 | 2929.9999 | 0 | 0 | 0 | 1.1069 | 1.1625 | 2.1084 | 3.1099 | 1159.1063 | 1272.8358 | 2121.6583 | 3084.2104 | 0 | 0
|  |  |  | 820 | 1.0513 | 1.104 | 2.0025 | 2.9538 | 1102.2022 | 1210.298 | 2017.578 | 2932.9537 | 0 | 0 | 0 | 1.1066 | 1.1621 | 2.1079 | 3.1093 | 1160.2129 | 1273.9979 | 2123.7663 | 3087.3197 | 0 | 0
|  |  |  | 821 | 1.051 | 1.1036 | 2.0021 | 2.9532 | 1103.2532 | 1211.4016 | 2019.5801 | 2935.9069 | 0 | 0 | 0 | 1.1063 | 1.1617 | 2.1075 | 3.1086 | 1161.3192 | 1275.1596 | 2125.8738 | 3090.4283 | 0 | 0
|  |  |  | 822 | 1.0507 | 1.1033 | 2.0016 | 2.9526 | 1104.304 | 1212.5049 | 2021.5817 | 2938.8595 | 0 | 0 | 0 | 1.106 | 1.1614 | 2.107 | 3.108 | 1162.4252 | 1276.321 | 2127.9807 | 3093.5363 | 0 | 0
|  |  |  | 823 | 1.0504 | 1.103 | 2.0012 | 2.9519 | 1105.3544 | 1213.6079 | 2023.5829 | 2941.8114 | 0 | 0 | 0 | 1.1057 | 1.161 | 2.1065 | 3.1073 | 1163.5309 | 1277.482 | 2130.0873 | 3096.6436 | 0 | 0
|  |  |  | 824 | 1.0502 | 1.1026 | 2.0007 | 2.9513 | 1106.4045 | 1214.7105 | 2025.5836 | 2944.7627 | 0 | 0 | 0 | 1.1054 | 1.1606 | 2.106 | 3.1066 | 1164.6364 | 1278.6426 | 2132.1933 | 3099.7502 | 0 | 0
|  |  |  | 825 | 1.0499 | 1.1023 | 2.0003 | 2.9507 | 1107.4544 | 1215.8128 | 2027.5839 | 2947.7134 | 0 | 0 | 0 | 1.1051 | 1.1603 | 2.1056 | 3.106 | 1165.7415 | 1279.8029 | 2134.2989 | 3102.8562 | 0 | 0
|  |  |  | 826 | 1.0496 | 1.1019 | 1.9998 | 2.9501 | 1108.504 | 1216.9147 | 2029.5837 | 2950.6635 | 0 | 0 | 0 | 1.1048 | 1.1599 | 2.1051 | 3.1053 | 1166.8463 | 1280.9629 | 2136.4039 | 3105.9615 | 0 | 0
|  |  |  | 827 | 1.0493 | 1.1016 | 1.9994 | 2.9494 | 1109.5533 | 1218.0163 | 2031.5831 | 2953.6129 | 0 | 0 | 0 | 1.1045 | 1.1596 | 2.1046 | 3.1047 | 1167.9509 | 1282.1224 | 2138.5085 | 3109.0662 | 0 | 0
|  |  |  | 828 | 1.049 | 1.1013 | 1.9989 | 2.9488 | 1110.6024 | 1219.1176 | 2033.582 | 2956.5617 | 0 | 0 | 0 | 1.1043 | 1.1592 | 2.1041 | 3.104 | 1169.0551 | 1283.2816 | 2140.6127 | 3112.1702 | 0 | 0
|  |  |  | 829 | 1.0488 | 1.1009 | 1.9985 | 2.9482 | 1111.6511 | 1220.2185 | 2035.5805 | 2959.5099 | 0 | 0 | 0 | 1.104 | 1.1589 | 2.1037 | 3.1034 | 1170.1591 | 1284.4405 | 2142.7163 | 3115.2736 | 0 | 0
|  |  |  | 830 | 1.0485 | 1.1006 | 1.998 | 2.9476 | 1112.6996 | 1221.3191 | 2037.5786 | 2962.4575 | 0 | 0 | 0 | 1.1037 | 1.1585 | 2.1032 | 3.1027 | 1171.2628 | 1285.599 | 2144.8195 | 3118.3763 | 0 | 0
|  |  |  | 831 | 1.0482 | 1.1002 | 1.9976 | 2.947 | 1113.7478 | 1222.4193 | 2039.5761 | 2965.4045 | 0 | 0 | 0 | 1.1034 | 1.1582 | 2.1027 | 3.1021 | 1172.3661 | 1286.7572 | 2146.9223 | 3121.4784 | 0 | 0
|  |  |  | 832 | 1.0479 | 1.0999 | 1.9971 | 2.9463 | 1114.7957 | 1223.5192 | 2041.5733 | 2968.3508 | 0 | 0 | 0 | 1.1031 | 1.1578 | 2.1022 | 3.1014 | 1173.4692 | 1287.915 | 2149.0245 | 3124.5798 | 0 | 0
|  |  |  | 833 | 1.0476 | 1.0996 | 1.9967 | 2.9457 | 1115.8434 | 1224.6188 | 2043.57 | 2971.2965 | 0 | 0 | 0 | 1.1028 | 1.1574 | 2.1018 | 3.1008 | 1174.572 | 1289.0724 | 2151.1263 | 3127.6806 | 0 | 0
|  |  |  | 834 | 1.0474 | 1.0992 | 1.9962 | 2.9451 | 1116.8908 | 1225.718 | 2045.5662 | 2974.2417 | 0 | 0 | 0 | 1.1025 | 1.1571 | 2.1013 | 3.1001 | 1175.6745 | 1290.2295 | 2153.2276 | 3130.7807 | 0 | 0
|  |  |  | 835 | 1.0471 | 1.0989 | 1.9958 | 2.9445 | 1117.9379 | 1226.8169 | 2047.562 | 2977.1862 | 0 | 0 | 0 | 1.1022 | 1.1567 | 2.1008 | 3.0995 | 1176.7767 | 1291.3862 | 2155.3284 | 3133.8802 | 0 | 0
|  |  |  | 836 | 1.0468 | 1.0986 | 1.9954 | 2.9439 | 1118.9847 | 1227.9155 | 2049.5574 | 2980.13 | 0 | 0 | 0 | 1.1019 | 1.1564 | 2.1004 | 3.0988 | 1177.8786 | 1292.5426 | 2157.4288 | 3136.979 | 0 | 0
|  |  |  | 837 | 1.0465 | 1.0982 | 1.9949 | 2.9433 | 1120.0312 | 1229.0137 | 2051.5523 | 2983.0733 | 0 | 0 | 0 | 1.1016 | 1.156 | 2.0999 | 3.0982 | 1178.9802 | 1293.6986 | 2159.5287 | 3140.0772 | 0 | 0
|  |  |  | 838 | 1.0463 | 1.0979 | 1.9945 | 2.9427 | 1121.0775 | 1230.1116 | 2053.5467 | 2986.016 | 0 | 0 | 0 | 1.1013 | 1.1557 | 2.0994 | 3.0975 | 1180.0816 | 1294.8543 | 2161.6281 | 3143.1747 | 0 | 0
|  |  |  | 839 | 1.046 | 1.0976 | 1.994 | 2.942 | 1122.1235 | 1231.2092 | 2055.5408 | 2988.958 | 0 | 0 | 0 | 1.101 | 1.1553 | 2.099 | 3.0969 | 1181.1826 | 1296.0096 | 2163.7271 | 3146.2716 | 0 | 0
|  |  |  | 840 | 1.0457 | 1.0972 | 1.9936 | 2.9414 | 1123.1692 | 1232.3064 | 2057.5343 | 2991.8995 | 0 | 0 | 0 | 1.1008 | 1.155 | 2.0985 | 3.0962 | 1182.2834 | 1297.1646 | 2165.8256 | 3149.3678 | 0 | 0
|  |  |  | 841 | 1.0454 | 1.0969 | 1.9931 | 2.9408 | 1124.2147 | 1233.4033 | 2059.5275 | 2994.8403 | 0 | 0 | 0 | 1.1005 | 1.1546 | 2.098 | 3.0956 | 1183.3839 | 1298.3192 | 2167.9237 | 3152.4634 | 0 | 0
|  |  |  | 842 | 1.0452 | 1.0966 | 1.9927 | 2.9402 | 1125.2598 | 1234.4998 | 2061.5202 | 2997.7805 | 0 | 0 | 0 | 1.1002 | 1.1543 | 2.0976 | 3.095 | 1184.484 | 1299.4735 | 2170.0212 | 3155.5584 | 0 | 0
|  |  |  | 843 | 1.0449 | 1.0962 | 1.9923 | 2.9396 | 1126.3047 | 1235.5961 | 2063.5124 | 3000.7201 | 0 | 0 | 0 | 1.0999 | 1.1539 | 2.0971 | 3.0943 | 1185.5839 | 1300.6274 | 2172.1183 | 3158.6527 | 0 | 0
|  |  |  | 844 | 1.0446 | 1.0959 | 1.9918 | 2.939 | 1127.3494 | 1236.692 | 2065.5042 | 3003.6591 | 0 | 0 | 0 | 1.0996 | 1.1536 | 2.0966 | 3.0937 | 1186.6836 | 1301.781 | 2174.215 | 3161.7464 | 0 | 0
|  |  |  | 845 | 1.0444 | 1.0956 | 1.9914 | 2.9384 | 1128.3937 | 1237.7875 | 2067.4956 | 3006.5975 | 0 | 0 | 0 | 1.0993 | 1.1532 | 2.0962 | 3.093 | 1187.7829 | 1302.9343 | 2176.3112 | 3164.8395 | 0 | 0
|  |  |  | 846 | 1.0441 | 1.0952 | 1.9909 | 2.9378 | 1129.4378 | 1238.8828 | 2069.4866 | 3009.5353 | 0 | 0 | 0 | 1.099 | 1.1529 | 2.0957 | 3.0924 | 1188.8819 | 1304.0871 | 2178.4069 | 3167.9319 | 0 | 0
|  |  |  | 847 | 1.0438 | 1.0949 | 1.9905 | 2.9372 | 1130.4816 | 1239.9777 | 2071.4771 | 3012.4725 | 0 | 0 | 0 | 1.0988 | 1.1525 | 2.0953 | 3.0918 | 1189.9807 | 1305.2397 | 2180.5022 | 3171.0237 | 0 | 0
|  |  |  | 848 | 1.0435 | 1.0946 | 1.9901 | 2.9366 | 1131.5252 | 1241.0723 | 2073.4671 | 3015.4091 | 0 | 0 | 0 | 1.0985 | 1.1522 | 2.0948 | 3.0911 | 1191.0791 | 1306.3919 | 2182.597 | 3174.1148 | 0 | 0
|  |  |  | 849 | 1.0433 | 1.0943 | 1.9896 | 2.936 | 1132.5685 | 1242.1665 | 2075.4567 | 3018.345 | 0 | 0 | 0 | 1.0982 | 1.1518 | 2.0943 | 3.0905 | 1192.1773 | 1307.5437 | 2184.6913 | 3177.2053 | 0 | 0
|  |  |  | 850 | 1.043 | 1.0939 | 1.9892 | 2.9354 | 1133.6115 | 1243.2604 | 2077.4459 | 3021.2804 | 0 | 0 | 0 | 1.0979 | 1.1515 | 2.0939 | 3.0899 | 1193.2752 | 1308.6952 | 2186.7852 | 3180.2952 | 0 | 0
|  |  |  | 851 | 1.0427 | 1.0936 | 1.9888 | 2.9348 | 1134.6542 | 1244.354 | 2079.4347 | 3024.2152 | 0 | 0 | 0 | 1.0976 | 1.1512 | 2.0934 | 3.0892 | 1194.3728 | 1309.8464 | 2188.8786 | 3183.3844 | 0 | 0
|  |  |  | 852 | 1.0425 | 1.0933 | 1.9883 | 2.9342 | 1135.6967 | 1245.4473 | 2081.423 | 3027.1494 | 0 | 0 | 0 | 1.0973 | 1.1508 | 2.093 | 3.0886 | 1195.4702 | 1310.9972 | 2190.9716 | 3186.473 | 0 | 0
|  |  |  | 853 | 1.0422 | 1.0929 | 1.9879 | 2.9336 | 1136.7388 | 1246.5403 | 2083.4109 | 3030.083 | 0 | 0 | 0 | 1.097 | 1.1505 | 2.0925 | 3.088 | 1196.5672 | 1312.1476 | 2193.0641 | 3189.561 | 0 | 0
|  |  |  | 854 | 1.0419 | 1.0926 | 1.9875 | 2.933 | 1137.7808 | 1247.6329 | 2085.3984 | 3033.0159 | 0 | 0 | 0 | 1.0968 | 1.1501 | 2.0921 | 3.0873 | 1197.664 | 1313.2978 | 2195.1562 | 3192.6483 | 0 | 0
|  |  |  | 855 | 1.0417 | 1.0923 | 1.987 | 2.9324 | 1138.8224 | 1248.7252 | 2087.3854 | 3035.9483 | 0 | 0 | 0 | 1.0965 | 1.1498 | 2.0916 | 3.0867 | 1198.7605 | 1314.4475 | 2197.2478 | 3195.7351 | 0 | 0
|  |  |  | 856 | 1.0414 | 1.092 | 1.9866 | 2.9318 | 1139.8638 | 1249.8171 | 2089.372 | 3038.8801 | 0 | 0 | 0 | 1.0962 | 1.1494 | 2.0911 | 3.0861 | 1199.8567 | 1315.597 | 2199.3389 | 3198.8212 | 0 | 0
|  |  |  | 857 | 1.0411 | 1.0916 | 1.9862 | 2.9312 | 1140.9049 | 1250.9088 | 2091.3581 | 3041.8113 | 0 | 0 | 0 | 1.0959 | 1.1491 | 2.0907 | 3.0855 | 1200.9526 | 1316.7461 | 2201.4296 | 3201.9066 | 0 | 0
|  |  |  | 858 | 1.0409 | 1.0913 | 1.9857 | 2.9306 | 1141.9458 | 1252.0001 | 2093.3438 | 3044.7419 | 0 | 0 | 0 | 1.0956 | 1.1488 | 2.0902 | 3.0848 | 1202.0482 | 1317.8948 | 2203.5198 | 3204.9914 | 0 | 0
|  |  |  | 859 | 1.0406 | 1.091 | 1.9853 | 2.93 | 1142.9864 | 1253.0911 | 2095.3291 | 3047.6719 | 0 | 0 | 0 | 1.0954 | 1.1484 | 2.0898 | 3.0842 | 1203.1436 | 1319.0432 | 2205.6096 | 3208.0757 | 0 | 0
|  |  |  | 860 | 1.0403 | 1.0907 | 1.9849 | 2.9294 | 1144.0267 | 1254.1817 | 2097.314 | 3050.6013 | 0 | 0 | 0 | 1.0951 | 1.1481 | 2.0893 | 3.0836 | 1204.2386 | 1320.1913 | 2207.6989 | 3211.1592 | 0 | 0
|  |  |  | 861 | 1.0401 | 1.0903 | 1.9844 | 2.9288 | 1145.0668 | 1255.2721 | 2099.2984 | 3053.5301 | 0 | 0 | 0 | 1.0948 | 1.1477 | 2.0889 | 3.083 | 1205.3334 | 1321.339 | 2209.7878 | 3214.2422 | 0 | 0
|  |  |  | 862 | 1.0398 | 1.09 | 1.984 | 2.9282 | 1146.1066 | 1256.3621 | 2101.2824 | 3056.4583 | 0 | 0 | 0 | 1.0945 | 1.1474 | 2.0884 | 3.0823 | 1206.428 | 1322.4864 | 2211.8762 | 3217.3245 | 0 | 0
|  |  |  | 863 | 1.0395 | 1.0897 | 1.9836 | 2.9276 | 1147.1461 | 1257.4518 | 2103.266 | 3059.3859 | 0 | 0 | 0 | 1.0942 | 1.1471 | 2.088 | 3.0817 | 1207.5222 | 1323.6335 | 2213.9642 | 3220.4062 | 0 | 0
|  |  |  | 864 | 1.0393 | 1.0894 | 1.9831 | 2.927 | 1148.1854 | 1258.5412 | 2105.2492 | 3062.313 | 0 | 0 | 0 | 1.094 | 1.1467 | 2.0875 | 3.0811 | 1208.6162 | 1324.7802 | 2216.0517 | 3223.4873 | 0 | 0
|  |  |  | 865 | 1.039 | 1.0891 | 1.9827 | 2.9264 | 1149.2243 | 1259.6303 | 2107.2319 | 3065.2394 | 0 | 0 | 0 | 1.0937 | 1.1464 | 2.0871 | 3.0805 | 1209.7098 | 1325.9266 | 2218.1388 | 3226.5678 | 0 | 0
|  |  |  | 866 | 1.0387 | 1.0887 | 1.9823 | 2.9259 | 1150.2631 | 1260.719 | 2109.2142 | 3068.1653 | 0 | 0 | 0 | 1.0934 | 1.146 | 2.0866 | 3.0798 | 1210.8032 | 1327.0726 | 2220.2254 | 3229.6476 | 0 | 0
|  |  |  | 867 | 1.0385 | 1.0884 | 1.9819 | 2.9253 | 1151.3015 | 1261.8074 | 2111.196 | 3071.0905 | 0 | 0 | 0 | 1.0931 | 1.1457 | 2.0862 | 3.0792 | 1211.8964 | 1328.2183 | 2222.3116 | 3232.7269 | 0 | 0
|  |  |  | 868 | 1.0382 | 1.0881 | 1.9814 | 2.9247 | 1152.3398 | 1262.8955 | 2113.1775 | 3074.0152 | 0 | 0 | 0 | 1.0928 | 1.1454 | 2.0857 | 3.0786 | 1212.9892 | 1329.3637 | 2224.3974 | 3235.8055 | 0 | 0
|  |  |  | 869 | 1.0379 | 1.0878 | 1.981 | 2.9241 | 1153.3777 | 1263.9833 | 2115.1585 | 3076.9393 | 0 | 0 | 0 | 1.0926 | 1.145 | 2.0853 | 3.078 | 1214.0818 | 1330.5087 | 2226.4826 | 3238.8835 | 0 | 0
|  |  |  | 870 | 1.0377 | 1.0875 | 1.9806 | 2.9235 | 1154.4154 | 1265.0708 | 2117.1391 | 3079.8628 | 0 | 0 | 0 | 1.0923 | 1.1447 | 2.0848 | 3.0774 | 1215.1741 | 1331.6534 | 2228.5675 | 3241.9609 | 0 | 0
|  |  |  | 871 | 1.0374 | 1.0871 | 1.9802 | 2.9229 | 1155.4528 | 1266.1579 | 2119.1193 | 3082.7857 | 0 | 0 | 0 | 1.092 | 1.1444 | 2.0844 | 3.0768 | 1216.2661 | 1332.7978 | 2230.6519 | 3245.0376 | 0 | 0
|  |  |  | 872 | 1.0372 | 1.0868 | 1.9797 | 2.9223 | 1156.49 | 1267.2447 | 2121.099 | 3085.7081 | 0 | 0 | 0 | 1.0917 | 1.144 | 2.0839 | 3.0761 | 1217.3578 | 1333.9418 | 2232.7358 | 3248.1138 | 0 | 0
|  |  |  | 873 | 1.0369 | 1.0865 | 1.9793 | 2.9218 | 1157.5268 | 1268.3312 | 2123.0783 | 3088.6298 | 0 | 0 | 0 | 1.0915 | 1.1437 | 2.0835 | 3.0755 | 1218.4493 | 1335.0855 | 2234.8193 | 3251.1893 | 0 | 0
|  |  |  | 874 | 1.0366 | 1.0862 | 1.9789 | 2.9212 | 1158.5635 | 1269.4174 | 2125.0572 | 3091.551 | 0 | 0 | 0 | 1.0912 | 1.1434 | 2.0831 | 3.0749 | 1219.5405 | 1336.2289 | 2236.9024 | 3254.2642 | 0 | 0
|  |  |  | 875 | 1.0364 | 1.0859 | 1.9785 | 2.9206 | 1159.5999 | 1270.5033 | 2127.0357 | 3094.4716 | 0 | 0 | 0 | 1.0909 | 1.143 | 2.0826 | 3.0743 | 1220.6314 | 1337.3719 | 2238.985 | 3257.3385 | 0 | 0
|  |  |  | 876 | 1.0361 | 1.0856 | 1.9781 | 2.92 | 1160.636 | 1271.5889 | 2129.0138 | 3097.3916 | 0 | 0 | 0 | 1.0906 | 1.1427 | 2.0822 | 3.0737 | 1221.7221 | 1338.5146 | 2241.0671 | 3260.4122 | 0 | 0
|  |  |  | 877 | 1.0359 | 1.0852 | 1.9776 | 2.9194 | 1161.6718 | 1272.6741 | 2130.9914 | 3100.311 | 0 | 0 | 0 | 1.0904 | 1.1424 | 2.0817 | 3.0731 | 1222.8124 | 1339.6569 | 2243.1489 | 3263.4853 | 0 | 0
|  |  |  | 878 | 1.0356 | 1.0849 | 1.9772 | 2.9189 | 1162.7074 | 1273.759 | 2132.9687 | 3103.2299 | 0 | 0 | 0 | 1.0901 | 1.142 | 2.0813 | 3.0725 | 1223.9025 | 1340.799 | 2245.2302 | 3266.5578 | 0 | 0
|  |  |  | 879 | 1.0353 | 1.0846 | 1.9768 | 2.9183 | 1163.7427 | 1274.8436 | 2134.9455 | 3106.1482 | 0 | 0 | 0 | 1.0898 | 1.1417 | 2.0808 | 3.0719 | 1224.9924 | 1341.9407 | 2247.311 | 3269.6296 | 0 | 0
|  |  |  | 880 | 1.0351 | 1.0843 | 1.9764 | 2.9177 | 1164.7778 | 1275.9279 | 2136.9218 | 3109.0659 | 0 | 0 | 0 | 1.0896 | 1.1414 | 2.0804 | 3.0713 | 1226.0819 | 1343.082 | 2249.3914 | 3272.7009 | 0 | 0
|  |  |  | 881 | 1.0348 | 1.084 | 1.976 | 2.9171 | 1165.8126 | 1277.0119 | 2138.8978 | 3111.983 | 0 | 0 | 0 | 1.0893 | 1.141 | 2.08 | 3.0706 | 1227.1712 | 1344.2231 | 2251.4714 | 3275.7716 | 0 | 0
|  |  |  | 882 | 1.0346 | 1.0837 | 1.9755 | 2.9165 | 1166.8472 | 1278.0956 | 2140.8734 | 3114.8995 | 0 | 0 | 0 | 1.089 | 1.1407 | 2.0795 | 3.07 | 1228.2602 | 1345.3638 | 2253.5509 | 3278.8416 | 0 | 0
|  |  |  | 883 | 1.0343 | 1.0834 | 1.9751 | 2.916 | 1167.8815 | 1279.179 | 2142.8485 | 3117.8155 | 0 | 0 | 0 | 1.0887 | 1.1404 | 2.0791 | 3.0694 | 1229.3489 | 1346.5042 | 2255.63 | 3281.911 | 0 | 0
|  |  |  | 884 | 1.034 | 1.083 | 1.9747 | 2.9154 | 1168.9155 | 1280.262 | 2144.8232 | 3120.7309 | 0 | 0 | 0 | 1.0885 | 1.14 | 2.0786 | 3.0688 | 1230.4374 | 1347.6442 | 2257.7086 | 3284.9799 | 0 | 0
|  |  |  | 885 | 1.0338 | 1.0827 | 1.9743 | 2.9148 | 1169.9493 | 1281.3447 | 2146.7975 | 3123.6457 | 0 | 0 | 0 | 1.0882 | 1.1397 | 2.0782 | 3.0682 | 1231.5256 | 1348.7839 | 2259.7868 | 3288.0481 | 0 | 0
|  |  |  | 886 | 1.0335 | 1.0824 | 1.9739 | 2.9142 | 1170.9829 | 1282.4272 | 2148.7714 | 3126.5599 | 0 | 0 | 0 | 1.0879 | 1.1394 | 2.0778 | 3.0676 | 1232.6135 | 1349.9233 | 2261.8646 | 3291.1157 | 0 | 0
|  |  |  | 887 | 1.0333 | 1.0821 | 1.9735 | 2.9137 | 1172.0161 | 1283.5093 | 2150.7449 | 3129.4736 | 0 | 0 | 0 | 1.0877 | 1.1391 | 2.0773 | 3.067 | 1233.7012 | 1351.0624 | 2263.942 | 3294.1827 | 0 | 0
|  |  |  | 888 | 1.033 | 1.0818 | 1.9731 | 2.9131 | 1173.0491 | 1284.5911 | 2152.7179 | 3132.3867 | 0 | 0 | 0 | 1.0874 | 1.1387 | 2.0769 | 3.0664 | 1234.7886 | 1352.2011 | 2266.0189 | 3297.2492 | 0 | 0
|  |  |  | 889 | 1.0328 | 1.0815 | 1.9726 | 2.9125 | 1174.0819 | 1285.6726 | 2154.6906 | 3135.2992 | 0 | 0 | 0 | 1.0871 | 1.1384 | 2.0765 | 3.0658 | 1235.8757 | 1353.3396 | 2268.0953 | 3300.315 | 0 | 0
|  |  |  | 890 | 1.0325 | 1.0812 | 1.9722 | 2.912 | 1175.1144 | 1286.7538 | 2156.6628 | 3138.2112 | 0 | 0 | 0 | 1.0868 | 1.1381 | 2.076 | 3.0652 | 1236.9625 | 1354.4776 | 2270.1714 | 3303.3802 | 0 | 0
|  |  |  | 891 | 1.0322 | 1.0809 | 1.9718 | 2.9114 | 1176.1467 | 1287.8346 | 2158.6346 | 3141.1226 | 0 | 0 | 0 | 1.0866 | 1.1378 | 2.0756 | 3.0646 | 1238.0491 | 1355.6154 | 2272.247 | 3306.4448 | 0 | 0
|  |  |  | 892 | 1.032 | 1.0806 | 1.9714 | 2.9108 | 1177.1786 | 1288.9152 | 2160.606 | 3144.0334 | 0 | 0 | 0 | 1.0863 | 1.1374 | 2.0752 | 3.064 | 1239.1354 | 1356.7528 | 2274.3221 | 3309.5088 | 0 | 0
|  |  |  | 893 | 1.0317 | 1.0803 | 1.971 | 2.9103 | 1178.2104 | 1289.9954 | 2162.577 | 3146.9436 | 0 | 0 | 0 | 1.086 | 1.1371 | 2.0747 | 3.0634 | 1240.2215 | 1357.8899 | 2276.3969 | 3312.5723 | 0 | 0
|  |  |  | 894 | 1.0315 | 1.0799 | 1.9706 | 2.9097 | 1179.2419 | 1291.0754 | 2164.5476 | 3149.8533 | 0 | 0 | 0 | 1.0858 | 1.1368 | 2.0743 | 3.0628 | 1241.3072 | 1359.0267 | 2278.4712 | 3315.6351 | 0 | 0
|  |  |  | 895 | 1.0312 | 1.0796 | 1.9702 | 2.9091 | 1180.2731 | 1292.155 | 2166.5178 | 3152.7624 | 0 | 0 | 0 | 1.0855 | 1.1365 | 2.0739 | 3.0622 | 1242.3927 | 1360.1632 | 2280.545 | 3318.6973 | 0 | 0
|  |  |  | 896 | 1.031 | 1.0793 | 1.9698 | 2.9086 | 1181.3041 | 1293.2344 | 2168.4875 | 3155.671 | 0 | 0 | 0 | 1.0852 | 1.1361 | 2.0734 | 3.0616 | 1243.478 | 1361.2993 | 2282.6185 | 3321.7589 | 0 | 0
|  |  |  | 897 | 1.0307 | 1.079 | 1.9694 | 2.908 | 1182.3348 | 1294.3134 | 2170.4569 | 3158.579 | 0 | 0 | 0 | 1.085 | 1.1358 | 2.073 | 3.061 | 1244.563 | 1362.4352 | 2284.6915 | 3324.82 | 0 | 0
|  |  |  | 898 | 1.0305 | 1.0787 | 1.9689 | 2.9074 | 1183.3653 | 1295.3921 | 2172.4258 | 3161.4864 | 0 | 0 | 0 | 1.0847 | 1.1355 | 2.0726 | 3.0604 | 1245.6477 | 1363.5706 | 2286.7641 | 3327.8804 | 0 | 0
|  |  |  | 899 | 1.0302 | 1.0784 | 1.9685 | 2.9069 | 1184.3955 | 1296.4705 | 2174.3944 | 3164.3933 | 0 | 0 | 0 | 1.0844 | 1.1352 | 2.0721 | 3.0599 | 1246.7321 | 1364.7058 | 2288.8362 | 3330.9403 | 0 | 0
|  |  |  | 900 | 1.03 | 1.0781 | 1.9681 | 2.9063 | 1185.4255 | 1297.5486 | 2176.3625 | 3167.2996 | 0 | 0 | 0 | 1.0842 | 1.1349 | 2.0717 | 3.0593 | 1247.8163 | 1365.8407 | 2290.9079 | 3333.9995 | 0 | 0
|  |  |  | 901 | 1.0297 | 1.0778 | 1.9677 | 2.9057 | 1186.4552 | 1298.6264 | 2178.3302 | 3170.2053 | 0 | 0 | 0 | 1.0839 | 1.1345 | 2.0713 | 3.0587 | 1248.9002 | 1366.9752 | 2292.9792 | 3337.0582 | 0 | 0
|  |  |  | 902 | 1.0295 | 1.0775 | 1.9673 | 2.9052 | 1187.4847 | 1299.7039 | 2180.2976 | 3173.1105 | 0 | 0 | 0 | 1.0836 | 1.1342 | 2.0709 | 3.0581 | 1249.9839 | 1368.1094 | 2295.0501 | 3340.1163 | 0 | 0
|  |  |  | 903 | 1.0292 | 1.0772 | 1.9669 | 2.9046 | 1188.5139 | 1300.7811 | 2182.2645 | 3176.0151 | 0 | 0 | 0 | 1.0834 | 1.1339 | 2.0704 | 3.0575 | 1251.0672 | 1369.2433 | 2297.1205 | 3343.1738 | 0 | 0
|  |  |  | 904 | 1.029 | 1.0769 | 1.9665 | 2.9041 | 1189.5428 | 1301.858 | 2184.231 | 3178.9191 | 0 | 0 | 0 | 1.0831 | 1.1336 | 2.07 | 3.0569 | 1252.1504 | 1370.3769 | 2299.1905 | 3346.2307 | 0 | 0
|  |  |  | 905 | 1.0287 | 1.0766 | 1.9661 | 2.9035 | 1190.5716 | 1302.9346 | 2186.1971 | 3181.8226 | 0 | 0 | 0 | 1.0829 | 1.1333 | 2.0696 | 3.0563 | 1253.2332 | 1371.5101 | 2301.2601 | 3349.287 | 0 | 0
|  |  |  | 906 | 1.0285 | 1.0763 | 1.9657 | 2.9029 | 1191.6 | 1304.0109 | 2188.1628 | 3184.7256 | 0 | 0 | 0 | 1.0826 | 1.1329 | 2.0692 | 3.0557 | 1254.3158 | 1372.6431 | 2303.3293 | 3352.3427 | 0 | 0
|  |  |  | 907 | 1.0282 | 1.076 | 1.9653 | 2.9024 | 1192.6282 | 1305.0869 | 2190.1281 | 3187.6279 | 0 | 0 | 0 | 1.0823 | 1.1326 | 2.0687 | 3.0551 | 1255.3981 | 1373.7757 | 2305.398 | 3355.3978 | 0 | 0
|  |  |  | 908 | 1.028 | 1.0757 | 1.9649 | 2.9018 | 1193.6562 | 1306.1626 | 2192.093 | 3190.5298 | 0 | 0 | 0 | 1.0821 | 1.1323 | 2.0683 | 3.0545 | 1256.4802 | 1374.908 | 2307.4663 | 3358.4524 | 0 | 0
|  |  |  | 909 | 1.0277 | 1.0754 | 1.9645 | 2.9013 | 1194.6839 | 1307.2379 | 2194.0575 | 3193.431 | 0 | 0 | 0 | 1.0818 | 1.132 | 2.0679 | 3.054 | 1257.562 | 1376.0399 | 2309.5342 | 3361.5063 | 0 | 0
|  |  |  | 910 | 1.0275 | 1.0751 | 1.9641 | 2.9007 | 1195.7114 | 1308.313 | 2196.0216 | 3196.3317 | 0 | 0 | 0 | 1.0815 | 1.1317 | 2.0675 | 3.0534 | 1258.6436 | 1377.1716 | 2311.6016 | 3364.5597 | 0 | 0
|  |  |  | 911 | 1.0272 | 1.0748 | 1.9637 | 2.9002 | 1196.7386 | 1309.3878 | 2197.9853 | 3199.2319 | 0 | 0 | 0 | 1.0813 | 1.1313 | 2.067 | 3.0528 | 1259.7249 | 1378.303 | 2313.6687 | 3367.6125 | 0 | 0
|  |  |  | 912 | 1.027 | 1.0745 | 1.9633 | 2.8996 | 1197.7656 | 1310.4623 | 2199.9485 | 3202.1315 | 0 | 0 | 0 | 1.081 | 1.131 | 2.0666 | 3.0522 | 1260.8059 | 1379.434 | 2315.7353 | 3370.6647 | 0 | 0
|  |  |  | 913 | 1.0267 | 1.0742 | 1.9629 | 2.899 | 1198.7923 | 1311.5365 | 2201.9114 | 3205.0305 | 0 | 0 | 0 | 1.0808 | 1.1307 | 2.0662 | 3.0516 | 1261.8866 | 1380.5647 | 2317.8015 | 3373.7164 | 0 | 0
|  |  |  | 914 | 1.0265 | 1.0739 | 1.9625 | 2.8985 | 1199.8188 | 1312.6103 | 2203.8739 | 3207.929 | 0 | 0 | 0 | 1.0805 | 1.1304 | 2.0658 | 3.051 | 1262.9671 | 1381.6951 | 2319.8673 | 3376.7674 | 0 | 0
|  |  |  | 915 | 1.0262 | 1.0736 | 1.9621 | 2.8979 | 1200.845 | 1313.6839 | 2205.836 | 3210.827 | 0 | 0 | 0 | 1.0802 | 1.1301 | 2.0654 | 3.0505 | 1264.0474 | 1382.8252 | 2321.9326 | 3379.8179 | 0 | 0
|  |  |  | 916 | 1.026 | 1.0733 | 1.9617 | 2.8974 | 1201.871 | 1314.7572 | 2207.7977 | 3213.7244 | 0 | 0 | 0 | 1.08 | 1.1298 | 2.0649 | 3.0499 | 1265.1274 | 1383.9549 | 2323.9976 | 3382.8678 | 0 | 0
|  |  |  | 917 | 1.0257 | 1.073 | 1.9613 | 2.8968 | 1202.8967 | 1315.8302 | 2209.759 | 3216.6212 | 0 | 0 | 0 | 1.0797 | 1.1295 | 2.0645 | 3.0493 | 1266.2071 | 1385.0844 | 2326.0621 | 3385.9171 | 0 | 0
|  |  |  | 918 | 1.0255 | 1.0727 | 1.9609 | 2.8963 | 1203.9222 | 1316.9029 | 2211.7199 | 3219.5175 | 0 | 0 | 0 | 1.0795 | 1.1291 | 2.0641 | 3.0487 | 1267.2866 | 1386.2135 | 2328.1262 | 3388.9658 | 0 | 0
|  |  |  | 919 | 1.0252 | 1.0724 | 1.9605 | 2.8957 | 1204.9475 | 1317.9752 | 2213.6804 | 3222.4132 | 0 | 0 | 0 | 1.0792 | 1.1288 | 2.0637 | 3.0481 | 1268.3658 | 1387.3424 | 2330.1899 | 3392.0139 | 0 | 0
|  |  |  | 920 | 1.025 | 1.0721 | 1.9601 | 2.8952 | 1205.9725 | 1319.0473 | 2215.6405 | 3225.3084 | 0 | 0 | 0 | 1.0789 | 1.1285 | 2.0633 | 3.0476 | 1269.4447 | 1388.4709 | 2332.2531 | 3395.0615 | 0 | 0
|  |  |  | 921 | 1.0248 | 1.0718 | 1.9597 | 2.8946 | 1206.9972 | 1320.1191 | 2217.6002 | 3228.2031 | 0 | 0 | 0 | 1.0787 | 1.1282 | 2.0628 | 3.047 | 1270.5234 | 1389.5991 | 2334.316 | 3398.1085 | 0 | 0
|  |  |  | 922 | 1.0245 | 1.0715 | 1.9593 | 2.8941 | 1208.0218 | 1321.1906 | 2219.5595 | 3231.0972 | 0 | 0 | 0 | 1.0784 | 1.1279 | 2.0624 | 3.0464 | 1271.6018 | 1390.727 | 2336.3784 | 3401.1549 | 0 | 0
|  |  |  | 923 | 1.0243 | 1.0712 | 1.9589 | 2.8936 | 1209.046 | 1322.2618 | 2221.5184 | 3233.9907 | 0 | 0 | 0 | 1.0782 | 1.1276 | 2.062 | 3.0458 | 1272.68 | 1391.8545 | 2338.4404 | 3404.2008 | 0 | 0
|  |  |  | 924 | 1.024 | 1.0709 | 1.9585 | 2.893 | 1210.07 | 1323.3327 | 2223.4769 | 3236.8837 | 0 | 0 | 0 | 1.0779 | 1.1273 | 2.0616 | 3.0453 | 1273.7579 | 1392.9818 | 2340.502 | 3407.246 | 0 | 0
|  |  |  | 925 | 1.0238 | 1.0706 | 1.9581 | 2.8925 | 1211.0938 | 1324.4033 | 2225.435 | 3239.7762 | 0 | 0 | 0 | 1.0777 | 1.127 | 2.0612 | 3.0447 | 1274.8356 | 1394.1088 | 2342.5632 | 3410.2907 | 0 | 0
|  |  |  | 926 | 1.0235 | 1.0703 | 1.9577 | 2.8919 | 1212.1174 | 1325.4737 | 2227.3927 | 3242.6681 | 0 | 0 | 0 | 1.0774 | 1.1266 | 2.0608 | 3.0441 | 1275.913 | 1395.2354 | 2344.6239 | 3413.3349 | 0 | 0
|  |  |  | 927 | 1.0233 | 1.07 | 1.9573 | 2.8914 | 1213.1407 | 1326.5437 | 2229.3501 | 3245.5595 | 0 | 0 | 0 | 1.0772 | 1.1263 | 2.0604 | 3.0436 | 1276.9902 | 1396.3618 | 2346.6843 | 3416.3784 | 0 | 0
|  |  |  | 928 | 1.0231 | 1.0697 | 1.9569 | 2.8908 | 1214.1637 | 1327.6134 | 2231.307 | 3248.4503 | 0 | 0 | 0 | 1.0769 | 1.126 | 2.0599 | 3.043 | 1278.0671 | 1397.4878 | 2348.7442 | 3419.4214 | 0 | 0
|  |  |  | 929 | 1.0228 | 1.0694 | 1.9565 | 2.8903 | 1215.1865 | 1328.6828 | 2233.2636 | 3251.3406 | 0 | 0 | 0 | 1.0766 | 1.1257 | 2.0595 | 3.0424 | 1279.1437 | 1398.6135 | 2350.8038 | 3422.4638 | 0 | 0
|  |  |  | 930 | 1.0226 | 1.0691 | 1.9562 | 2.8897 | 1216.2091 | 1329.752 | 2235.2197 | 3254.2304 | 0 | 0 | 0 | 1.0764 | 1.1254 | 2.0591 | 3.0418 | 1280.2201 | 1399.7389 | 2352.8629 | 3425.5056 | 0 | 0
|  |  |  | 931 | 1.0223 | 1.0688 | 1.9558 | 2.8892 | 1217.2314 | 1330.8208 | 2237.1755 | 3257.1196 | 0 | 0 | 0 | 1.0761 | 1.1251 | 2.0587 | 3.0413 | 1281.2962 | 1400.864 | 2354.9216 | 3428.5469 | 0 | 0
|  |  |  | 932 | 1.0221 | 1.0686 | 1.9554 | 2.8887 | 1218.2535 | 1331.8894 | 2239.1309 | 3260.0082 | 0 | 0 | 0 | 1.0759 | 1.1248 | 2.0583 | 3.0407 | 1282.3721 | 1401.9888 | 2356.9799 | 3431.5876 | 0 | 0
|  |  |  | 933 | 1.0218 | 1.0683 | 1.955 | 2.8881 | 1219.2753 | 1332.9576 | 2241.0858 | 3262.8964 | 0 | 0 | 0 | 1.0756 | 1.1245 | 2.0579 | 3.0401 | 1283.4477 | 1403.1133 | 2359.0377 | 3434.6277 | 0 | 0
|  |  |  | 934 | 1.0216 | 1.068 | 1.9546 | 2.8876 | 1220.2969 | 1334.0256 | 2243.0404 | 3265.784 | 0 | 0 | 0 | 1.0754 | 1.1242 | 2.0575 | 3.0396 | 1284.5231 | 1404.2375 | 2361.0952 | 3437.6673 | 0 | 0
|  |  |  | 935 | 1.0214 | 1.0677 | 1.9542 | 2.8871 | 1221.3183 | 1335.0933 | 2244.9946 | 3268.671 | 0 | 0 | 0 | 1.0751 | 1.1239 | 2.0571 | 3.039 | 1285.5982 | 1405.3614 | 2363.1523 | 3440.7063 | 0 | 0
|  |  |  | 936 | 1.0211 | 1.0674 | 1.9538 | 2.8865 | 1222.3394 | 1336.1607 | 2246.9485 | 3271.5575 | 0 | 0 | 0 | 1.0749 | 1.1236 | 2.0567 | 3.0384 | 1286.6731 | 1406.4849 | 2365.2089 | 3443.7448 | 0 | 0
|  |  |  | 937 | 1.0209 | 1.0671 | 1.9534 | 2.886 | 1223.3603 | 1337.2278 | 2248.9019 | 3274.4435 | 0 | 0 | 0 | 1.0746 | 1.1233 | 2.0562 | 3.0379 | 1287.7477 | 1407.6082 | 2367.2652 | 3446.7826 | 0 | 0
|  |  |  | 938 | 1.0206 | 1.0668 | 1.953 | 2.8854 | 1224.3809 | 1338.2946 | 2250.8549 | 3277.3289 | 0 | 0 | 0 | 1.0744 | 1.123 | 2.0558 | 3.0373 | 1288.822 | 1408.7311 | 2369.321 | 3449.8199 | 0 | 0
|  |  |  | 939 | 1.0204 | 1.0665 | 1.9527 | 2.8849 | 1225.4013 | 1339.3611 | 2252.8076 | 3280.2138 | 0 | 0 | 0 | 1.0741 | 1.1227 | 2.0554 | 3.0367 | 1289.8961 | 1409.8538 | 2371.3764 | 3452.8567 | 0 | 0
|  |  |  | 940 | 1.0202 | 1.0662 | 1.9523 | 2.8844 | 1226.4215 | 1340.4273 | 2254.7599 | 3283.0982 | 0 | 0 | 0 | 1.0739 | 1.1223 | 2.055 | 3.0362 | 1290.97 | 1410.9761 | 2373.4314 | 3455.8929 | 0 | 0
|  |  |  | 941 | 1.0199 | 1.0659 | 1.9519 | 2.8838 | 1227.4414 | 1341.4933 | 2256.7117 | 3285.9821 | 0 | 0 | 0 | 1.0736 | 1.122 | 2.0546 | 3.0356 | 1292.0436 | 1412.0982 | 2375.486 | 3458.9285 | 0 | 0
|  |  |  | 942 | 1.0197 | 1.0657 | 1.9515 | 2.8833 | 1228.4611 | 1342.5589 | 2258.6632 | 3288.8654 | 0 | 0 | 0 | 1.0734 | 1.1217 | 2.0542 | 3.0351 | 1293.117 | 1413.2199 | 2377.5402 | 3461.9635 | 0 | 0
|  |  |  | 943 | 1.0194 | 1.0654 | 1.9511 | 2.8828 | 1229.4806 | 1343.6243 | 2260.6143 | 3291.7481 | 0 | 0 | 0 | 1.0731 | 1.1214 | 2.0538 | 3.0345 | 1294.1901 | 1414.3414 | 2379.594 | 3464.998 | 0 | 0
|  |  |  | 944 | 1.0192 | 1.0651 | 1.9507 | 2.8822 | 1230.4998 | 1344.6894 | 2262.5651 | 3294.6304 | 0 | 0 | 0 | 1.0729 | 1.1211 | 2.0534 | 3.0339 | 1295.2629 | 1415.4625 | 2381.6474 | 3468.032 | 0 | 0
|  |  |  | 945 | 1.019 | 1.0648 | 1.9503 | 2.8817 | 1231.5187 | 1345.7542 | 2264.5154 | 3297.5121 | 0 | 0 | 0 | 1.0726 | 1.1208 | 2.053 | 3.0334 | 1296.3355 | 1416.5833 | 2383.7004 | 3471.0653 | 0 | 0
|  |  |  | 946 | 1.0187 | 1.0645 | 1.95 | 2.8812 | 1232.5375 | 1346.8187 | 2266.4654 | 3300.3933 | 0 | 0 | 0 | 1.0724 | 1.1205 | 2.0526 | 3.0328 | 1297.4079 | 1417.7039 | 2385.753 | 3474.0982 | 0 | 0
|  |  |  | 947 | 1.0185 | 1.0642 | 1.9496 | 2.8806 | 1233.556 | 1347.8829 | 2268.4149 | 3303.2739 | 0 | 0 | 0 | 1.0721 | 1.1202 | 2.0522 | 3.0323 | 1298.48 | 1418.8241 | 2387.8052 | 3477.1304 | 0 | 0
|  |  |  | 948 | 1.0183 | 1.0639 | 1.9492 | 2.8801 | 1234.5742 | 1348.9468 | 2270.3641 | 3306.154 | 0 | 0 | 0 | 1.0719 | 1.1199 | 2.0518 | 3.0317 | 1299.5518 | 1419.944 | 2389.857 | 3480.1621 | 0 | 0
|  |  |  | 949 | 1.018 | 1.0636 | 1.9488 | 2.8796 | 1235.5923 | 1350.0105 | 2272.3129 | 3309.0336 | 0 | 0 | 0 | 1.0716 | 1.1196 | 2.0514 | 3.0311 | 1300.6234 | 1421.0636 | 2391.9084 | 3483.1933 | 0 | 0
|  |  |  | 950 | 1.0178 | 1.0634 | 1.9484 | 2.8791 | 1236.6101 | 1351.0738 | 2274.2614 | 3311.9127 | 0 | 0 | 0 | 1.0714 | 1.1193 | 2.051 | 3.0306 | 1301.6948 | 1422.183 | 2393.9593 | 3486.2239 | 0 | 0
|  |  |  | 951 | 1.0176 | 1.0631 | 1.948 | 2.8785 | 1237.6276 | 1352.1369 | 2276.2094 | 3314.7912 | 0 | 0 | 0 | 1.0711 | 1.119 | 2.0506 | 3.03 | 1302.7659 | 1423.302 | 2396.0099 | 3489.2539 | 0 | 0
|  |  |  | 952 | 1.0173 | 1.0628 | 1.9477 | 2.878 | 1238.6449 | 1353.1997 | 2278.1571 | 3317.6692 | 0 | 0 | 0 | 1.0709 | 1.1187 | 2.0502 | 3.0295 | 1303.8368 | 1424.4207 | 2398.0601 | 3492.2834 | 0 | 0
|  |  |  | 953 | 1.0171 | 1.0625 | 1.9473 | 2.8775 | 1239.662 | 1354.2622 | 2280.1044 | 3320.5467 | 0 | 0 | 0 | 1.0706 | 1.1184 | 2.0498 | 3.0289 | 1304.9074 | 1425.5392 | 2400.1099 | 3495.3123 | 0 | 0
|  |  |  | 954 | 1.0169 | 1.0622 | 1.9469 | 2.877 | 1240.6789 | 1355.3244 | 2282.0513 | 3323.4237 | 0 | 0 | 0 | 1.0704 | 1.1181 | 2.0494 | 3.0284 | 1305.9778 | 1426.6573 | 2402.1592 | 3498.3407 | 0 | 0
|  |  |  | 955 | 1.0166 | 1.0619 | 1.9465 | 2.8764 | 1241.6955 | 1356.3864 | 2283.9978 | 3326.3001 | 0 | 0 | 0 | 1.0701 | 1.1178 | 2.049 | 3.0278 | 1307.0479 | 1427.7751 | 2404.2082 | 3501.3685 | 0 | 0
|  |  |  | 956 | 1.0164 | 1.0617 | 1.9461 | 2.8759 | 1242.7119 | 1357.448 | 2285.9439 | 3329.176 | 0 | 0 | 0 | 1.0699 | 1.1175 | 2.0486 | 3.0273 | 1308.1178 | 1428.8926 | 2406.2568 | 3504.3958 | 0 | 0
|  |  |  | 957 | 1.0161 | 1.0614 | 1.9458 | 2.8754 | 1243.728 | 1358.5094 | 2287.8897 | 3332.0514 | 0 | 0 | 0 | 1.0696 | 1.1172 | 2.0482 | 3.0267 | 1309.1874 | 1430.0099 | 2408.305 | 3507.4225 | 0 | 0
|  |  |  | 958 | 1.0159 | 1.0611 | 1.9454 | 2.8749 | 1244.7439 | 1359.5705 | 2289.8351 | 3334.9262 | 0 | 0 | 0 | 1.0694 | 1.1169 | 2.0478 | 3.0262 | 1310.2568 | 1431.1268 | 2410.3527 | 3510.4487 | 0 | 0
|  |  |  | 959 | 1.0157 | 1.0608 | 1.945 | 2.8743 | 1245.7596 | 1360.6313 | 2291.7801 | 3337.8006 | 0 | 0 | 0 | 1.0691 | 1.1166 | 2.0474 | 3.0256 | 1311.3259 | 1432.2435 | 2412.4001 | 3513.4743 | 0 | 0
|  |  |  | 960 | 1.0154 | 1.0605 | 1.9446 | 2.8738 | 1246.7751 | 1361.6918 | 2293.7247 | 3340.6744 | 0 | 0 | 0 | 1.0689 | 1.1163 | 2.047 | 3.0251 | 1312.3948 | 1433.3598 | 2414.4471 | 3516.4994 | 0 | 0
|  |  |  | 961 | 1.0152 | 1.0602 | 1.9443 | 2.8733 | 1247.7903 | 1362.7521 | 2295.669 | 3343.5477 | 0 | 0 | 0 | 1.0686 | 1.116 | 2.0466 | 3.0245 | 1313.4635 | 1434.4758 | 2416.4937 | 3519.5239 | 0 | 0
|  |  |  | 962 | 1.015 | 1.06 | 1.9439 | 2.8728 | 1248.8053 | 1363.812 | 2297.6129 | 3346.4205 | 0 | 0 | 0 | 1.0684 | 1.1158 | 2.0462 | 3.024 | 1314.5319 | 1435.5916 | 2418.5399 | 3522.5479 | 0 | 0
|  |  |  | 963 | 1.0148 | 1.0597 | 1.9435 | 2.8723 | 1249.82 | 1364.8717 | 2299.5564 | 3349.2927 | 0 | 0 | 0 | 1.0682 | 1.1155 | 2.0458 | 3.0234 | 1315.6 | 1436.7071 | 2420.5857 | 3525.5713 | 0 | 0
|  |  |  | 964 | 1.0145 | 1.0594 | 1.9431 | 2.8717 | 1250.8345 | 1365.9311 | 2301.4995 | 3352.1645 | 0 | 0 | 0 | 1.0679 | 1.1152 | 2.0454 | 3.0229 | 1316.6679 | 1437.8222 | 2422.6311 | 3528.5942 | 0 | 0
|  |  |  | 965 | 1.0143 | 1.0591 | 1.9428 | 2.8712 | 1251.8488 | 1366.9902 | 2303.4423 | 3355.0357 | 0 | 0 | 0 | 1.0677 | 1.1149 | 2.045 | 3.0223 | 1317.7356 | 1438.9371 | 2424.6761 | 3531.6165 | 0 | 0
|  |  |  | 966 | 1.0141 | 1.0588 | 1.9424 | 2.8707 | 1252.8629 | 1368.0491 | 2305.3846 | 3357.9064 | 0 | 0 | 0 | 1.0674 | 1.1146 | 2.0446 | 3.0218 | 1318.803 | 1440.0517 | 2426.7207 | 3534.6383 | 0 | 0
|  |  |  | 967 | 1.0138 | 1.0586 | 1.942 | 2.8702 | 1253.8767 | 1369.1076 | 2307.3267 | 3360.7766 | 0 | 0 | 0 | 1.0672 | 1.1143 | 2.0442 | 3.0212 | 1319.8702 | 1441.1659 | 2428.7649 | 3537.6596 | 0 | 0
|  |  |  | 968 | 1.0136 | 1.0583 | 1.9416 | 2.8697 | 1254.8903 | 1370.1659 | 2309.2683 | 3363.6463 | 0 | 0 | 0 | 1.0669 | 1.114 | 2.0438 | 3.0207 | 1320.9372 | 1442.2799 | 2430.8087 | 3540.6803 | 0 | 0
|  |  |  | 969 | 1.0134 | 1.058 | 1.9413 | 2.8692 | 1255.9037 | 1371.2239 | 2311.2096 | 3366.5154 | 0 | 0 | 0 | 1.0667 | 1.1137 | 2.0434 | 3.0202 | 1322.0039 | 1443.3936 | 2432.8522 | 3543.7004 | 0 | 0
|  |  |  | 970 | 1.0131 | 1.0577 | 1.9409 | 2.8686 | 1256.9168 | 1372.2817 | 2313.1504 | 3369.3841 | 0 | 0 | 0 | 1.0665 | 1.1134 | 2.043 | 3.0196 | 1323.0703 | 1444.507 | 2434.8952 | 3546.7201 | 0 | 0
|  |  |  | 971 | 1.0129 | 1.0575 | 1.9405 | 2.8681 | 1257.9297 | 1373.3391 | 2315.091 | 3372.2522 | 0 | 0 | 0 | 1.0662 | 1.1131 | 2.0426 | 3.0191 | 1324.1366 | 1445.6201 | 2436.9378 | 3549.7391 | 0 | 0
|  |  |  | 972 | 1.0127 | 1.0572 | 1.9401 | 2.8676 | 1258.9424 | 1374.3963 | 2317.0311 | 3375.1198 | 0 | 0 | 0 | 1.066 | 1.1128 | 2.0423 | 3.0185 | 1325.2025 | 1446.7329 | 2438.9801 | 3552.7577 | 0 | 0
|  |  |  | 973 | 1.0124 | 1.0569 | 1.9398 | 2.8671 | 1259.9549 | 1375.4532 | 2318.9709 | 3377.9869 | 0 | 0 | 0 | 1.0657 | 1.1125 | 2.0419 | 3.018 | 1326.2683 | 1447.8455 | 2441.022 | 3555.7757 | 0 | 0
|  |  |  | 974 | 1.0122 | 1.0566 | 1.9394 | 2.8666 | 1260.9671 | 1376.5098 | 2320.9103 | 3380.8535 | 0 | 0 | 0 | 1.0655 | 1.1122 | 2.0415 | 3.0175 | 1327.3338 | 1448.9577 | 2443.0634 | 3558.7931 | 0 | 0
|  |  |  | 975 | 1.012 | 1.0563 | 1.939 | 2.8661 | 1261.9791 | 1377.5662 | 2322.8493 | 3383.7195 | 0 | 0 | 0 | 1.0653 | 1.1119 | 2.0411 | 3.0169 | 1328.399 | 1450.0696 | 2445.1045 | 3561.8101 | 0 | 0
|  |  |  | 976 | 1.0118 | 1.0561 | 1.9387 | 2.8656 | 1262.9908 | 1378.6222 | 2324.788 | 3386.5851 | 0 | 0 | 0 | 1.065 | 1.1117 | 2.0407 | 3.0164 | 1329.464 | 1451.1813 | 2447.1452 | 3564.8264 | 0 | 0
|  |  |  | 977 | 1.0115 | 1.0558 | 1.9383 | 2.8651 | 1264.0024 | 1379.678 | 2326.7263 | 3389.4502 | 0 | 0 | 0 | 1.0648 | 1.1114 | 2.0403 | 3.0158 | 1330.5288 | 1452.2927 | 2449.1855 | 3567.8423 | 0 | 0
|  |  |  | 978 | 1.0113 | 1.0555 | 1.9379 | 2.8645 | 1265.0137 | 1380.7336 | 2328.6642 | 3392.3147 | 0 | 0 | 0 | 1.0645 | 1.1111 | 2.0399 | 3.0153 | 1331.5933 | 1453.4037 | 2451.2255 | 3570.8576 | 0 | 0
|  |  |  | 979 | 1.0111 | 1.0552 | 1.9376 | 2.864 | 1266.0248 | 1381.7888 | 2330.6017 | 3395.1787 | 0 | 0 | 0 | 1.0643 | 1.1108 | 2.0395 | 3.0148 | 1332.6576 | 1454.5145 | 2453.265 | 3573.8724 | 0 | 0
|  |  |  | 980 | 1.0109 | 1.055 | 1.9372 | 2.8635 | 1267.0356 | 1382.8438 | 2332.5389 | 3398.0423 | 0 | 0 | 0 | 1.0641 | 1.1105 | 2.0391 | 3.0142 | 1333.7217 | 1455.625 | 2455.3041 | 3576.8866 | 0 | 0
|  |  |  | 981 | 1.0106 | 1.0547 | 1.9368 | 2.863 | 1268.0462 | 1383.8985 | 2334.4757 | 3400.9053 | 0 | 0 | 0 | 1.0638 | 1.1102 | 2.0388 | 3.0137 | 1334.7855 | 1456.7352 | 2457.3429 | 3579.9003 | 0 | 0
|  |  |  | 982 | 1.0104 | 1.0544 | 1.9365 | 2.8625 | 1269.0566 | 1384.9529 | 2336.4122 | 3403.7678 | 0 | 0 | 0 | 1.0636 | 1.1099 | 2.0384 | 3.0132 | 1335.8491 | 1457.8451 | 2459.3813 | 3582.9134 | 0 | 0
|  |  |  | 983 | 1.0102 | 1.0541 | 1.9361 | 2.862 | 1270.0668 | 1386.007 | 2338.3483 | 3406.6298 | 0 | 0 | 0 | 1.0633 | 1.1096 | 2.038 | 3.0126 | 1336.9124 | 1458.9548 | 2461.4193 | 3585.9261 | 0 | 0
|  |  |  | 984 | 1.0099 | 1.0539 | 1.9357 | 2.8615 | 1271.0768 | 1387.0609 | 2340.284 | 3409.4913 | 0 | 0 | 0 | 1.0631 | 1.1093 | 2.0376 | 3.0121 | 1337.9755 | 1460.0641 | 2463.4569 | 3588.9382 | 0 | 0
|  |  |  | 985 | 1.0097 | 1.0536 | 1.9354 | 2.861 | 1272.0865 | 1388.1145 | 2342.2194 | 3412.3523 | 0 | 0 | 0 | 1.0629 | 1.1091 | 2.0372 | 3.0116 | 1339.0384 | 1461.1732 | 2465.4941 | 3591.9497 | 0 | 0
|  |  |  | 986 | 1.0095 | 1.0533 | 1.935 | 2.8605 | 1273.096 | 1389.1678 | 2344.1544 | 3415.2127 | 0 | 0 | 0 | 1.0626 | 1.1088 | 2.0368 | 3.011 | 1340.101 | 1462.2819 | 2467.5309 | 3594.9608 | 0 | 0
|  |  |  | 987 | 1.0093 | 1.0531 | 1.9346 | 2.86 | 1274.1052 | 1390.2209 | 2346.089 | 3418.0727 | 0 | 0 | 0 | 1.0624 | 1.1085 | 2.0364 | 3.0105 | 1341.1634 | 1463.3904 | 2469.5673 | 3597.9713 | 0 | 0
|  |  |  | 988 | 1.009 | 1.0528 | 1.9343 | 2.8595 | 1275.1143 | 1391.2737 | 2348.0232 | 3420.9322 | 0 | 0 | 0 | 1.0622 | 1.1082 | 2.0361 | 3.01 | 1342.2256 | 1464.4986 | 2471.6034 | 3600.9812 | 0 | 0
|  |  |  | 989 | 1.0088 | 1.0525 | 1.9339 | 2.859 | 1276.1231 | 1392.3262 | 2349.9571 | 3423.7912 | 0 | 0 | 0 | 1.0619 | 1.1079 | 2.0357 | 3.0094 | 1343.2875 | 1465.6065 | 2473.6391 | 3603.9907 | 0 | 0
|  |  |  | 990 | 1.0086 | 1.0522 | 1.9335 | 2.8585 | 1277.1317 | 1393.3785 | 2351.8907 | 3426.6496 | 0 | 0 | 0 | 1.0617 | 1.1076 | 2.0353 | 3.0089 | 1344.3492 | 1466.7142 | 2475.6744 | 3606.9996 | 0 | 0
|  |  |  | 991 | 1.0084 | 1.052 | 1.9332 | 2.858 | 1278.1401 | 1394.4304 | 2353.8238 | 3429.5076 | 0 | 0 | 0 | 1.0614 | 1.1073 | 2.0349 | 3.0084 | 1345.4106 | 1467.8215 | 2477.7093 | 3610.008 | 0 | 0
|  |  |  | 992 | 1.0082 | 1.0517 | 1.9328 | 2.8575 | 1279.1482 | 1395.4821 | 2355.7566 | 3432.365 | 0 | 0 | 0 | 1.0612 | 1.1071 | 2.0345 | 3.0079 | 1346.4718 | 1468.9286 | 2479.7438 | 3613.0158 | 0 | 0
|  |  |  | 993 | 1.0079 | 1.0514 | 1.9324 | 2.857 | 1280.1562 | 1396.5336 | 2357.6891 | 3435.222 | 0 | 0 | 0 | 1.061 | 1.1068 | 2.0342 | 3.0073 | 1347.5328 | 1470.0353 | 2481.778 | 3616.0232 | 0 | 0
|  |  |  | 994 | 1.0077 | 1.0512 | 1.9321 | 2.8565 | 1281.1639 | 1397.5847 | 2359.6212 | 3438.0785 | 0 | 0 | 0 | 1.0607 | 1.1065 | 2.0338 | 3.0068 | 1348.5935 | 1471.1418 | 2483.8118 | 3619.03 | 0 | 0
|  |  |  | 995 | 1.0075 | 1.0509 | 1.9317 | 2.856 | 1282.1713 | 1398.6356 | 2361.5529 | 3440.9344 | 0 | 0 | 0 | 1.0605 | 1.1062 | 2.0334 | 3.0063 | 1349.654 | 1472.248 | 2485.8451 | 3622.0362 | 0 | 0
|  |  |  | 996 | 1.0073 | 1.0506 | 1.9314 | 2.8555 | 1283.1786 | 1399.6862 | 2363.4842 | 3443.7899 | 0 | 0 | 0 | 1.0603 | 1.1059 | 2.033 | 3.0057 | 1350.7143 | 1473.3539 | 2487.8782 | 3625.042 | 0 | 0
|  |  |  | 997 | 1.007 | 1.0504 | 1.931 | 2.855 | 1284.1856 | 1400.7366 | 2365.4152 | 3446.6449 | 0 | 0 | 0 | 1.06 | 1.1056 | 2.0326 | 3.0052 | 1351.7744 | 1474.4596 | 2489.9108 | 3628.0472 | 0 | 0
|  |  |  | 998 | 1.0068 | 1.0501 | 1.9306 | 2.8545 | 1285.1925 | 1401.7867 | 2367.3459 | 3449.4993 | 0 | 0 | 0 | 1.0598 | 1.1054 | 2.0323 | 3.0047 | 1352.8342 | 1475.5649 | 2491.943 | 3631.0519 | 0 | 0
|  |  |  | 999 | 1.0066 | 1.0498 | 1.9303 | 2.854 | 1286.199 | 1402.8365 | 2369.2762 | 3452.3533 | 0 | 0 | 0 | 1.0596 | 1.1051 | 2.0319 | 3.0042 | 1353.8937 | 1476.67 | 2493.9749 | 3634.0561 | 0 | 0
|  |  |  | 1000 | 1.0064 | 1.0496 | 1.9299 | 2.8535 | 1287.2054 | 1403.8861 | 2371.2061 | 3455.2068 | 0 | 0 | 0 | 1.0593 | 1.1048 | 2.0315 | 3.0037 | 1354.9531 | 1477.7748 | 2496.0064 | 3637.0598 | 0 | 0

## Version Control
Versions
| Version no. | Date | Detail | Name
1 | V1.0 | 2017-02-01 | IMP/001/911: LV COP V4.0 alignment; to calculate the Design Demand with new ADMD Guidance on Tx Sizing | Rimnesh Shah
2 | V1.1 | 2017-11-21 | Added general notes tab to provide the user with assistance on how to use the tool | Rimnesh Shah
3 | V2.0 | 2018-08-15 | Changed the formula for 16A EV chargers to match that in IMP/001/911 and added 32A EV charger as an option | Paris Hadjiodysseos
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Notes on Graph (hidden)
To add or redefine ranges: Create the rows and columns in the spreadsheet as required. Enter the Excel Name Manager from the Formulas tab on the ribbon. The named ranges used are dynamic. They use the INDIRECT function (great tool) to turn a string into an Excel range reference. The ranges are then defined partly by a static string (the “Calculations!F3:F” bit) and then they use a formula (targeted at the defined number of customers of a given type, or the maximum of all different types) to take the other end of the range. Whatever goes in formulaic bit, it must boil down to a single integer number greater than 2. The “&” sign in the formula then concatenates this number to the end of the static bit, and then the INDIRECT function converts the whole thing into a range. This range can then be referred to by its name. To add these to the chart you can set them as the data source for a series, but you may need a fully-qualified name (i.e. the whole workbook’s file name, then the worksheet, then the name).