## Introduction
Distribution Network Options Assessment (DNOA) Report 1 Datasheets 2024
Summary Page
Published March 2024
This document is the excel format version of the Distribution Network Options Assessment (DNOA) Report. The purpose of the DNOA is to transparently communicate our investment decisions and future network intervention plans to stakeholders, and to highlight areas where Flexibility Services may be required over the next five years. This benefits our stakeholders by enabling them to factor our network plans and requirements for Flexibility Services into their planning.
Contents
Worksheet | Description
Table 1 | Our planned network interventions over the next 5 years for our whole network down to the primary substation level

## Table 1
[12 empty] | Flexibility Required (Best View) (MW) |  |  |  |  | Flexibility Procured (MW) |  | Flexibility Procured (%)
Substation Name | Voltages | Substation Postcode | Licence Area | Number of Transformers | Transformer Rating ONAN/OFAF (MVA) | Substation Capacity (MVA) | DNOA Intervention Decision | Constraint Year | Constraint Season | Flexibility ceiling price (£/MWh) | Reinforcement delivery time (years) | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023/24 | 2024/25 | 2023/24 | 2024/25 | Postal Sectors | Scheme Description
Crowle | 66/11kV | DN17 4BB | Yorkshire | Single | 7.5/15 | 4.5 | Flexibility/Reinforcement | 2023/24 | Autumn and Winter | 141 | 2 | 0.5 | 0.5 | 0.6 | 0.7 | 1 | 0.05 | 0.12 | 11 | 23 | DN17 1; DN17 3; DN17 4; DN8 5; DN9 1 | — Crowle 66/11 kV substation is equipped with a single 7.5 MVA transformer, and has a firm capacity of 4.5 MVA. Network load is forecasted to exceed firm capacity in 2023/24. — Insufficient Flexibility Services have been procured. Hence we will start planning reinforcement works and use partial Flexibility Services to help relieve the network overload in the interim. — We will continue flexibility tendering and may stall reinforcement works plans if enough flexibility is procured.
Holme Upon Spalding Moor | 33/11kV | YO43 4BX | Yorkshire | Single | 2024-12-12 | 8 | Signpost | 2026/27 | TBC | TBC | TBC | - | - | - | 0.1 | 0.3 | - | - | 0 | 0 | DN14 7; HU15 2; YO42 1; YO42 4; YO43 3; YO43 4; YO62 5; YO8 6; YO8 7 | — Holme Upon Spalding Moor 33/11 kV substation is equipped with a single 24 MVA transformer, and has a firm capacity of 8 MVA. Network load is forecasted to exceed firm capacity in 2026/27. — To relieve the network overload, we have signposted the need for Flexibility Services in our 2023 Autumn flexibility tendering.
Kirkburn | 66/11kV | YO25 9EH | Yorkshire | Single | 15/30 | 8 | Signpost | 2027/28 | TBC | TBC | TBC | - | - | - | - | 0.4 | - | - | 0 | 0 | YO17 9; YO25 0; YO25 1; YO25 3; YO25 4; YO25 8; YO25 9; YO42 1 | — Kirkburn 66/11 kV substation is equipped with a single 15/30 MVA transformer, and has a firm capacity of 8 MVA. Network load is forecasted to exceed firm capacity in 2027/28. — To relieve the network overload, we have signposted the need for Flexibility Services in our 2023 Autumn flexibility tendering.
Martongate | 66/11kV | YO16 6RX | Yorkshire | Double | 10/12.5 | 14.1 | Signpost | 2027/28 | TBC | TBC | TBC | - | - | - | - | 0.8 | - | - | 0 | 0 | YO14 0; YO14 9; YO15 1; YO15 2; YO16 4; YO16 6; YO16 7 | — Martongate 66/11 kV substation is equipped with 2x 12.5 MVA transformers, and has a firm capacity of 14.1 MVA. Network load is forecasted to exceed firm capacity in 2027/28. — To relieve the network overload, we have signposted the need for Flexibility Services in our 2023 Autumn flexibility tendering.
Monkseaton | 33/11kV | NE25 9AF | Northeast | Double | 15/18.75 | 20.5 | Signpost | 2027/28 | TBC | TBC | TBC | - | - | - | - | 0.4 | - | - | 0 | 0 | NE25 0; NE25 8; NE25 9; NE26 1; NE26 2; NE26 3; NE26 4; NE27 0; NE29 8 | — Monseaton 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 20.5 MVA. Network load is forecasted to exceed firm capacity in 2027/28. — To relieve the network overload, we have signposted the need for Flexibility Services in our 2023 Autumn flexibility tendering.
Ripon | 33/11kV | HG4 1QE | Northeast | Double | 2024-12-12 | 18.7 | Signpost | 2027/28 | TBC | TBC | TBC | - | - | - | - | 0.3 | - | - | 0 | 0 | DL7 9; DL8 2; HG3 3; HG4 1; HG4 2; HG4 3; HG4 4; HG4 5; YO7 3; YO7 4 | — Ripon 33/11 kV substation is equipped with 2x 12/24 MVA transformers, and has a firm capacity of 18.7 MVA. Network load is forecasted to exceed firm capacity in 2027/28. — To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Southgate | 33/11kV | YO43 3BE | Yorkshire | Single | 11.5/23 | 8 | Flexibility/Reinforcement | 2023/24 | Autumn and Winter | 900 | 2 | 0.2 | 0.3 | 0.4 | 0.6 | 0.9 | 0.14 | 0.21 | 70 | 69 | HU15 2; HU17 7; YO25 9; YO42 4; YO4 3; YO43 3; YO43 4 | — Southgate 33/11 kV substation is equipped with a single 11.5/23 MVA transformer, and has a firm capacity of 8.0 MVA. Network load is forecasted to exceed firm capacity in 2023/24. — Insufficient Flexibility Services have been procured. Hence we will start planning reinforcement works and use partial Flexibility Services to help relieve the network overload in the interim. — We will continue flexibility tendering and may stall reinforcement works plans if enough flexibility is procured.