## Introduction
Distribution Network Options Assessment (DNOA) Report 1 2025 Datasheets
Summary Page
Published March 2025
This document is the excel format version of the Distribution Network Options Assessment (DNOA) Report. The purpose of the DNOA is to transparently communicate our investment decisions and future network intervention plans to stakeholders, and to highlight areas where Flexibility Services may be required over the next five years. This benefits our stakeholders by enabling them to factor our network plans and requirements for Flexibility Services into their planning.
Contents
Worksheet | Description
Table 1 | Our planned network interventions over the next 5 years for our whole network down to the primary substation level

## DNOA 3 March 2025 Data Table
[13 empty] | Flexibility Required (NPg Reference Scenario) (MW) |  |  |  |  | Flexibility Procured (MW) |  | Flexibility Procured (%) |  | Expressions of Intterest received to date (MW)
Licence Area | DNOA 3 Mar 2025 Decision | Substation Name | NPg Region | Voltages | Substation Postcode | Number of Transformers | Transformer Rating ONAN/OFAF (MVA) | Substation Capacity (MVA) | Constraint Year | Constraint Season | Flexibility ceiling price (£/MWh) | Reinforcement delivery time (years) | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2025/26 | 2026/27 | 2025/26 | 2026/27 | EOI 2025/26 | EOI 2026/27 | EOI 2027/28 | EOI 2028/29 | EOI 2029/30 | Postal Sectors | Scheme Description
Northeast | Flexibility / Reinforcement | Starbeck | North Yorkshire | 33/11kV | HG2 7PT | Double | 15/18.75 | 21.1 | 2025/26 | Autumn and Winter | TBC | TBC | 1.2593 | 1.9198 | 2.6788 | 3.4378 | 4.202 | 0.055 |  | 11% | [6 empty] | HG1 3; HG1 4; HG2 7; HG2 8; HG3 1; HG3 3; HG5 0; HG5 8; HG5 10 | -Starbeck 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 21.1 MVA. - Network load is forecasted to exceed firm capacity in 2025/26 - We have currently not secured sufficient flexibility services to date to defer network reinforcement and as such have initiated reinforcement works. We will utilise contracted flexibility services during build in order to manage risk on the network and will continue to tender for flexibility services with the option to stall construction if efficient to do so.
Northeast | Flexibility | Faraday Street | Teesside | 66/11kV | TS1 4JG | Double | 15/18.75 | 22.86 | 2025/26 | Winter | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2025/26: 0.23272; Flexibility Required (NPg Reference Scenario) (MW) 2026/27: 3.887; Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 4.694; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 5.5546; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 6.4255 | [5 empty] | TS1 2; TS1 3; TS1 4; TS1 5; TS177; TS2 1; TS3 7; TS4 2; TS5 4; TS5 5; TS5 6 | - Faraday Street 66/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 22.86 MVA determined by the rating of the secondary switchboard. - Network load is forecasted to exceed firm capacity in 2025/26 - To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement.
Northeast | Flexibility | Husthwaite | North Yorkshire | 33/11kV | YO61 4PN | Double | 7.5/15 | 15 | 2026/27 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2026/27: 0.42759; Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 0.9804; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 1.5344; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 2.0989 | [5 empty] | DL6 3; TS9 7; YO51 9; YO60 6; YO61 1; YO61 2; YO61 3; YO61 4; YO61 5; YO62 4; YO62 5; YO6 3; YO7 2; YO7 3 | - Husthwaite 33/11 kV substation is equipped with 2x 7.5/15 MVA transformers, and has a firm capacity of 15.0 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2026/27. - To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement.
Northeast | Flexibility | Monkseaton | Tyne and Wear | 33/11kV | NE25 9AF | Double | 15/18.75 | 20.5 | 2026/27 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2026/27: 0.061535; Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 0.71833; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 1.3659; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 2.0083 |  | 0.676 |  |  |  | NE25 0; NE25 8; NE25 9; NE26 1; NE26 2; NE26 3; NE26 4; NE27 0; NE29 8 | - Monkseaton 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 20.5 MVA. - Network load is forecasted to exceed firm capacity in 2026/27. - To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement.
Northeast | Signpost | Ripon | North Yorkshire | 33/11kV | HG4 1QE | Double | 2024-12-12 | 18.7 | 2027/28 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 0.37456; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 1.1218; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.9154 |  |  |  | 0.407 |  | DL7 9; DL8 2; HG3 3; HG4 1; HG4 2; HG4 3; HG4 4; HG4 5; YO7 3; YO7 4 | - Ripon 33/11 kV substation is equipped with 2x 12/24 MVA transformers, and has a firm capacity of 18.7 MVA determined by the rating of the secondary switchboard. - Network load is forecasted to exceed firm capacity in 2027/28. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Northeast | Signpost | Thirsk | North Yorkshire | 33/11kV | YO7 4NH | Double | 10/14 | 14.7 | 2027/28 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 0.33523; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 0.96936; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.6097 | [5 empty] | DL63; DL79; DL82; YO612; YO71; YO72; YO73; YO74 | - Thirsk 33/11 kV substation is equipped with 2x 10/14 MVA transformers, and has a firm capacity of 14.7 MVA determined by the cyclic rating of the transformers. - Network load is forecasted to exceed firm capacity in 2027/28. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Northeast | Signpost | Darlington West | Teesside | 33/11kV | DL3 9QG | Double | 15/18.75 | 24 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.217 | [5 empty] | DL11; DL22; DL30; DL36; DL37; DL38; DL39 | - Darlington West 33/11 kV substation is equipped with 2 x 15/18.75 MVA transformers, and has a firm capacity of 24.0 MVA determined cyclic rating of the transformers. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Northeast | Signpost | Fawdon T1 | Tyne & Wear | 66/20kV | NE3 2SW | Single | 18.75/25 | 25 | 2028/29 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 0.056924; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.91275 | [5 empty] | NE136; NE137; NE139; NE150; NE159; NE180; NE200; NE209; NE237; NE32; NE35; NE51 | - Fawdon T1 66/20 kV substation is equipped with 1 x 18.75/25 MVA transformer, and has a firm capacity of 25.0 MVA determined by the cyclic rating of the transformers. - Network load is forecasted to exceed firm capacity in 2028/29. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Northeast | Signpost | Seaton Burn T1 | Tyne & Wear | 66/20kV | NE13 6BH | Single | 18.75/25 | 25 | 2028/29 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 0.056924; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.91275 | [5 empty] | NE136; NE137; NE200; NE209; NE237; NE613; NE616 | - Seaton Burn T1 66/20 kV substation is equipped with 1 x 18.75/25 MVA transformer, and has a firm capacity of 25.0 MVA determined by the cyclic rating of the transformers. - Network load is forecasted to exceed firm capacity in 2028/29. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Northeast | Signpost | Prissick | Teesside | 66/11kV | TS4 3SA | Double | 15/18.75 | 22.8 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.54023 | [5 empty] | TS30; TS37; TS43; TS57; TS58; TS70; TS78; TS80; TS89; TS96 | - Prissick 66/11 kV substation is equipped with 2 x 15/18.75 MVA transformers, and has a firm capacity of 22.8 MVA determined by the rating of the secondary switchboard. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Flexibility / Reinforcement | Crowle | Humber | 66/11kV | DN17 4BB | Single | 7.5/15 | 4.5 | 2025/26 | Autumn and Winter | 248 | 2 | 2.1053 | 2.2948 | 2.5768 | 2.8945 | 3.1832 |  | 0.18 | [7 empty] | DN17 1; DN17 3; DN17 4; DN8 5; DN9 1 | - Crowle 66/11 kV substation is equipped with a single 7.5/15 MVA transformer, and has a firm capacity of 4.5 MVA. - Network load is forecasted to exceed firm capacity in 2025/26 - We have currently not secured sufficient flexibility services to date to defer network reinforcement and as such have initiated reinforcement works. We will utilise contracted flexibility services during build in order to manage risk on the network and will continue to tender for flexibility services with the option to stall construction if efficient to do so.
Yorkshire | Flexibility | Wheatacre Road | South Yorkshire | 66/11kV | S36 2GQ | Single | 10/12.5 | 6.6 | 2025/26 | TBD | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2025/26: 1.8248; Flexibility Required (NPg Reference Scenario) (MW) 2026/27: 2.0519; Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 2.3072; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 2.5468; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 2.7864 | [5 empty] | S305; S350; S357; S361; S362; S363; S364; S369; S66 | - Wheatacre Road 66/11 kV substation is equipped with a single 10/12.5 MVA transformer, and has a firm capacity of 6.6 MVA determined by the capacity of normally connected secondary interconnection. - Network load is forecasted to exceed firm capacity in 2025/26. - We will continue Flexibility tendering and may stall reinforcement works if enough Flexibility is procured.
Yorkshire | Flexibility | Kirkburn | North Yorkshire | 66/11kV | YO25 9EH | Single | 15/30 | 8 | 2025/26 | Autumn and Winter | 1200 | 2 | 0.38564 | 0.51955 | 0.70044 | 0.90835 | 1.1339 | 0.3 | [8 empty] | YO17 9; YO25 0; YO25 1; YO25 3; YO25 4; YO25 8; YO25 9; YO42 1 | - Kirkburn 66/11 kV substation is equipped with a single 15/30 MVA transformer, and has a firm capacity of 8 MVA determined by the capacity of normally connected secondary interconnection. - Network load is forecasted to exceed firm capacity in 2025/26. - To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement.
Yorkshire | Flexibility | Audby Lane | West Yorkshire | 33/11kV | LS22 7SU | Double | 11.5/23 | 23 | 2025/26 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2025/26: 3.8982; Flexibility Required (NPg Reference Scenario) (MW) 2026/27: 3.9441; Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 4.098; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 4.3808; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 4.6971 | [5 empty] | HG31; HG58; LS224; LS225; LS226; LS227; LS236; LS237; LS248; YO267; YO268; YO58 | - Audby Lane 33/11 kV substation is equipped with a double 11.5/23 MVA transformer, and has a firm capacity of 23 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2025/26. - To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement.
Yorkshire | Reinforcement | Gibson Lane | Humber | 33/11kV | HU14 3HH | Double | 15/18.75 | 23 | 2026/27 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2026/27: 0.31978; Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 1.1457; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 1.998; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 2.9219 | [5 empty] | HU107; HU12; HU130; HU143; HU151; HU20 | - Gibson Lane 33/11 kV substation is equipped with a double 15/18.75 MVA transformer, and has a firm capacity of 23 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2026/27. - Customer driven reinforcement works (non-discretionary) are being completed
Yorkshire | Reinforcement | Hayton | North Yorkshire | 66/11kV | YO42 1RJ | Double | 10/12.5 | 15.3 | 2027/28 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 0.54734; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 1.1471; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.7405 | [5 empty] | YO259; YO415; YO42; YO421; YO422; YO424; YO433; YO434; YO45; YO86 | - Hayton 66/11 kV substation is equipped with a double 10/12.5 MVA transformer, and has a firm capacity of 15.3 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2027/28. - Customer driven reinforcement works (non-discretionary) are being completed
Yorkshire | Signpost | Moor Road | West Yorkshire | 33/11kV | LS6 4BJ | Double | 15/18.75 | 20.1 | 2027/28 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2027/28: 0.38984; Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 0.96963; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.5606 | 0.163 |  |  |  |  | LS16 5; LS16 7; LS16 8; LS4 2; LS5 3; LS6 1; LS6 2; LS6 3; LS6 4 | - Moor Road 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 20.1 MVA. - Network load is forecasted to exceed firm capacity in 2027/28. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Hemsworth | West Yorkshire | 66/11kV | WF9 5BZ | Single | 2024-12-12 | 10 | 2028/29 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2028/29: 0.59028; Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.199 |  |  | 0.258 |  |  | WF4 1; WF4 2; WF7 7; WF8 3; WF9 1; WF9 4; WF9 5 | - Hemsworth 66/11 kV substation is equipped with a single 12/24 MVA transformer, and has a firm capacity of 10.0 MVA. - Network load is forecasted to exceed firm capacity in 2028/29. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Commonside Lane | West Yorkshire | 33/11kV | WF7 5DF | Double | 2024-12-12 | 18.7 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.48159 | [5 empty] | WF27; WF41; WF61; WF64; WF75; WF76; WF77; WF84 | - Commonsite Lane 33/11 kV substation is equipped with a double 12/24 MVA transformer, and has a firm capacity of 18.7 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Martongate | North Yorkshire | 66/11kV | YO16 6RX | Double | 10/12.5 | 14.1 | 2028/29 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.48936 |  |  |  | 0.322 |  | YO14 0; YO14 9; YO15 1; YO15 2; YO16 4; YO16 6; YO16 7 | - Martongate 66/11 kV substation is equipped with 2x 10/12.5 MVA transformers, and has a firm capacity of 14.1 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Rodley Lane | West Yorkshire | 33/11kV | LS13 1LJ | Double | 10/12.5 | 15.3 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.427 | [5 empty] | BD100; LS131; LS184; LS185; LS196; LS285; LS288; LS53 | - Rodley Lane 33/11 kV substation is equipped with a double 10/12.5 MVA transformer, and has a firm capacity of 15.3 MVA determined by the cyclic rating of the transformer. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Saint Andrews Road 132/33kV | West Yorkshire | 132/33kV | HD1 6SE | Double | 45/108 | 64.4 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 1.6491 | [5 empty] | HD14; HD15; HD16; HD21; HD22; HD33; HD11; HD12; HD13; HD46; HD58; HD59; HD45; HD47; HD71; HD50; HD80 | - Saint Andrews Road 132/33kV supply point is equipped with a double 45/108 MVA transformer, and has a firm capacity of 64.4 MVA determined by the rating of the incoming circuit(s). - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Barrow | North Lincolnshire | 33/11kV | DN19 7EG | Single | 12/24 | 11.6 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.18041 | [5 empty] | DN197; DN378; DN386; DN396; DN403 | - Barrow 33/11 kV substation is equipped with a single 12/24 MVA transformer, and has a firm capacity of 11.6 MVA determined by the capacity of normally connected secondary interconnection - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Belmont Avenue | South Yorkshire | 33/11kV | DN4 8DF | Double | 11.5/23 | 23 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.092482 | [5 empty] | DN13; DN40; DN45; DN48; DN49 | - Belmont Avenue 33/11 kV substation is equipped with a double 11.5/23 MVA transformer, and has a firm capacity of 23.0 MVA determined by the cyclic rating of a transformer. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Bramley | West Yorkshire | 33/11kV | LS13 3ST | Double | 15/18.75 | 23 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.82005 | [5 empty] | LS122; LS123; LS131; LS132; LS133; LS134 | - Bramley 33/11 kV substation is equipped with a double 15/18.75 MVA transformer, and has a firm capacity of 23.0 MVA determined by the cyclic rating of a transformer. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services
Yorkshire | Signpost | Scartho | Humber | 33/11kV | DN33 3JL | Double | 15/18.75 | 23 | 2029/30 | TBC | TBC | TBC | Flexibility Required (NPg Reference Scenario) (MW) 2029/30: 0.090109 | [5 empty] | DN320; DN329; DN331; DN332; DN333; DN345; DN364; DN365; DN370; DN377; DN379; LN76 | - Scartho 33/11 kV substation is equipped with a double 15/18.75 MVA transformer, and has a firm capacity of 23.0 MVA determined by the cyclic rating of a transformer. - Network load is forecasted to exceed firm capacity in 2029/30. - As part of the future plan to relieve the network overload, we are signposting the need for Flexibility Services