## Scheme Header
Scheme Submission Form for use with
NEW METERED CONNECTIONS
Scheme Title |  | Notes
Scheme Ref Number
Date Submitted
Number of non- electric heated domestic properties |  | A maximum of 20 properties can be connected
Number of properties with EV charging points |  | A maximum of 6 properties can be connected
Number of electric heated domestic properties |  | A maximum of 6 properties can be connected
No of Single Phase Commercial properties |  | A maximum of 4 single phase properties can be connected
No of 3 phase Connections |  | Only One 3 phase Connection permitted
Maximum Service Length |  | The maximum service length is 30 metres for metered connections
Source Transformer rating |  | The minimum transformer rating permited for 1 to 6 single phase domestic properties or one single phase commercial property is 315kVA. The minimum rating for all other connections is 500kVA
Do any of the above connections have G83 compliant PV cells fitted. If so how many? |  | A maximum of 6 PV's can be submitted on new connections under the SDR's. G83 compliant is up to 16A (3.68kW) per phase .
Please add any additional comments you may have regarding the application.
Guidance Notes
1. Six Properties with Electric Heating or Electric Vehicle Charging points can be connected with up to 14 non electrically heated properties.
2. Up to 6 Heat Pumps can be fitted without checks but they must to be compliant as per "Form A" and be no greater than 16A/phase.

## Equiv Cable lengths
Scheme Title |  | 0
Scheme Ref Number |  | 0
Date Submitted |  | 0
Table for use with METERED Connections
|  | Version 1.3 | 2017-07-27
Equivalent length rebased to specific size reffered to in SDR's
Cable Size | Cable length
Conductors |  | Wf95 | Wf185 | Wf300
95Al |  | 0 | 0 | 0
120Al |  | 0 | 0 | 0
185Al |  | 0 | 0 | 0
300Al |  | 0 | 0 | 0
0.15Al |  | 0 | 0 | 0
0.2Al |  | 0 | 0 | 0
0.25Al |  | 0 | 0 | 0
0.3Al |  | 0 | 0 | 0
0.5Al |  | 0 | 0 | 0
0.1Cu |  | 0 | 0 | 0
0.15Cu |  | 0 | 0 | 0
0.2Cu |  | 0 | 0 | 0
0.25Cu |  | 0 | 0 | 0
0.3CU |  | 0 | 0 | 0
0.5Cu |  | 0 | 0 | 0
Total Equivalent lengths to be used |  | 0 | 0 | 0
Max Equivalent Lengths permitted. | For Metered Services | 190 | 340 | 400

## Version Control
Version Control Sheet
| Version | Date | Detail | Name
1 | V1.0 | 2017-03-06 | Spreadsheet developed for use with IMP/001/107 CoP for Connection Assessment using Standard design Rules | Michael Catling
2 | V1.1 | 2017-04-05 | Scheme Header added for use with scheme submissions | Michael Catling
3 | V1.2 | 2017-05-12 | Max service length added as well as customer numbers changed following SDR review. | Michael Catling
4 | V1.3 | 2017-07-27 | Comments box added to scheme header. | Michael Catling
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0