## Version Control
Current Version |  | 1.2
Version | Date | Author | Description
1 | 2017-03-29 | Phil Jagger | Spreadsheet associated with IMP/001/013 released.
1.1 | 2018-10-23 | Aisha Ahmad | Minor amendments on 33kV 3c Gas filled-Pb Sheath-Imperial Current Rating (Ducted) Cyclic
1.2 | 2018-12-13 | Aisha Ahmad | Amended 11kV 0.25 Cu paper-belted Lead SWA cyclic rating from 264 to 364 Amps

## 0.23-0.4kV
LV Underground cable ratings and parameters datasheet (IMP/001/013)
Version: | 1.2
Voltage | Conductors |  |  | Construction |  |  | Current Rating (Laid Direct) | [5 empty] | Current Rating Ducted) | [5 empty] | Positive & Negative Sequence (Ohmic)
[7 empty] | Continuous |  | Cyclic |  | Emergency |  | Continuous |  | Cyclic |  | Emergency
(kV) | mm2/ in2 | Mat | No. | Insulation | Sheath | Protection | Amps | kVA | Amps | kVA | Amps | kVA | Amps | kVA | Amps | kVA | Amps | kVA | DC Resistance Ω/km (20°C) | AC Resistance at max insulator temp Ω/km | Reactance Ω/km | Neutral Resistance Ω/km | Earth Resistance Ω/km | Source
Waveform - 3c Al/Cu
0.4 | 35 | Al | 3 | XLPE | Cu |  | 125 | 86.6025 | 142.5 | 98.7269 | 151.25 | 104.7891 | 103.75 | 71.8801 | 118.275 | 81.9433 | 125.5375 | 86.9749 | 0.868 | 1.078 | 0.0755 | 0.433 | 0.433 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 70 | Al | 3 | XLPE | Cu |  | 185 | 128.1718 | 210.9 | 146.1158 | 223.85 | 155.0878 | 153.55 | 106.3826 | 175.047 | 121.2761 | 185.7955 | 128.7229 | 0.443 | 0.558 | 0.0735 | 0.32 | 0.32 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 95 | Al | 3 | XLPE | Cu |  | 235 | 162.8128 | 267.9 | 185.6066 | 284.35 | 197.0035 | 195.05 | 135.1346 | 222.357 | 154.0534 | 236.0105 | 163.5129 | 0.32 | 0.398 | 0.073 | 0.32 | 0.32 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 120 | Al | 3 | XLPE | Cu |  | 255 | 176.6692 | 290.7 | 201.4029 | 308.55 | 213.7697 | 211.65 | 146.6354 | 241.281 | 167.1644 | 256.0965 | 177.4289 | 0.253 | 0.32 | 0.074 | 0.164 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 185 | Al | 3 | XLPE | Cu |  | 335 | 232.0948 | 381.9 | 264.5881 | 405.35 | 280.8347 | 278.05 | 192.6387 | 316.977 | 219.6081 | 336.4405 | 233.0928 | 0.164 | 0.205 | 0.073 | 0.164 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 300 | Al | 3 | XLPE | Cu |  | 435 | 301.3768 | 495.9 | 343.5696 | 526.35 | 364.666 | 361.05 | 250.1428 | 411.597 | 285.1628 | 436.8705 | 302.6728 | 0.1 | 0.126 | 0.0725 | 0.164 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
Waveform - 4c Al/Cu
0.4 | 95 | Al | 4 | XLPE | Cu |  | 235 | 162.8128 | 267.9 | 185.6066 | 284.35 | 197.0035 | 195.05 | 135.1346 | 222.357 | 154.0534 | 236.0105 | 163.5129 | 0.32 | 0.398 | 0.0735 | 0.32 | 0.32 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 185 | Al | 4 | XLPE | Cu |  | 335 | 232.0948 | 381.9 | 264.5881 | 405.35 | 280.8347 | 278.05 | 192.6387 | 316.977 | 219.6081 | 336.4405 | 233.0928 | 0.164 | 0.205 | 0.074 | 0.164 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 300 | Al | 4 | XLPE | Cu |  | 435 | 301.3768 | 495.9 | 343.5696 | 526.35 | 364.666 | 361.05 | 250.1428 | 411.597 | 285.1628 | 436.8705 | 302.6728 | 0.1 | 0.126 | 0.0725 | 0.1 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
Waveform - 3c Al/Al
0.4 | 35 | Al | 3 | XLPE | Al |  | 125 | 86.6025 | 142.5 | 98.7269 | 151.25 | 104.7891 | 103.75 | 71.8801 | 118.275 | 81.9433 | 125.5375 | 86.9749 | 0.857 | 1.078 | 0.074 | 0.857 | 0.857 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 70 | Al | 3 | XLPE | Al |  | 185 | 128.1718 | 210.9 | 146.1158 | 223.85 | 155.0878 | 153.55 | 106.3826 | 175.047 | 121.2761 | 185.7955 | 128.7229 | 0.443 | 0.558 | 0.073 | 0.443 | 0.443 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 120 | Al | 3 | XLPE | Al |  | 255 | 176.6692 | 290.7 | 201.4029 | 308.55 | 213.7697 | 211.65 | 146.6354 | 241.281 | 167.1644 | 256.0965 | 177.4289 | 0.253 | 0.32 | 0.075 | 0.253 | 0.253 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 185 | Al | 3 | XLPE | Al |  | 330 | 228.6307 | 376.2 | 260.639 | 399.3 | 276.6432 | 273.9 | 189.7635 | 312.246 | 216.3304 | 331.419 | 229.6138 | 0.164 | 0.205 | 0.074 | 0.164 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.4 | 300 | Al | 3 | XLPE | Al |  | 430 | 297.9127 | 490.2 | 339.6205 | 520.3 | 360.4744 | 356.9 | 247.2676 | 406.866 | 281.885 | 431.849 | 299.1938 | 0.1 | 0.126 | 0.0725 | 0.164 | 0.164 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
PILC - Cu Imperial
0.4 | 0.0225 | Cu | 4 | Paper | Pb | STA | 100 | 69.282 | 114 | 78.9815 | 121 | 83.8313 | 83 | 57.5041 | 94.62 | 65.5547 | 100.43 | 69.5799 | 1.26 | 1.553 | 0.086 | 1.257 | 2.27 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.04 | Cu | 4 | Paper | Pb | STA | 140 | 96.9948 | 159.6 | 110.5741 | 169.4 | 117.3638 | 116.2 | 80.5057 | 132.468 | 91.7765 | 140.602 | 97.4119 | 0.703 | 0.875 | 0.078 | 0.703 | 2.14 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.05 | Cu | 4 | Paper | Pb | STA | 160 | 110.8513 | 182.4 | 126.3704 | 193.6 | 134.13 | 132.8 | 92.0065 | 151.392 | 104.8875 | 160.688 | 111.3279 | 0.583 | 0.68 | 0.076 | 0.544 | 2.067 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.06 | Cu | 4 | Paper | Pb | STA | 175 | 121.2436 | 199.5 | 138.2177 | 211.75 | 146.7047 | 145.25 | 100.6322 | 165.585 | 114.7207 | 175.7525 | 121.7649 | 0.464 | 0.58 | 0.075 | 0.464 | 1.99 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.075 | Cu | 4 | Paper | Pb | STA | 205 | 142.0282 | 233.7 | 161.9121 | 248.05 | 171.8541 | 170.15 | 117.8834 | 193.971 | 134.3871 | 205.8815 | 142.6389 | 0.376 | 0.48 | 0.074 | 0.376 | 1.93 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.1 | Cu | 4 | Paper | Pb | STA | 240 | 166.2769 | 273.6 | 189.5556 | 290.4 | 201.195 | 199.2 | 138.0098 | 227.088 | 157.3312 | 241.032 | 166.9919 | 0.276 | 0.339 | 0.073 | 0.276 | 1.7 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.15 | Cu | 4 | Paper | Pb | STA | 290 | 200.9179 | 330.6 | 229.0464 | 350.9 | 243.1107 | 240.7 | 166.7619 | 274.398 | 190.1085 | 291.247 | 201.7818 | 0.188 | 0.241 | 0.07 | 0.188 | 1.325 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.2 | Cu | 4 | Paper | Pb | STA | 345 | 239.023 | 393.3 | 272.4862 | 417.45 | 289.2178 | 286.35 | 198.3891 | 326.439 | 226.1636 | 346.4835 | 240.0508 | 0.142 | 0.186 | 0.069 | 0.142 | 1.09 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.25 | Cu | 4 | Paper | Pb | STA | 395 | 273.664 | 450.3 | 311.977 | 477.95 | 331.1335 | 327.85 | 227.1411 | 373.749 | 258.9409 | 396.6985 | 274.8408 | 0.113 | 0.153 | 0.067 | 0.113 | 0.917 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.3 | Cu | 4 | Paper | Pb | STA | 445 | 308.305 | 507.3 | 351.4677 | 538.45 | 373.0491 | 369.35 | 255.8932 | 421.059 | 291.7182 | 446.9135 | 309.6308 | 0.092 | 0.131 | 0.067 | 0.142 | 0.747 | Lead sheath interpolated from Metric.CRATER ducted ratings
PILC - Al Imperial
0.4 | 0.06 | Al | 4 | Paper | Pb | STA | 135 | 93.5307 | 153.9 | 106.625 | 163.35 | 113.1722 | 112.05 | 77.6305 | 127.737 | 88.4988 | 135.5805 | 93.9329 | 0.767 | 0.952 | 0.075 | 0.767 | 1.99 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.1 | Al | 4 | Paper | Pb | STA | 185 | 128.1718 | 210.9 | 146.1158 | 223.85 | 155.0878 | 153.55 | 106.3826 | 175.047 | 121.2761 | 185.7955 | 128.7229 | 0.456 | 0.596 | 0.073 | 0.456 | 1.7 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.15 | Al | 4 | Paper | Pb | STA | 225 | 155.8846 | 256.5 | 177.7084 | 272.25 | 188.6203 | 186.75 | 129.3842 | 212.895 | 147.498 | 225.9675 | 156.5549 | 0.312 | 0.394 | 0.07 | 0.312 | 1.325 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.2 | Al | 4 | Paper | Pb | STA | 270 | 187.0615 | 307.8 | 213.2501 | 326.7 | 226.3444 | 224.1 | 155.261 | 255.474 | 176.9976 | 271.161 | 187.8659 | 0.234 | 0.295 | 0.069 | 0.234 | 1.09 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.25 | Al | 4 | Paper | Pb | STA | 310 | 214.7743 | 353.4 | 244.8427 | 375.1 | 259.8769 | 257.3 | 178.2627 | 293.322 | 203.2194 | 311.333 | 215.6978 | 0.187 | 0.241 | 0.068 | 0.187 | 0.917 | Lead sheath interpolated from Metric.CRATER ducted ratings
0.4 | 0.3 | Al | 4 | Paper | Pb | STA | 350 | 242.4871 | 399 | 276.4353 | 423.5 | 293.4094 | 290.5 | 201.2643 | 331.17 | 229.4413 | 351.505 | 243.5298 | 0.152 | 0.197 | 0.068 | 0.152 | 0.747 | Lead sheath interpolated from Metric.CRATER ducted ratings
PILC - Al Metric
0.4 | 70 | Al | 4 | Paper | Pb | STA | 185 | 128.1718 | 210.9 | 146.1158 | 223.85 | 155.0878 | 153.55 | 106.3826 | 175.047 | 121.2761 | 185.7955 | 128.7229 | 0.443 | 0.55 | 0.071 | 0.443 | 1.63 | Lead sheath resistance from BS6480:1988 - STA resistance ignored. CRATER ducted ratings
0.4 | 95 | Al | 4 | Paper | Pb | STA | 225 | 155.8846 | 256.5 | 177.7084 | 272.25 | 188.6203 | 186.75 | 129.3842 | 212.895 | 147.498 | 225.9675 | 156.5549 | 0.32 | 0.398 | 0.07 | 0.32 | 1.34 | Lead sheath resistance from BS6480:1988 - STA resistance ignored. CRATER ducted ratings
0.4 | 120 | Al | 4 | Paper | Pb | STA | 255 | 176.6692 | 290.7 | 201.4029 | 308.55 | 213.7697 | 211.65 | 146.6354 | 241.281 | 167.1644 | 256.0965 | 177.4289 | 0.253 | 0.315 | 0.068 | 0.253 | 1.14 | Lead sheath resistance from BS6480:1988 - STA resistance ignored. CRATER ducted ratings
0.4 | 185 | Al | 4 | Paper | Pb | STA | 330 | 228.6307 | 376.2 | 260.639 | 399.3 | 276.6432 | 273.9 | 189.7635 | 312.246 | 216.3304 | 331.419 | 229.6138 | 0.164 | 0.205 | 0.068 | 0.164 | 0.79 | Lead sheath resistance from BS6480:1988 - STA resistance ignored. CRATER ducted ratings
0.4 | 300 | Al | 4 | Paper | Pb | STA | 430 | 297.9127 | 490.2 | 339.6205 | 520.3 | 360.4744 | 356.9 | 247.2676 | 406.866 | 281.885 | 431.849 | 299.1938 | 0.1 | 0.126 | 0.067 | 0.164 | 0.55 | Lead sheath resistance from BS6480:1988 - STA resistance ignored. CRATER ducted ratings
Service Cable - Imperial
0.23 | 0.007 | Cu | 1 | Paper | Split Concentric |  | 56 | 12.88 | 63.84 | 14.6832 | 67.76 | 15.5848 | 46.48 | 10.6904 | 52.9872 | 12.1871 | 56.2408 | 12.9354 | 4.1 | 5.125 | 0.12 | 4.1 | 4.1 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 0.0225 | Cu | 1 | Paper | Split Concentric |  | 110 | 25.3 | 125.4 | 28.842 | 133.1 | 30.613 | 91.3 | 20.999 | 104.082 | 23.9389 | 110.473 | 25.4088 | 1.26 | 1.575 | 0.086 | 1.26 | 1.26 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 0.04 | Cu | 1 | Paper | Split Concentric |  | 155 | 35.65 | 176.7 | 40.641 | 187.55 | 43.1365 | 128.65 | 29.5895 | 146.661 | 33.732 | 155.6665 | 35.8033 | 0.703 | 0.87875 | 0.078 | 0.703 | 0.703 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 0.007 | Cu | 2 | Paper | Pb | STA | 62 | 14.26 | 70.68 | 16.2564 | 75.02 | 17.2546 | 51.46 | 11.8358 | 58.6644 | 13.4928 | 62.2666 | 14.3213 | 4.1 | 5.125 | 0.1 | 4.1 | 4.1 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 0.0225 | Cu | 2 | Paper | Pb | STA | 120 | 27.6 | 136.8 | 31.464 | 145.2 | 33.396 | 99.6 | 22.908 | 113.544 | 26.1151 | 120.516 | 27.7187 | 1.26 | 1.575 | 0.086 | 1.26 | 1.26 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 0.04 | Cu | 2 | Paper | Pb | STA | 165 | 37.95 | 188.1 | 43.263 | 199.65 | 45.9195 | 136.95 | 31.4985 | 156.123 | 35.9083 | 165.7095 | 38.1132 | 0.703 | 0.87875 | 0.078 | 0.703 | 0.703 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
Service Cable - Metric
0.23 | 4 | Cu | 1 | PVC | Split Concentric |  | 53 | 12.19 | 60.42 | 13.8966 | 64.13 | 14.7499 | 43.99 | 10.1177 | 50.1486 | 11.5342 | 53.2279 | 12.2424 | 4.61 | 5.7625 | 0.117 | 4.8 | 4.8 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 16 | Al | 1 | PVC | Split Concentric |  | 84 | 19.32 | 95.76 | 22.0248 | 101.64 | 23.3772 | 69.72 | 16.0356 | 79.4808 | 18.2806 | 84.3612 | 19.4031 | 1.9 | 2.375 | 0.079 | 1.9 | 1.9 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 4 | Cu | 1 | PVC | Concentric |  | 53 | 12.19 | 60.42 | 13.8966 | 64.13 | 14.7499 | 43.99 | 10.1177 | 50.1486 | 11.5342 | 53.2279 | 12.2424 | 4.61 | 5.7625 | 0.103 | 4.61 | 4.61 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 25 | Al | 1 | PVC | Concentric |  | 115 | 26.45 | 131.1 | 30.153 | 139.15 | 32.0045 | 95.45 | 21.9535 | 108.813 | 25.027 | 115.4945 | 26.5637 | 1.2 | 1.5 | 0.08 | 1.2 | 1.2 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings
0.23 | 35 | Al | 1 | PVC | Concentric |  | 140 | 32.2 | 159.6 | 36.708 | 169.4 | 38.962 | 116.2 | 26.726 | 132.468 | 30.4676 | 140.602 | 32.3385 | 0.868 | 1.085 | 0.0775 | 0.868 | 0.868 | DSS/007/031 and NPgY volt drop spreadsheet. CRATER ducted ratings

## 11kV
11kV Underground cable ratings and parameters datasheet (IMP/001/013)
Version: | 1.2
| Conductors |  |  | Construction |  |  | Current Rating (Laid Direct) | [5 empty] | Current Rating (Ducted) | [5 empty] | Positive & Negative Sequence (Ohmic) | [5 empty] | Zero Sequence (Ohmic) |  |  |  | Positive & Negative Sequence (100MVA Base) |  |  |  | Zero Sequence (100MVA Base)
Voltage (kV) | mm2/in2 | Material | No. | Insulation | Sheath | Protection | Continuous |  | Cyclic |  | Emergency |  | Continuous |  | Cyclic |  | Emergency |  | DC Resistance Ω/km (20°C) | AC Resistance at max insulator temp Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | Charging Current A/km | Resistance Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | DC Resistance %/km (20°C) | AC Resistance at max insulator temp %/km | Reactance %/km | Susceptance %/km | Resistance %/km | Reactance %/km | Susceptance %/km
U | [6 empty] | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Rdc | R1=R2 | X1=X2 | C1=C2 | B1=B2 | IC | R0 | X0 | C0 | B0 | Rdc | R1=R2 | X1=X2 | B1=B2 | R0 | X0 | B0 | Source
11kV 3c PILCSWA - Al Imperial
11 | 0.04 | Al | 3 | Paper(Belted) | Lead | SWA | 89 | 1.6957 | 97 | 1.8481 | 104 | 1.9815 | 76.7241 | 1.4618 | 83.6207 | 1.5932 | 89.6552 | 1.7082 | 1.106 | 1.4329 | 0.119 | 0.28 | 87.9646 | 0.55865 | 2.9349 | 0.176 | 0.23333 | 73.3038 | 91.405 | 118.4187 | 9.8347 | 0.010644 | 242.5572 | 14.5455 | 0.0088698 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.05 | Al | 3 | Paper(Belted) | Lead | SWA | 100 | 1.9053 | 110 | 2.0958 | 117 | 2.2291 | 86.2069 | 1.6425 | 94.8276 | 1.8067 | 100.8621 | 1.9217 | 0.918 | 1.1103 | 0.114 | 0.303 | 95.1903 | 0.60454 | 2.6648 | 0.169 | 0.2525 | 79.3252 | 75.8678 | 91.7605 | 9.4215 | 0.011518 | 220.2278 | 13.9669 | 0.0095984 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.06 | Al | 3 | Paper(Belted) | Lead | SWA | 112 | 2.1339 | 124 | 2.3625 | 133 | 2.534 | 96.5517 | 1.8396 | 106.8966 | 2.0367 | 114.6552 | 2.1845 | 0.7302 | 0.91846 | 0.108 | 0.327 | 102.7301 | 0.65242 | 2.2951 | 0.162 | 0.2725 | 85.6084 | 60.3471 | 75.9058 | 8.9256 | 0.01243 | 189.6763 | 13.3884 | 0.010359 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.075 | Al | 3 | Paper(Belted) | Lead | SWA | 126 | 2.4006 | 140 | 2.6674 | 150 | 2.8579 | 108.6207 | 2.0695 | 120.6897 | 2.2994 | 129.3103 | 2.4637 | 0.594 | 0.7385 | 0.102 | 0.358 | 112.469 | 0.71427 | 2.0201 | 0.153 | 0.29833 | 93.7242 | 49.0909 | 61.0334 | 8.4298 | 0.013609 | 166.9513 | 12.6446 | 0.011341 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.1 | Al | 3 | Paper(Belted) | Lead | SWA | 150 | 2.8579 | 166 | 3.1627 | 180 | 3.4295 | 129.3103 | 2.4637 | 143.1034 | 2.7265 | 155.1724 | 2.9564 | 0.4342 | 0.53987 | 0.096 | 0.403 | 126.6062 | 0.80406 | 1.7836 | 0.146 | 0.33583 | 105.5052 | 35.8843 | 44.6175 | 7.9339 | 0.015319 | 147.4019 | 12.0661 | 0.012766 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.15 | Al | 3 | Paper(Belted) | Lead | SWA | 186 | 3.5438 | 208 | 3.9629 | 226 | 4.3059 | 160.3448 | 3.055 | 179.3103 | 3.4163 | 194.8276 | 3.712 | 0.2965 | 0.3684 | 0.092 | 0.459 | 144.1991 | 0.91579 | 1.6091 | 0.138 | 0.3825 | 120.1659 | 24.5041 | 30.4465 | 7.6033 | 0.017448 | 132.9826 | 11.405 | 0.01454 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.2 | Al | 3 | Paper(Belted) | Lead | SWA | 220 | 4.1916 | 248 | 4.725 | 271 | 5.1632 | 189.6552 | 3.6134 | 213.7931 | 4.0733 | 233.6207 | 4.4511 | 0.2231 | 0.27333 | 0.086 | 0.5 | 157.0796 | 0.99759 | 1.355 | 0.132 | 0.41667 | 130.8997 | 18.438 | 22.5894 | 7.1074 | 0.019007 | 111.9875 | 10.9091 | 0.015839 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.25 | Al | 3 | Paper(Belted) | Lead | SWA | 250 | 4.7631 | 284 | 5.4109 | 311 | 5.9253 | 215.5172 | 4.1062 | 244.8276 | 4.6646 | 268.1034 | 5.1081 | 0.1777 | 0.2207 | 0.08 | 0.502 | 157.708 | 1.0016 | 1.1584 | 0.131 | 0.41833 | 131.4233 | 14.686 | 18.2399 | 6.6116 | 0.019083 | 95.7375 | 10.8264 | 0.015902 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.3 | Al | 3 | Paper(Belted) | Lead | SWA | 281 | 5.3538 | 321 | 6.1159 | 352 | 6.7065 | 242.2414 | 4.6153 | 276.7241 | 5.2723 | 303.4483 | 5.7815 | 0.1448 | 0.18505 | 0.078 | 0.534 | 167.761 | 1.0654 | 0.94483 | 0.128 | 0.445 | 139.8009 | 11.9669 | 15.2934 | 6.4463 | 0.020299 | 78.0853 | 10.5785 | 0.016916 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.4 | Al | 3 | Paper(Belted) | Lead | SWA | 332 | 6.3254 | 381 | 7.259 | 421 | 8.0211 | 286.2069 | 5.453 | 328.4483 | 6.2578 | 362.931 | 6.9148 | 0.1078 | 0.13921 | 0.075 | 0.584 | 183.469 | 1.1652 | 0.85423 | 0.123 | 0.48667 | 152.8908 | 8.9091 | 11.5051 | 6.1983 | 0.0222 | 70.5978 | 10.1653 | 0.0185 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.5 | Al | 3 | Paper(Belted) | Lead | SWA | 371 | 7.0685 | 429 | 8.1735 | 476 | 9.069 | 319.8276 | 6.0935 | 369.8276 | 7.0462 | 410.3448 | 7.8181 | 0.08787 | 0.11375 | 0.073 | 0.628 | 197.292 | 1.253 | 0.76578 | 0.119 | 0.52333 | 164.41 | 7.262 | 9.4005 | 6.0331 | 0.023872 | 63.288 | 9.8347 | 0.019894 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.04 | Al | 3 | Paper (Screened) | Lead | SWA | 96 | 1.829 | 107 | 2.0386 | 114 | 2.172 | 82.7586 | 1.5768 | 92.2414 | 1.7574 | 98.2759 | 1.8724 | 1.106 | 1.463 | 0.124 | 0.351 | 110.2699 | 0.70031 | 2.93 | 0.163 | 0.351 | 110.2699 | 91.405 | 120.9055 | 10.2479 | 0.013343 | 242.1488 | 13.4711 | 0.013343 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.05 | Al | 3 | Paper (Screened) | Lead | SWA | 110 | 2.0958 | 123 | 2.3435 | 132 | 2.5149 | 94.8276 | 1.8067 | 106.0345 | 2.0202 | 113.7931 | 2.168 | 0.918 | 1.1336 | 0.118 | 0.388 | 121.8938 | 0.77413 | 2.6648 | 0.156 | 0.388 | 121.8938 | 75.8678 | 93.6875 | 9.7521 | 0.014749 | 220.2278 | 12.8926 | 0.014749 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.06 | Al | 3 | Paper (Screened) | Lead | SWA | 122 | 2.3244 | 136 | 2.5911 | 146 | 2.7817 | 105.1724 | 2.0038 | 117.2414 | 2.2337 | 125.8621 | 2.398 | 0.7302 | 0.93775 | 0.112 | 0.423 | 132.8894 | 0.84396 | 2.2951 | 0.15 | 0.423 | 132.8894 | 60.3471 | 77.4999 | 9.2562 | 0.01608 | 189.6763 | 12.3967 | 0.01608 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.075 | Al | 3 | Paper (Screened) | Lead | SWA | 138 | 2.6293 | 155 | 2.9531 | 167 | 3.1818 | 118.9655 | 2.2666 | 133.6207 | 2.5458 | 143.9655 | 2.7429 | 0.594 | 0.75401 | 0.106 | 0.468 | 147.0265 | 0.93374 | 2.0201 | 0.145 | 0.468 | 147.0265 | 49.0909 | 62.3151 | 8.7603 | 0.01779 | 166.9513 | 11.9835 | 0.01779 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.1 | Al | 3 | Paper (Screened) | Lead | SWA | 163 | 3.1056 | 183 | 3.4866 | 200 | 3.8105 | 140.5172 | 2.6772 | 157.7586 | 3.0057 | 172.4138 | 3.2849 | 0.4342 | 0.55121 | 0.093 | 0.503 | 158.0221 | 1.0036 | 1.7836 | 0.14 | 0.503 | 158.0221 | 35.8843 | 45.5545 | 7.686 | 0.019121 | 147.4019 | 11.5702 | 0.019121 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.15 | Al | 3 | Paper (Screened) | Lead | SWA | 201 | 3.8296 | 227 | 4.3249 | 250 | 4.7631 | 173.2759 | 3.3013 | 195.6897 | 3.7284 | 215.5172 | 4.1062 | 0.2965 | 0.37614 | 0.087 | 0.579 | 181.8982 | 1.1552 | 1.6091 | 0.131 | 0.579 | 181.8982 | 24.5041 | 31.0859 | 7.1901 | 0.02201 | 132.9826 | 10.8264 | 0.02201 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.2 | Al | 3 | Paper (Screened) | Lead | SWA | 235 | 4.4774 | 268 | 5.1061 | 297 | 5.6586 | 202.5862 | 3.8598 | 231.0345 | 4.4018 | 256.0345 | 4.8781 | 0.2231 | 0.27907 | 0.082 | 0.652 | 204.8318 | 1.3009 | 1.355 | 0.126 | 0.652 | 204.8318 | 18.438 | 23.0637 | 6.7769 | 0.024785 | 111.9875 | 10.4132 | 0.024785 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.25 | Al | 3 | Paper (Screened) | Lead | SWA | 267 | 5.087 | 305 | 5.811 | 340 | 6.4779 | 230.1724 | 4.3854 | 262.931 | 5.0095 | 293.1034 | 5.5844 | 0.1777 | 0.22534 | 0.08 | 0.712 | 223.6814 | 1.4206 | 1.1584 | 0.122 | 0.712 | 223.6814 | 14.686 | 18.6229 | 6.6116 | 0.027065 | 95.7375 | 10.0826 | 0.027065 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.3 | Al | 3 | Paper (Screened) | Lead | SWA | 298 | 5.6777 | 343 | 6.535 | 384 | 7.3162 | 256.8966 | 4.8945 | 295.6897 | 5.6336 | 331.0345 | 6.3071 | 0.1448 | 0.18894 | 0.079 | 0.765 | 240.3318 | 1.5263 | 0.94483 | 0.119 | 0.765 | 240.3318 | 11.9669 | 15.6146 | 6.5289 | 0.02908 | 78.0853 | 9.8347 | 0.02908 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.4 | Al | 3 | Paper (Screened) | Lead | SWA | 351 | 6.6874 | 406 | 7.7353 | 461 | 8.7832 | 302.5862 | 5.765 | 350 | 6.6684 | 397.4138 | 7.5717 | 0.1078 | 0.14214 | 0.075 | 0.861 | 270.4911 | 1.7178 | 0.85423 | 0.115 | 0.861 | 270.4911 | 8.9091 | 11.7467 | 6.1983 | 0.032729 | 70.5978 | 9.5041 | 0.032729 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11 | 0.5 | Al | 3 | Paper (Screened) | Lead | SWA | 391 | 7.4496 | 454 | 8.6499 | 514 | 9.793 | 337.069 | 6.422 | 391.3793 | 7.4568 | 443.1034 | 8.4423 | 0.08787 | 0.11614 | 0.074 | 0.94 | 295.3097 | 1.8755 | 0.76578 | 0.111 | 0.94 | 295.3097 | 7.262 | 9.598 | 6.1157 | 0.035732 | 63.288 | 9.1736 | 0.035732 | Conversion from Cu Values in ABB T&D 5th Edition Table 6. R0 resistances estimated from metric PILCSWA. CRATER Ratings
11kV 3c PILCSWA - Cu Imperial
11 | 0.04 | Cu | 3 | Paper(Belted) | Lead | SWA | 114 | 2.172 | 126 | 2.4006 | 135 | 2.5721 | 98.2759 | 1.8724 | 108.6207 | 2.0695 | 116.3793 | 2.2173 | 0.6748 | 0.844 | 0.119 | 0.28 | 87.9646 | 0.55865 | 2.45 | 0.176 | 0.23333 | 73.3038 | 55.7686 | 69.7521 | 9.8347 | 0.010644 | 202.4793 | 14.5455 | 0.0088698 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.05 | Cu | 3 | Paper(Belted) | Lead | SWA | 130 | 2.4768 | 142 | 2.7055 | 151 | 2.8769 | 112.069 | 2.1352 | 122.4138 | 2.3323 | 130.1724 | 2.4801 | 0.5298 | 0.654 | 0.114 | 0.303 | 95.1903 | 0.60454 | 2.08 | 0.169 | 0.2525 | 79.3252 | 43.7851 | 54.0496 | 9.4215 | 0.011518 | 171.9008 | 13.9669 | 0.0095984 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.06 | Cu | 3 | Paper(Belted) | Lead | SWA | 144 | 2.7436 | 159 | 3.0294 | 171 | 3.258 | 124.1379 | 2.3651 | 137.069 | 2.6115 | 147.4138 | 2.8086 | 0.4455 | 0.541 | 0.108 | 0.327 | 102.7301 | 0.65242 | 1.86 | 0.162 | 0.2725 | 85.6084 | 36.8182 | 44.7107 | 8.9256 | 0.01243 | 153.719 | 13.3884 | 0.010359 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.075 | Cu | 3 | Paper(Belted) | Lead | SWA | 163 | 3.1056 | 181 | 3.4485 | 194 | 3.6962 | 140.5172 | 2.6772 | 156.0345 | 2.9729 | 167.2414 | 3.1864 | 0.3616 | 0.435 | 0.102 | 0.358 | 112.469 | 0.71427 | 1.7 | 0.153 | 0.29833 | 93.7242 | 29.8843 | 35.9504 | 8.4298 | 0.013609 | 140.4959 | 12.6446 | 0.011341 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.1 | Cu | 3 | Paper(Belted) | Lead | SWA | 193 | 3.6771 | 214 | 4.0772 | 231 | 4.4011 | 166.3793 | 3.17 | 184.4828 | 3.5149 | 199.1379 | 3.7941 | 0.2649 | 0.318 | 0.096 | 0.403 | 126.6062 | 0.80406 | 1.57 | 0.146 | 0.33583 | 105.5052 | 21.8926 | 26.281 | 7.9339 | 0.015319 | 129.7521 | 12.0661 | 0.012766 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.15 | Cu | 3 | Paper(Belted) | Lead | SWA | 239 | 4.5536 | 268 | 5.1061 | 291 | 5.5443 | 206.0345 | 3.9255 | 231.0345 | 4.4018 | 250.8621 | 4.7796 | 0.1808 | 0.217 | 0.092 | 0.459 | 144.1991 | 0.91579 | 1.31 | 0.138 | 0.3825 | 120.1659 | 14.9421 | 17.9339 | 7.6033 | 0.017448 | 108.2645 | 11.405 | 0.01454 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.2 | Cu | 3 | Paper(Belted) | Lead | SWA | 283 | 5.3919 | 319 | 6.0778 | 348 | 6.6303 | 243.9655 | 4.6482 | 275 | 5.2395 | 300 | 5.7158 | 0.1361 | 0.161 | 0.086 | 0.5 | 157.0796 | 0.99759 | 1.11 | 0.132 | 0.41667 | 130.8997 | 11.2479 | 13.3058 | 7.1074 | 0.019007 | 91.7355 | 10.9091 | 0.015839 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.25 | Cu | 3 | Paper(Belted) | Lead | SWA | 321 | 6.1159 | 364 | 6.9351 | 399 | 7.602 | 276.7241 | 5.2723 | 313.7931 | 5.9786 | 343.9655 | 6.5534 | 0.1084 | 0.13 | 0.08 | 0.502 | 157.708 | 1.0016 | 0.9 | 0.131 | 0.41833 | 131.4233 | 8.9587 | 10.7438 | 6.6116 | 0.019083 | 74.3802 | 10.8264 | 0.015902 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.3 | Cu | 3 | Paper(Belted) | Lead | SWA | 360 | 6.8589 | 410 | 7.8115 | 451 | 8.5927 | 310.3448 | 5.9129 | 353.4483 | 6.7341 | 388.7931 | 7.4075 | 0.08837 | 0.109 | 0.078 | 0.534 | 167.761 | 1.0654 | 0.83 | 0.128 | 0.445 | 139.8009 | 7.3033 | 9.0083 | 6.4463 | 0.020299 | 68.595 | 10.5785 | 0.016916 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.4 | Cu | 3 | Paper(Belted) | Lead | SWA | 421 | 8.0211 | 485 | 9.2405 | 535 | 10.1931 | 362.931 | 6.9148 | 418.1034 | 7.9659 | 461.2069 | 8.7872 | 0.06576 | 0.082 | 0.075 | 0.584 | 183.469 | 1.1652 | 0.74 | 0.123 | 0.48667 | 152.8908 | 5.4347 | 6.7769 | 6.1983 | 0.0222 | 61.157 | 10.1653 | 0.0185 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.5 | Cu | 3 | Paper(Belted) | Lead | SWA | 467 | 8.8975 | 541 | 10.3074 | 601 | 11.4506 | 402.5862 | 7.6703 | 466.3793 | 8.8857 | 518.1034 | 9.8712 | 0.05361 | 0.067 | 0.073 | 0.628 | 197.292 | 1.253 | 0.65 | 0.119 | 0.52333 | 164.41 | 4.4306 | 5.5372 | 6.0331 | 0.023872 | 53.719 | 9.8347 | 0.019894 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.04 | Cu | 3 | Paper (Screened) | Lead | SWA | 124 | 2.3625 | 138 | 2.6293 | 150 | 2.8579 | 106.8966 | 2.0367 | 118.9655 | 2.2666 | 129.3103 | 2.4637 | 0.6748 | 0.86105 | 0.124 | 0.351 | 110.2699 | 0.70031 | 2.45 | 0.163 | 0.351 | 110.2699 | 55.7686 | 71.1614 | 10.2479 | 0.013343 | 202.4793 | 13.4711 | 0.013343 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.05 | Cu | 3 | Paper (Screened) | Lead | SWA | 142 | 2.7055 | 159 | 3.0294 | 170 | 3.2389 | 122.4138 | 2.3323 | 137.069 | 2.6115 | 146.5517 | 2.7922 | 0.5298 | 0.66721 | 0.118 | 0.388 | 121.8938 | 0.77413 | 2.08 | 0.156 | 0.388 | 121.8938 | 43.7851 | 55.1417 | 9.7521 | 0.014749 | 171.9008 | 12.8926 | 0.014749 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.06 | Cu | 3 | Paper (Screened) | Lead | SWA | 157 | 2.9913 | 175 | 3.3342 | 192 | 3.6581 | 135.3448 | 2.5787 | 150.8621 | 2.8743 | 165.5172 | 3.1535 | 0.4455 | 0.55193 | 0.112 | 0.423 | 132.8894 | 0.84396 | 1.86 | 0.15 | 0.423 | 132.8894 | 36.8182 | 45.6141 | 9.2562 | 0.01608 | 153.719 | 12.3967 | 0.01608 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.075 | Cu | 3 | Paper (Screened) | Lead | SWA | 178 | 3.3914 | 200 | 3.8105 | 216 | 4.1154 | 153.4483 | 2.9236 | 172.4138 | 3.2849 | 186.2069 | 3.5477 | 0.3616 | 0.44379 | 0.106 | 0.468 | 147.0265 | 0.93374 | 1.7 | 0.145 | 0.468 | 147.0265 | 29.8843 | 36.6768 | 8.7603 | 0.01779 | 140.4959 | 11.9835 | 0.01779 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.1 | Cu | 3 | Paper (Screened) | Lead | SWA | 209 | 3.982 | 236 | 4.4964 | 260 | 4.9537 | 180.1724 | 3.4327 | 203.4483 | 3.8762 | 224.1379 | 4.2704 | 0.2649 | 0.32443 | 0.093 | 0.503 | 158.0221 | 1.0036 | 1.57 | 0.14 | 0.503 | 158.0221 | 21.8926 | 26.812 | 7.686 | 0.019121 | 129.7521 | 11.5702 | 0.019121 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.15 | Cu | 3 | Paper (Screened) | Lead | SWA | 258 | 4.9156 | 293 | 5.5824 | 324 | 6.173 | 222.4138 | 4.2376 | 252.5862 | 4.8124 | 279.3103 | 5.3216 | 0.1808 | 0.22138 | 0.087 | 0.579 | 181.8982 | 1.1552 | 1.31 | 0.131 | 0.579 | 181.8982 | 14.9421 | 18.2962 | 7.1901 | 0.02201 | 108.2645 | 10.8264 | 0.02201 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.2 | Cu | 3 | Paper (Screened) | Lead | SWA | 302 | 5.7539 | 344 | 6.5541 | 383 | 7.2971 | 260.3448 | 4.9602 | 296.5517 | 5.6501 | 330.1724 | 6.2906 | 0.1361 | 0.16425 | 0.082 | 0.652 | 204.8318 | 1.3009 | 1.11 | 0.126 | 0.652 | 204.8318 | 11.2479 | 13.5746 | 6.7769 | 0.024785 | 91.7355 | 10.4132 | 0.024785 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.25 | Cu | 3 | Paper (Screened) | Lead | SWA | 342 | 6.516 | 391 | 7.4496 | 435 | 8.2879 | 294.8276 | 5.6172 | 337.069 | 6.422 | 375 | 7.1447 | 0.1084 | 0.13263 | 0.08 | 0.712 | 223.6814 | 1.4206 | 0.9 | 0.122 | 0.712 | 223.6814 | 8.9587 | 10.9609 | 6.6116 | 0.027065 | 74.3802 | 10.0826 | 0.027065 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.3 | Cu | 3 | Paper (Screened) | Lead | SWA | 381 | 7.259 | 438 | 8.345 | 490 | 9.3358 | 328.4483 | 6.2578 | 377.5862 | 7.194 | 422.4138 | 8.0481 | 0.08837 | 0.1112 | 0.079 | 0.765 | 240.3318 | 1.5263 | 0.83 | 0.119 | 0.765 | 240.3318 | 7.3033 | 9.1903 | 6.5289 | 0.02908 | 68.595 | 9.8347 | 0.02908 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.4 | Cu | 3 | Paper (Screened) | Lead | SWA | 446 | 8.4974 | 516 | 9.8311 | 581 | 11.0695 | 384.4828 | 7.3254 | 444.8276 | 8.4751 | 500.8621 | 9.5427 | 0.06576 | 0.083657 | 0.075 | 0.861 | 270.4911 | 1.7178 | 0.74 | 0.115 | 0.861 | 270.4911 | 5.4347 | 6.9138 | 6.1983 | 0.032729 | 61.157 | 9.5041 | 0.032729 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11 | 0.5 | Cu | 3 | Paper (Screened) | Lead | SWA | 492 | 9.3739 | 573 | 10.9171 | 646 | 12.308 | 424.1379 | 8.0809 | 493.9655 | 9.4113 | 556.8966 | 10.6103 | 0.05361 | 0.068354 | 0.074 | 0.94 | 295.3097 | 1.8755 | 0.65 | 0.111 | 0.94 | 295.3097 | 4.4306 | 5.6491 | 6.1157 | 0.035732 | 53.719 | 9.1736 | 0.035732 | ABB T&D 5th Edition Table 6. Rdc from temp equation. R0 resistances estimated from metric PILCSWA; CRATER Ratings
11kV 3c PICAS - Al Metric
11 | 95 | Al | 3 | Paper(Belted) | CAS | PVC | 185 | 3.5247 | 210.9 | 4.0182 | 223.85 | 4.2649 | 160 | 3.0484 | 182.4 | 3.4752 | 193.6 | 3.6886 | 0.32 | 0.379 | 0.087 | 0.45 | 141.3717 | 0.9 | 0.495 | 0.099 | 0.375 | 117.8097 | 26.4463 | 31.3223 | 7.1901 | 0.017106 | 40.9091 | 8.1818 | 0.014255 | ENA TS 09-12. R0X0 calculated from 09-12 Dimensions
11 | 185 | Al | 3 | Paper(Belted) | CAS | PVC | 270 | 5.1442 | 307.8 | 5.8644 | 326.7 | 6.2245 | 230 | 4.3821 | 262.2 | 4.9956 | 278.3 | 5.3023 | 0.164 | 0.195 | 0.08 | 0.58 | 182.2124 | 1.16 | 0.27 | 0.092 | 0.48333 | 151.8436 | 13.5537 | 16.1157 | 6.6116 | 0.022048 | 22.314 | 7.6033 | 0.018373 | ENA TS 09-12. R0X0 calculated from 09-12 Dimensions
11 | 300 | Al | 3 | Paper(Belted) | CAS | PVC | 355 | 6.7637 | 404.7 | 7.7106 | 429.55 | 8.184 | 305 | 5.811 | 347.7 | 6.6246 | 369.05 | 7.0313 | 0.1 | 0.12 | 0.077 | 0.71 | 223.0531 | 1.42 | 0.171 | 0.088 | 0.59167 | 185.8776 | 8.2645 | 9.9174 | 6.3636 | 0.026989 | 14.1322 | 7.2727 | 0.022491 | ENA TS 09-12. R0X0 calculated from 09-12 Dimensions
11 | 95 | Al | 3 | Paper (Screened) | CAS | PVC | 205 | 3.9058 | 233.7 | 4.4526 | 248.05 | 4.726 | 170 | 3.2389 | 193.8 | 3.6924 | 205.7 | 3.9191 | 0.32 | 0.384 | 0.087 | 0.6 | 188.4956 | 1.2 | 0.495 | 0.099 | 0.6 | 188.4956 | 26.4463 | 31.7355 | 7.1901 | 0.022808 | 40.9091 | 8.1818 | 0.022808 | ENA TS 09-12. R0X0 calculated from 09-12 Dimensions
11 | 185 | Al | 3 | Paper (Screened) | CAS | PVC | 295 | 5.6205 | 336.3 | 6.4074 | 356.95 | 6.8008 | 250 | 4.7631 | 285 | 5.43 | 302.5 | 5.7634 | 0.164 | 0.198 | 0.081 | 0.81 | 254.469 | 1.62 | 0.27 | 0.092 | 0.81 | 254.469 | 13.5537 | 16.3636 | 6.6942 | 0.030791 | 22.314 | 7.6033 | 0.030791 | ENA TS 09-12. R0X0 calculated from 09-12 Dimensions
11 | 300 | Al | 3 | Paper (Screened) | CAS | PVC | 380 | 7.24 | 433.2 | 8.2536 | 459.8 | 8.7604 | 325 | 6.1921 | 370.5 | 7.059 | 393.25 | 7.4924 | 0.1 | 0.122 | 0.077 | 1 | 314.1593 | 2 | 0.171 | 0.088 | 1 | 314.1593 | 8.2645 | 10.0826 | 6.3636 | 0.038013 | 14.1322 | 7.2727 | 0.038013 | ENA TS 09-12. R0X0 calculated from 09-12 Dimensions
11kV 3c PICAS - Cu Metric
11 | 300 | Cu | 3 | Paper (Belted) | CAS | PVC | 434 | 8.2688 | 494.76 | 9.4264 | 525.14 | 10.0053 | 374.1379 | 7.1283 | 426.5172 | 8.1262 | 452.7069 | 8.6252 | 0.0601 | 0.072 | 0.077 | 0.71 | 223.0531 | 1.4166 | 0.1311 | 0.088 | 0.59167 | 185.8776 | 4.9669 | 5.9504 | 6.3636 | 0.026989 | 10.8347 | 7.2727 | 0.022491 | Dervied from ENATs 09-12 and PILC Spec; CRATER Ratings
11 | 300 | Cu | 3 | Paper (Screened) | CAS | PVC | 460 | 8.7642 | 524.4 | 9.9912 | 556.6 | 10.6047 | 396.5517 | 7.5553 | 452.069 | 8.6131 | 479.8276 | 9.1419 | 0.0601 | 0.075 | 0.077 | 1 | 314.1593 | 1.9952 | 0.1311 | 0.088 | 1 | 314.1593 | 4.9669 | 6.1983 | 6.3636 | 0.038013 | 10.8347 | 7.2727 | 0.038013 | Dervied from ENATs 09-12 and PILC Spec; CRATER Ratings
11kV 1c Triplex- Al Metric
11 | 95 | Al | 1x3 | XLPE |  | MDPE | 245 | 4.6679 | 279.3 | 5.3214 | 296.45 | 5.6481 | 205 | 3.9058 | 240.7759 | 4.5874 | 255.5603 | 4.8691 | 0.32 | 0.41 | 0.119 | 0.311 | 97.7035 | 0.6205 | 0.862 | 0.058 | 0.311 | 97.7035 | 26.4463 | 33.8843 | 9.8347 | 0.011822 | 71.2397 | 4.7934 | 0.011822 | Prysmian 11kV SAWU SAC 35M WST 0113
11 | 185 | Al | 1x3 | XLPE |  | MDPE | 355 | 6.7637 | 404.7 | 7.7106 | 429.55 | 8.184 | 295 | 5.6205 | 348.8793 | 6.647 | 370.3017 | 7.0552 | 0.164 | 0.211 | 0.108 | 0.4 | 125.6637 | 0.79807 | 0.748 | 0.052 | 0.4 | 125.6637 | 13.5537 | 17.438 | 8.9256 | 0.015205 | 61.8182 | 4.2975 | 0.015205 | Prysmian 11kV SAWU SAC 35M WST 0114
11 | 300 | Al | 1x3 | XLPE |  | MDPE | 460 | 8.7642 | 524.4 | 9.9912 | 556.6 | 10.6047 | 385 | 7.3352 | 452.069 | 8.6131 | 479.8276 | 9.1419 | 0.1 | 0.13 | 0.1 | 0.489 | 153.6239 | 0.97564 | 0.642 | 0.043 | 0.489 | 153.6239 | 8.2645 | 10.7438 | 8.2645 | 0.018588 | 53.0579 | 3.5537 | 0.018588 | Prysmian 11kV SAWU SAC 35M WST 0115
11 | 400 | Al | 1x3 | XLPE |  | MDPE | 537 | 10.2312 | 612.18 | 11.6636 | 649.77 | 12.3798 | 449 | 8.5546 | 527.7414 | 10.0548 | 560.1466 | 10.6722 | 0.078 | 0.102 | 0.096 | 0.555 | 174.3584 | 1.1073 | 0.621 | 0.042 | 0.555 | 174.3584 | 6.4463 | 8.4298 | 7.9339 | 0.021097 | 51.3223 | 3.4711 | 0.021097 | Nexans (Pg 29) R0X0 calculated from Cu. TS-09-17 ratings
11kV 1c Triplex/Trefoil - Cu Metric
11 | 300 | Cu | 1x3 | XLPE |  | MDPE | 590 | 11.241 | 672.6 | 12.8148 | 713.9 | 13.6016 | 495 | 9.431 | 564.3 | 10.7514 | 598.95 | 11.4115 | 0.0601 | 0.079 | 0.099 | 0.512 | 160.8495 | 1.0215 | 0.603 | 0.042 | 0.512 | 160.8495 | 4.9669 | 6.5289 | 8.1818 | 0.019463 | 49.8347 | 3.4711 | 0.019463 | Prysmian 11kV SCWU 35M WST 0113
11 | 400 | Cu | 1x3 | XLPE |  | MDPE | 665 | 12.67 | 758.1 | 14.4437 | 804.65 | 15.3306 | 540 | 10.2884 | 615.6 | 11.7288 | 653.4 | 12.4489 | 0.047 | 0.0631 | 0.096 | 0.577 | 181.2699 | 1.1512 | 0.59 | 0.039 | 0.577 | 181.2699 | 3.8843 | 5.2149 | 7.9339 | 0.021934 | 48.7603 | 3.2231 | 0.021934 | Prysmian 11kV SCWU 35M WST 0113
11 | 500 | Cu | 1x3 | XLPE | Trefoil | MDPE | 750 | 14.2894 | 855 | 16.2899 | 907.5 | 17.2902 | 655 | 12.4794 | 746.7 | 14.2265 | 792.55 | 15.1001 | 0.0366 | 0.0508 | 0.092 | 0.647 | 203.261 | 1.2909 | 0.58 | 0.037 | 0.647 | 203.261 | 3.0248 | 4.1983 | 7.6033 | 0.024595 | 47.9339 | 3.0579 | 0.024595 | Prysmian 11kV SCWU 35M WST 0113
11 | 630 | Cu | 1x3 | XLPE | Trefoil | MDPE | 840 | 16.0041 | 957.6 | 18.2447 | 1016.4 | 19.365 | 730 | 13.9084 | 832.2 | 15.8555 | 883.3 | 16.8291 | 0.0283 | 0.0414 | 0.089 | 0.727 | 228.3938 | 1.4505 | 0.572 | 0.035 | 0.727 | 228.3938 | 2.3388 | 3.4215 | 7.3554 | 0.027636 | 47.2727 | 2.8926 | 0.027636 | Prysmian 11kV SCWU 35M WST 0113
11kV 3c PILCSWA - Al Metric
11 | 185 | Al | 3 | Paper (Belted) | Lead | SWA | 277 | 5.2776 | 319 | 6.0778 | 351 | 6.6874 | 238.7931 | 4.5496 | 275 | 5.2395 | 302.5862 | 5.765 | 0.164 | 0.195 | 0.07 | 0.57 | 179.0708 | 1.1373 | 0.92 | 0.102 | 0.475 | 149.2257 | 13.5537 | 16.1157 | 5.7851 | 0.021668 | 76.0331 | 8.4298 | 0.018056 | CBI Electric Table 17 - Al. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 240 | Al | 3 | Paper (Belted) | Lead | SWA | 323 | 6.154 | 373 | 7.1066 | 414 | 7.8878 | 278.4483 | 5.3052 | 321.5517 | 6.1264 | 356.8966 | 6.7998 | 0.125 | 0.15 | 0.068 | 0.64 | 201.0619 | 1.2769 | 0.819 | 0.098 | 0.53333 | 167.5516 | 10.3306 | 12.3967 | 5.6198 | 0.024328 | 67.686 | 8.0992 | 0.020274 | CBI Electric Table 17 - Al. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 300 | Al | 3 | Paper (Belted) | Lead | SWA | 364 | 6.9351 | 424 | 8.0783 | 473 | 9.0119 | 313.7931 | 5.9786 | 365.5172 | 6.964 | 407.7586 | 7.7688 | 0.1 | 0.12 | 0.066 | 0.7 | 219.9115 | 1.3966 | 0.679 | 0.094 | 0.58333 | 183.2596 | 8.2645 | 9.9174 | 5.4545 | 0.026609 | 56.1157 | 7.7686 | 0.022174 | CBI Electric Table 17 - Al. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 185 | Al | 3 | Paper (Screened) | Lead | SWA | 295 | 5.6205 | 342 | 6.516 | 379 | 7.2209 | 254.3103 | 4.8453 | 294.8276 | 5.6172 | 326.7241 | 6.2249 | 0.164 | 0.198 | 0.073 | 0.8 | 251.3274 | 1.5961 | 0.91 | 0.097 | 0.8 | 251.3274 | 13.5537 | 16.3636 | 6.0331 | 0.030411 | 75.2066 | 8.0165 | 0.030411 | CBI Electric Table 17 - Al. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 240 | Al | 3 | Paper (Screened) | Lead | SWA | 343 | 6.535 | 399 | 7.602 | 445 | 8.4784 | 295.6897 | 5.6336 | 343.9655 | 6.5534 | 383.6207 | 7.309 | 0.125 | 0.152 | 0.07 | 0.9 | 282.7433 | 1.7957 | 0.785 | 0.094 | 0.9 | 282.7433 | 10.3306 | 12.562 | 5.7851 | 0.034212 | 64.876 | 7.7686 | 0.034212 | CBI Electric Table 17 - Al. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 300 | Al | 3 | Paper (Screened) | Lead | SWA | 386 | 7.3543 | 453 | 8.6308 | 507 | 9.6596 | 332.7586 | 6.3399 | 390.5172 | 7.4404 | 437.069 | 8.3273 | 0.1 | 0.122 | 0.068 | 1 | 314.1593 | 1.9952 | 0.701 | 0.091 | 1 | 314.1593 | 8.2645 | 10.0826 | 5.6198 | 0.038013 | 57.9339 | 7.5207 | 0.038013 | CBI Electric Table 17 - Al. Capactiance from BICC Handbook P948. CRATER Ratings
11kV 3c PILCSWA - Cu Metric
11 | 185 | Cu | 3 | Paper (Belted) | Lead | SWA | 355 | 6.7637 | 407 | 7.7544 | 449 | 8.5546 | 306.0345 | 5.8307 | 350.8621 | 6.6848 | 387.069 | 7.3747 | 0.0991 | 0.118 | 0.07 | 0.57 | 179.0708 | 1.1373 | 0.842 | 0.102 | 0.475 | 149.2257 | 8.1901 | 9.7521 | 5.7851 | 0.021668 | 69.5868 | 8.4298 | 0.018056 | CBI Electric Table 17 - Cu. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 240 | Cu | 3 | Paper (Belted) | Lead | SWA | 411 | 7.8306 | 475 | 9.05 | 527 | 10.0407 | 354.3103 | 6.7505 | 409.4828 | 7.8017 | 454.3103 | 8.6558 | 0.074 | 0.09 | 0.068 | 0.64 | 201.0619 | 1.2769 | 0.759 | 0.098 | 0.53333 | 167.5516 | 6.1157 | 7.438 | 5.6198 | 0.024328 | 62.7273 | 8.0992 | 0.020274 | CBI Electric Table 17 - Cu. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 300 | Cu | 3 | Paper (Belted) | Lead | SWA | 460 | 8.7642 | 537 | 10.2312 | 599 | 11.4125 | 396.5517 | 7.5553 | 462.931 | 8.82 | 516.3793 | 9.8383 | 0.0601 | 0.072 | 0.066 | 0.7 | 219.9115 | 1.3966 | 0.68 | 0.094 | 0.58333 | 183.2596 | 4.9669 | 5.9504 | 5.4545 | 0.026609 | 56.1983 | 7.7686 | 0.022174 | CBI Electric Table 17 - Cu. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 185 | Cu | 3 | Paper (Screened) | Lead | SWA | 377 | 7.1828 | 437 | 8.326 | 485 | 9.2405 | 325 | 6.1921 | 376.7241 | 7.1776 | 418.1034 | 7.9659 | 0.0991 | 0.1201 | 0.073 | 0.8 | 251.3274 | 1.5961 | 0.832 | 0.097 | 0.8 | 251.3274 | 8.1901 | 9.9256 | 6.0331 | 0.030411 | 68.7603 | 8.0165 | 0.030411 | CBI Electric Table 17 - Cu. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 240 | Cu | 3 | Paper (Screened) | Lead | SWA | 436 | 8.3069 | 508 | 9.6787 | 567 | 10.8028 | 375.8621 | 7.1611 | 437.931 | 8.3437 | 488.7931 | 9.3128 | 0.0754 | 0.0923 | 0.07 | 0.9 | 282.7433 | 1.7957 | 0.726 | 0.094 | 0.9 | 282.7433 | 6.2314 | 7.6281 | 5.7851 | 0.034212 | 60 | 7.7686 | 0.034212 | CBI Electric Table 17 - Cu. Capactiance from BICC Handbook P948. CRATER Ratings
11 | 300 | Cu | 3 | Paper (Screened) | Lead | SWA | 488 | 9.2976 | 573 | 10.9171 | 643 | 12.2508 | 420.6897 | 8.0152 | 493.9655 | 9.4113 | 554.3103 | 10.561 | 0.0601 | 0.0746 | 0.068 | 1 | 314.1593 | 1.9952 | 0.653 | 0.091 | 1 | 314.1593 | 4.9669 | 6.1653 | 5.6198 | 0.038013 | 53.9669 | 7.5207 | 0.038013 | CBI Electric Table 17 - Cu. Capactiance from BICC Handbook P948. CRATER Ratings

## 20kV
20kV Underground cable ratings and parameters datasheet (IMP/001/013)
Version: | 1.2
| Conductors |  |  | Construction |  |  | Current Rating (Laid Direct) | [5 empty] | Current Rating (Ducted) | [5 empty] | Positive & Negative Sequence (Ohmic) | [5 empty] | Zero Sequence (Ohmic) |  |  |  | Positive & Negative Sequence (100MVA Base) |  |  |  | Zero Sequence (100MVA Base)
Voltage (kV) | mm2/in2 | Material | No. | Insulation | Sheath | Protection | Continuous |  | Cyclic |  | Emergency |  | Continuous |  | Cyclic |  | Emergency |  | DC Resistance Ω/km (20°C) | AC Resistance at max insulator temp Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | Charging Current A/km | Resistance Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | DC Resistance %/km (20°C) | AC Resistance at max insulator temp %/km | Reactance %/km | Susceptance %/km | Resistance %/km | Reactance %/km | Susceptance %/km
U | [6 empty] | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Rdc | R1=R2 | X1=X2 | C1=C2 | B1=B2 | IC | R0 | X0 | C0 | B0 | Rdc | R1=R2 | X1=X2 | B1=B2 | R0 | X0 | B0 | Source
20kV 3c PILCSWA Al - Metric
20 | 95 | Al | 3 | Paper (Screened) | Lead | SWA | 195 | 6.755 | 222.3 | 7.7007 | 235.95 | 8.1735 | 170 | 5.889 | 193.8 | 6.7134 | 205.7 | 7.1257 | 0.32 | 0.378 | 0.1 | 0.39 | 122.5221 | 1.4148 | 0.98136 | 0.1414 | 0.39 | 122.5221 | 8 | 9.45 | 2.5 | 0.049009 | 24.534 | 3.5349 | 0.049009 | BICC Cable Handbook table A12.20
20 | 185 | Al | 3 | Paper (Screened) | Lead | SWA | 285 | 9.8727 | 324.9 | 11.2549 | 344.85 | 11.946 | 245 | 8.487 | 279.3 | 9.6752 | 296.45 | 10.2693 | 0.164 | 0.195 | 0.091 | 0.51 | 160.2212 | 1.8501 | 0.7383 | 0.12829 | 0.51 | 160.2212 | 4.1 | 4.875 | 2.275 | 0.064088 | 18.4575 | 3.2072 | 0.064088 | BICC Cable Handbook table A12.20
20kV 3c PILCSWA Al - Imperial
20 | 0.04 | Al | 3 | Paper (Belted) | Lead | SWA | 82 | 2.8406 | 93.48 | 3.2382 | 99.22 | 3.4371 | 73 | 2.5288 | 83.22 | 2.8828 | 88.33 | 3.0598 | 1.106 | 1.4329 | 0.11815 | 0.20786 | 65.3011 | 0.75403 | 2.1662 | 0.16168 | 0.17322 | 54.4176 | 27.65 | 35.8217 | 2.9538 | 0.02612 | 54.1545 | 4.0421 | 0.021767 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.06 | Al | 3 | Paper (Belted) | Lead | SWA | 100 | 3.4641 | 114 | 3.9491 | 121 | 4.1916 | 90 | 3.1177 | 102.6 | 3.5542 | 108.9 | 3.7724 | 0.7302 | 0.91846 | 0.11049 | 0.24068 | 75.6119 | 0.87309 | 1.7648 | 0.14766 | 0.20057 | 63.0099 | 18.255 | 22.9615 | 2.7624 | 0.030245 | 44.1205 | 3.6916 | 0.025204 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.1 | Al | 3 | Paper (Belted) | Lead | SWA | 140 | 4.8497 | 159.6 | 5.5287 | 169.4 | 5.8682 | 125 | 4.3301 | 142.5 | 4.9363 | 151.25 | 5.2395 | 0.4342 | 0.53987 | 0.10174 | 0.2735 | 85.9226 | 0.99215 | 1.2847 | 0.13832 | 0.22792 | 71.6021 | 10.855 | 13.4968 | 2.5436 | 0.034369 | 32.1184 | 3.4579 | 0.028641 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.15 | Al | 3 | Paper (Belted) | Lead | SWA | 170 | 5.889 | 193.8 | 6.7134 | 205.7 | 7.1257 | 150 | 5.1962 | 171 | 5.9236 | 181.5 | 6.2873 | 0.2965 | 0.3684 | 0.096272 | 0.30632 | 96.2333 | 1.1112 | 1.0843 | 0.13364 | 0.25527 | 80.1944 | 7.4125 | 9.2101 | 2.4068 | 0.038493 | 27.1075 | 3.3411 | 0.032078 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.2 | Al | 3 | Paper (Belted) | Lead | SWA | 205 | 7.1014 | 233.7 | 8.0956 | 248.05 | 8.5927 | 185 | 6.4086 | 210.9 | 7.3058 | 223.85 | 7.7544 | 0.2231 | 0.27333 | 0.091896 | 0.35008 | 109.9809 | 1.2699 | 0.97894 | 0.12617 | 0.29173 | 91.6507 | 5.5775 | 6.8333 | 2.2974 | 0.043992 | 24.4735 | 3.1542 | 0.03666 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.25 | Al | 3 | Paper (Belted) | Lead | SWA | 235 | 8.1406 | 267.9 | 9.2803 | 284.35 | 9.8502 | 205 | 7.1014 | 233.7 | 8.0956 | 248.05 | 8.5927 | 0.1777 | 0.2207 | 0.089708 | 0.3829 | 120.2916 | 1.389 | 0.84069 | 0.1215 | 0.31908 | 100.243 | 4.4425 | 5.5176 | 2.2427 | 0.048117 | 21.0173 | 3.0374 | 0.040097 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.3 | Al | 3 | Paper (Belted) | Lead | SWA | 265 | 9.1799 | 302.1 | 10.4651 | 320.65 | 11.1076 | 235 | 8.1406 | 267.9 | 9.2803 | 284.35 | 9.8502 | 0.1448 | 0.18505 | 0.08752 | 0.41572 | 130.6023 | 1.5081 | 0.79886 | 0.11963 | 0.34643 | 108.8352 | 3.62 | 4.6263 | 2.188 | 0.052241 | 19.9716 | 2.9907 | 0.043534 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.04 | Al | 3 | Paper (Screened) | Lead | SWA | 95 | 3.2909 | 106 | 3.6719 | 113 | 3.9144 | 81.8966 | 2.837 | 91.3793 | 3.1655 | 97.4138 | 3.3745 | 1.106 | 1.463 | 0.138 | 0.289 | 90.792 | 1.0484 | 1.7069 | 0.173 | 0.289 | 90.792 | 27.65 | 36.5739 | 3.45 | 0.036317 | 42.673 | 4.325 | 0.036317 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20 | 0.06 | Al | 3 | Paper (Screened) | Lead | SWA | 119 | 4.1223 | 134 | 4.6419 | 144 | 4.9883 | 102.5862 | 3.5537 | 115.5172 | 4.0016 | 124.1379 | 4.3003 | 0.7302 | 0.93775 | 0.124 | 0.339 | 106.5 | 1.2298 | 1.461 | 0.158 | 0.339 | 106.5 | 18.255 | 23.4437 | 3.1 | 0.0426 | 36.5254 | 3.95 | 0.0426 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20 | 0.1 | Al | 3 | Paper (Screened) | Lead | SWA | 158 | 5.4733 | 179 | 6.2007 | 193 | 6.6857 | 136.2069 | 4.7183 | 154.3103 | 5.3455 | 166.3793 | 5.7635 | 0.4342 | 0.55121 | 0.104 | 0.399 | 125.3495 | 1.4474 | 1.104 | 0.148 | 0.399 | 125.3495 | 10.855 | 13.7802 | 2.6 | 0.05014 | 27.6002 | 3.7 | 0.05014 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20 | 0.15 | Al | 3 | Paper (Screened) | Lead | SWA | 196 | 6.7896 | 223 | 7.7249 | 241 | 8.3485 | 168.9655 | 5.8531 | 192.2414 | 6.6594 | 207.7586 | 7.197 | 0.2965 | 0.37614 | 0.095 | 0.459 | 144.1991 | 1.6651 | 0.96101 | 0.143 | 0.459 | 144.1991 | 7.4125 | 9.4035 | 2.375 | 0.05768 | 24.0252 | 3.575 | 0.05768 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20 | 0.2 | Al | 3 | Paper (Screened) | Lead | SWA | 229 | 7.9328 | 263 | 9.1106 | 285 | 9.8727 | 197.4138 | 6.8386 | 226.7241 | 7.854 | 245.6897 | 8.5109 | 0.2231 | 0.27907 | 0.091 | 0.513 | 161.1637 | 1.861 | 0.88617 | 0.135 | 0.513 | 161.1637 | 5.5775 | 6.9768 | 2.275 | 0.064465 | 22.1542 | 3.375 | 0.064465 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20 | 0.25 | Al | 3 | Paper (Screened) | Lead | SWA | 260 | 9.0067 | 299 | 10.3577 | 326 | 11.293 | 224.1379 | 7.7644 | 257.7586 | 8.929 | 281.0345 | 9.7353 | 0.1777 | 0.22534 | 0.088 | 0.554 | 174.0442 | 2.0097 | 0.76674 | 0.13 | 0.554 | 174.0442 | 4.4425 | 5.6334 | 2.2 | 0.069618 | 19.1684 | 3.25 | 0.069618 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20 | 0.3 | Al | 3 | Paper (Screened) | Lead | SWA | 290 | 10.0459 | 336 | 11.6394 | 367 | 12.7133 | 250 | 8.6603 | 289.6552 | 10.0339 | 316.3793 | 10.9597 | 0.1448 | 0.18894 | 0.086 | 0.593 | 186.2964 | 2.1512 | 0.73867 | 0.128 | 0.593 | 186.2964 | 3.62 | 4.7234 | 2.15 | 0.074519 | 18.4668 | 3.2 | 0.074519 | Conversion from Cu Values in ABB T&D 5th Edition Table 7. R0 estimated from metric PILCSWA. Ratings from CRATER
20kV 3c PILCSWA Cu - Imperial
20 | 0.04 | Cu | 3 | Paper (Belted) | Lead | SWA | 105 | 3.6373 | 119.7 | 4.1465 | 127.05 | 4.4011 | 94 | 3.2563 | 107.16 | 3.7121 | 113.74 | 3.9401 | 0.6748 | 0.844 | 0.11815 | 0.20786 | 65.3011 | 0.75403 | 1.7069 | 0.16168 | 0.17322 | 54.4176 | 16.87 | 21.1 | 2.9538 | 0.02612 | 42.673 | 4.0421 | 0.021767 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.06 | Cu | 3 | Paper (Belted) | Lead | SWA | 130 | 4.5033 | 148.2 | 5.1338 | 157.3 | 5.449 | 115 | 3.9837 | 131.1 | 4.5414 | 139.15 | 4.8203 | 0.4455 | 0.541 | 0.11049 | 0.24068 | 75.6119 | 0.87309 | 1.461 | 0.14766 | 0.20057 | 63.0099 | 11.1375 | 13.525 | 2.7624 | 0.030245 | 36.5254 | 3.6916 | 0.025204 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.1 | Cu | 3 | Paper (Belted) | Lead | SWA | 180 | 6.2354 | 205.2 | 7.1083 | 217.8 | 7.5448 | 160 | 5.5426 | 182.4 | 6.3185 | 193.6 | 6.7065 | 0.2649 | 0.318 | 0.10174 | 0.2735 | 85.9226 | 0.99215 | 1.104 | 0.13832 | 0.22792 | 71.6021 | 6.6225 | 7.95 | 2.5436 | 0.034369 | 27.6002 | 3.4579 | 0.028641 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.15 | Cu | 3 | Paper (Belted) | Lead | SWA | 220 | 7.621 | 250.8 | 8.688 | 266.2 | 9.2214 | 195 | 6.755 | 222.3 | 7.7007 | 235.95 | 8.1735 | 0.1808 | 0.217 | 0.096272 | 0.30632 | 96.2333 | 1.1112 | 0.96101 | 0.13364 | 0.25527 | 80.1944 | 4.52 | 5.425 | 2.4068 | 0.038493 | 24.0252 | 3.3411 | 0.032078 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.2 | Cu | 3 | Paper (Belted) | Lead | SWA | 265 | 9.1799 | 302.1 | 10.4651 | 320.65 | 11.1076 | 235 | 8.1406 | 267.9 | 9.2803 | 284.35 | 9.8502 | 0.1361 | 0.161 | 0.091896 | 0.35008 | 109.9809 | 1.2699 | 0.88617 | 0.12617 | 0.29173 | 91.6507 | 3.4025 | 4.025 | 2.2974 | 0.043992 | 22.1542 | 3.1542 | 0.03666 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.25 | Cu | 3 | Paper (Belted) | Lead | SWA | 300 | 10.3923 | 342 | 11.8472 | 363 | 12.5747 | 265 | 9.1799 | 302.1 | 10.4651 | 320.65 | 11.1076 | 0.1084 | 0.13 | 0.089708 | 0.3829 | 120.2916 | 1.389 | 0.76674 | 0.1215 | 0.31908 | 100.243 | 2.71 | 3.25 | 2.2427 | 0.048117 | 19.1684 | 3.0374 | 0.040097 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.3 | Cu | 3 | Paper (Belted) | Lead | SWA | 335 | 11.6047 | 381.9 | 13.2294 | 405.35 | 14.0417 | 295 | 10.2191 | 336.3 | 11.6498 | 356.95 | 12.3651 | 0.08837 | 0.109 | 0.08752 | 0.41572 | 130.6023 | 1.5081 | 0.73867 | 0.11963 | 0.34643 | 108.8352 | 2.2092 | 2.725 | 2.188 | 0.052241 | 18.4668 | 2.9907 | 0.043534 | BS480 Table x. R0X0 estimated from 11kV belted.
20 | 0.04 | Cu | 3 | Paper (Screened) | Lead | SWA | 122 | 4.2262 | 137 | 4.7458 | 146 | 5.0576 | 105.1724 | 3.6433 | 118.1034 | 4.0912 | 125.8621 | 4.36 | 0.6748 | 0.86105 | 0.138 | 0.289 | 90.792 | 1.0484 | 1.3524 | 0.173 | 0.289 | 90.792 | 16.87 | 21.5263 | 3.45 | 0.036317 | 33.8102 | 4.325 | 0.036317 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20 | 0.06 | Cu | 3 | Paper (Screened) | Lead | SWA | 154 | 5.3347 | 173 | 5.9929 | 185 | 6.4086 | 132.7586 | 4.5989 | 149.1379 | 5.1663 | 159.4828 | 5.5246 | 0.4455 | 0.55193 | 0.124 | 0.339 | 106.5 | 1.2298 | 1.1965 | 0.158 | 0.339 | 106.5 | 11.1375 | 13.7983 | 3.1 | 0.0426 | 29.9119 | 3.95 | 0.0426 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20 | 0.1 | Cu | 3 | Paper (Screened) | Lead | SWA | 204 | 7.0668 | 231 | 8.0021 | 248 | 8.591 | 175.8621 | 6.092 | 199.1379 | 6.8983 | 213.7931 | 7.406 | 0.2649 | 0.32443 | 0.104 | 0.399 | 125.3495 | 1.4474 | 0.94558 | 0.148 | 0.399 | 125.3495 | 6.6225 | 8.1106 | 2.6 | 0.05014 | 23.6394 | 3.7 | 0.05014 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20 | 0.15 | Cu | 3 | Paper (Screened) | Lead | SWA | 251 | 8.6949 | 286 | 9.9073 | 309 | 10.7041 | 216.3793 | 7.4956 | 246.5517 | 8.5408 | 266.3793 | 9.2276 | 0.1808 | 0.22138 | 0.095 | 0.459 | 144.1991 | 1.6651 | 0.8549 | 0.143 | 0.459 | 144.1991 | 4.52 | 5.5346 | 2.375 | 0.05768 | 21.3725 | 3.575 | 0.05768 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20 | 0.2 | Cu | 3 | Paper (Screened) | Lead | SWA | 294 | 10.1845 | 337 | 11.674 | 366 | 12.6786 | 253.4483 | 8.7797 | 290.5172 | 10.0638 | 315.5172 | 10.9298 | 0.1361 | 0.16425 | 0.091 | 0.513 | 161.1637 | 1.861 | 0.80744 | 0.135 | 0.513 | 161.1637 | 3.4025 | 4.1063 | 2.275 | 0.064465 | 20.186 | 3.375 | 0.064465 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20 | 0.25 | Cu | 3 | Paper (Screened) | Lead | SWA | 332 | 11.5008 | 382 | 13.2329 | 416 | 14.4107 | 286.2069 | 9.9145 | 329.3103 | 11.4076 | 358.6207 | 12.423 | 0.1084 | 0.13263 | 0.088 | 0.554 | 174.0442 | 2.0097 | 0.70317 | 0.13 | 0.554 | 174.0442 | 2.71 | 3.3157 | 2.2 | 0.069618 | 17.5792 | 3.25 | 0.069618 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20 | 0.3 | Cu | 3 | Paper (Screened) | Lead | SWA | 370 | 12.8172 | 428 | 14.8264 | 468 | 16.212 | 318.9655 | 11.0493 | 368.9655 | 12.7813 | 403.4483 | 13.9759 | 0.08837 | 0.1112 | 0.086 | 0.593 | 186.2964 | 2.1512 | 0.68537 | 0.128 | 0.593 | 186.2964 | 2.2092 | 2.7801 | 2.15 | 0.074519 | 17.1343 | 3.2 | 0.074519 | ABB T&D 5th Edition Table 7. Rdc from temp equation. R0 resistances estimated from metric PILCSWA
20kV 1c Triplex Al - Metric
20 | 95 | Al | 1 | XLPE |  | MDPE | 245 | 8.487 | 279.3 | 9.6752 | 296.45 | 10.2693 | 205 | 7.1014 | 233.7 | 8.0956 | 248.05 | 8.5927 | 0.32 | 0.411 | 0.129 | 0.219 | 68.8009 | 0.79444 | 0.862 | 0.07 | 0.219 | 68.8009 | 8 | 10.275 | 3.225 | 0.02752 | 21.55 | 1.75 | 0.02752 | Prysmian 22kV SAWU SAC 35M WST 0113
20 | 150 | Al | 1 | XLPE |  | MPDE | 310 | 10.7387 | 353.4 | 12.2421 | 375.1 | 12.9938 | 265 | 9.1799 | 302.1 | 10.4651 | 320.65 | 11.1076 | 0.206 | 0.265 | 0.12 | 0.254 | 79.7965 | 0.92141 | 0.748 | 0.062 | 0.254 | 79.7965 | 5.15 | 6.625 | 3 | 0.031919 | 18.7 | 1.55 | 0.031919 | Prysmian 22kV SAWU SAC 35M WST 0114
20 | 185 | Al | 1 | XLPE |  | MDPE | 355 | 12.2976 | 404.7 | 14.0192 | 429.55 | 14.88 | 295 | 10.2191 | 336.3 | 11.6498 | 356.95 | 12.3651 | 0.164 | 0.211 | 0.116 | 0.274 | 86.0796 | 0.99396 | 0.706 | 0.059 | 0.274 | 86.0796 | 4.1 | 5.275 | 2.9 | 0.034432 | 17.65 | 1.475 | 0.034432 | Prysmian 22kV SAWU SAC 35M WST 0115
20 | 240 | Al | 1 | XLPE |  | MDPE | 410 | 14.2028 | 467.4 | 16.1912 | 496.1 | 17.1854 | 355 | 12.2976 | 404.7 | 14.0192 | 429.55 | 14.88 | 0.125 | 0.161 | 0.111 | 0.303 | 95.1903 | 1.0992 | 0.667 | 0.054 | 0.303 | 95.1903 | 3.125 | 4.025 | 2.775 | 0.038076 | 16.675 | 1.35 | 0.038076 | Prysmian 22kV SAWU SAC 35M WST 0116
20 | 300 | Al | 1 | XLPE |  | MDPE | 460 | 15.9349 | 524.4 | 18.1657 | 556.6 | 19.2812 | 400 | 13.8564 | 456 | 15.7963 | 484 | 16.7663 | 0.1 | 0.129 | 0.107 | 0.33 | 103.6726 | 1.1971 | 0.642 | 0.051 | 0.33 | 103.6726 | 2.5 | 3.225 | 2.675 | 0.041469 | 16.05 | 1.275 | 0.041469 | Prysmian 22kV SAWU SAC 35M WST 0117
20kV 1c Triplex/Trefoil Cu - Metric
20 | 150 | Cu | 1 | XLPE |  | MDPE | 405 | 14.0296 | 461.7 | 15.9938 | 490.05 | 16.9758 | 340 | 11.7779 | 387.6 | 13.4269 | 411.4 | 14.2513 | 0.124 | 0.159 | 0.119 | 0.265 | 83.2522 | 0.96131 | 0.666 | 0.061 | 0.265 | 83.2522 | 3.1 | 3.975 | 2.975 | 0.033301 | 16.65 | 1.525 | 0.033301 | Prysmian 22kV SCWU 35M WST 0113
20 | 185 | Cu | 1 | XLPE |  | MDPE | 455 | 15.7617 | 518.7 | 17.9683 | 550.55 | 19.0716 | 385 | 13.3368 | 438.9 | 15.2039 | 465.85 | 16.1375 | 0.0991 | 0.128 | 0.115 | 0.287 | 90.1637 | 1.0411 | 0.641 | 0.057 | 0.287 | 90.1637 | 2.4775 | 3.2 | 2.875 | 0.036065 | 16.025 | 1.425 | 0.036065 | Prysmian 22kV SCWU 35M WST 0113
20 | 240 | Cu | 1 | XLPE |  | MDPE | 525 | 18.1865 | 598.5 | 20.7326 | 635.25 | 22.0057 | 455 | 15.7617 | 518.7 | 17.9683 | 550.55 | 19.0716 | 0.0754 | 0.098 | 0.111 | 0.314 | 98.646 | 1.1391 | 0.618 | 0.054 | 0.314 | 98.646 | 1.885 | 2.45 | 2.775 | 0.039458 | 15.45 | 1.35 | 0.039458 | Prysmian 22kV SCWU 35M WST 0114
20 | 300 | Cu | 1 | XLPE |  | MDPE | 590 | 20.4382 | 672.6 | 23.2995 | 713.9 | 24.7302 | 510 | 17.6669 | 581.4 | 20.1403 | 617.1 | 21.377 | 0.0601 | 0.079 | 0.106 | 0.344 | 108.0708 | 1.2479 | 0.603 | 0.05 | 0.344 | 108.0708 | 1.5025 | 1.975 | 2.65 | 0.043228 | 15.075 | 1.25 | 0.043228 | Prysmian 22kV SCWU 35M WST 0115
20 | 400 | Cu | 1 | XLPE |  | MDPE | 670 | 23.2095 | 763.8 | 26.4588 | 810.7 | 28.0835 | 540 | 18.7061 | 615.6 | 21.325 | 653.4 | 22.6344 | 0.047 | 0.0627 | 0.102 | 0.385 | 120.9513 | 1.3966 | 0.59 | 0.047 | 0.385 | 120.9513 | 1.175 | 1.5675 | 2.55 | 0.048381 | 14.75 | 1.175 | 0.048381 | Prysmian 22kV SCWU 35M WST 0116
20 | 500 | Cu | 1 | XLPE | Trefoil | MDPE | 755 | 26.154 | 860.7 | 29.8155 | 913.55 | 31.6463 | 665 | 23.0363 | 758.1 | 26.2614 | 804.65 | 27.8739 | 0.0366 | 0.0503 | 0.099 | 0.434 | 136.3451 | 1.5744 | 0.58 | 0.044 | 0.434 | 136.3451 | 0.915 | 1.2575 | 2.475 | 0.054538 | 14.5 | 1.1 | 0.054538 | Prysmian 22kV SCWU 35M WST 0117
20 | 630 | Cu | 1 | XLPE | Trefoil | MDPE | 845 | 29.2717 | 963.3 | 33.3697 | 1022.45 | 35.4187 | 740 | 25.6344 | 843.6 | 29.2232 | 895.4 | 31.0176 | 0.0283 | 0.0408 | 0.095 | 0.484 | 152.0531 | 1.7558 | 0.572 | 0.041 | 0.484 | 152.0531 | 0.7075 | 1.02 | 2.375 | 0.060821 | 14.3 | 1.025 | 0.060821 | Prysmian 22kV SCWU 35M WST 0118

## 33kV
33kV Underground cable ratings and parameters datasheet (IMP/001/013)
Version: | 1.2
| Conductors |  |  | Construction |  |  | Current Rating (Laid Direct) | [5 empty] | Current Rating (Ducted) | [5 empty] | Positive & Negative Sequence (Ohmic) | [5 empty] | Zero Sequence (Ohmic) |  |  |  | Positive & Negative Sequence (100MVA Base) |  |  |  | Zero Sequence (100MVA Base)
Voltage (kV) | mm2/in2 | Material | No. | Insulation | Sheath | Protection | Continuous |  | Cyclic |  | Emergency |  | Continuous |  | Cyclic |  | Emergency |  | DC Resistance Ω/km (20°C) | AC Resistance at max insulator temp Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | Charging Current A/km | Resistance Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | DC Resistance %/km (20°C) | AC Resistance at max insulator temp %/km | Reactance %/km | Susceptance %/km | Resistance %/km | Reactance %/km | Susceptance %/km
U | [6 empty] | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Rdc | R1=R2 | X1=X2 | C1=C2 | B1=B2 | IC | R0 | X0 | C0 | B0 | Rdc | R1=R2 | X1=X2 | B1=B2 | R0 | X0 | B0 | Source
33kV 1c Trefoil XLPE Al - Pb Sheath - Metric
33 | 120 | Al | 1 | XLPE | Pb |  | 285 | 16.2899 | 324.9 | 18.5705 | 344.85 | 19.7108 | 270 | 15.4326 | 307.8 | 17.5931 | 326.7 | 18.6734 | 0.253 | 0.325 | 0.138 | 0.188 | 59.0619 | 1.1253 | 1.1 | 0.082 | 0.188 | 59.0619 | 2.3232 | 2.9844 | 1.2672 | 0.064318 | 10.101 | 0.75298 | 0.064318 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 150 | Al | 1 | XLPE | Pb |  | 320 | 18.2905 | 364.8 | 20.8511 | 387.2 | 22.1315 | 300 | 17.1473 | 342 | 19.5479 | 363 | 20.7482 | 0.206 | 0.265 | 0.133 | 0.2 | 62.8319 | 1.1971 | 1.064 | 0.078 | 0.2 | 62.8319 | 1.8916 | 2.4334 | 1.2213 | 0.068424 | 9.7704 | 0.71625 | 0.068424 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 185 | Al | 1 | XLPE | Pb |  | 360 | 20.5768 | 410.4 | 23.4575 | 435.6 | 24.8979 | 340 | 19.4336 | 387.6 | 22.1543 | 411.4 | 23.5147 | 0.164 | 0.211 | 0.128 | 0.216 | 67.8584 | 1.2929 | 1.029 | 0.073 | 0.216 | 67.8584 | 1.506 | 1.9376 | 1.1754 | 0.073898 | 9.449 | 0.67034 | 0.073898 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 240 | Al | 1 | XLPE | Pb |  | 420 | 24.0062 | 478.8 | 27.3671 | 508.2 | 29.0475 | 390 | 22.2915 | 444.6 | 25.4123 | 471.9 | 26.9727 | 0.125 | 0.161 | 0.122 | 0.239 | 75.0841 | 1.4305 | 0.982 | 0.067 | 0.239 | 75.0841 | 1.1478 | 1.4784 | 1.1203 | 0.081767 | 9.0174 | 0.61524 | 0.081767 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 300 | Al | 1 | XLPE | Pb |  | 475 | 27.1499 | 541.5 | 30.9509 | 574.75 | 32.8514 | 440 | 25.1494 | 501.6 | 28.6703 | 532.4 | 30.4307 | 1 | 0.129 | 0.118 | 0.255 | 80.1106 | 1.5263 | 0.878 | 0.064 | 0.255 | 80.1106 | 9.1827 | 1.1846 | 1.0836 | 0.08724 | 8.0624 | 0.5877 | 0.08724 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 400 | Al | 1 | XLPE | Pb |  | 540 | 30.8651 | 615.6 | 35.1863 | 653.4 | 37.3468 | 495 | 28.293 | 564.3 | 32.2541 | 598.95 | 34.2346 | 0.078 | 0.101 | 0.113 | 0.285 | 89.5354 | 1.7059 | 0.8 | 0.059 | 0.285 | 89.5354 | 0.71625 | 0.92746 | 1.0376 | 0.097504 | 7.3462 | 0.54178 | 0.097504 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 500 | Al | 1 | XLPE | Pb |  | 620 | 35.4378 | 706.8 | 40.399 | 750.2 | 42.8797 | 560 | 32.0083 | 638.4 | 36.4895 | 677.6 | 38.73 | 0.061 | 0.08 | 0.11 | 0.328 | 103.0442 | 1.9633 | 0.683 | 0.057 | 0.328 | 103.0442 | 0.56015 | 0.73462 | 1.0101 | 0.11222 | 6.2718 | 0.52342 | 0.11222 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 630 | Al | 1 | XLPE | Pb |  | 700 | 40.0104 | 798 | 45.6118 | 847 | 48.4126 | 630 | 36.0093 | 718.2 | 41.0506 | 762.3 | 43.5713 | 0.047 | 0.063 | 0.107 | 0.36 | 113.0973 | 2.1548 | 0.577 | 0.053 | 0.36 | 113.0973 | 0.43159 | 0.57851 | 0.98255 | 0.12316 | 5.2984 | 0.48669 | 0.12316 | Prysmian - 33kV BS7870-4.11 Al 0908
33 | 800 | Al | 1 | XLPE | Pb |  | 785 | 44.8688 | 894.9 | 51.1504 | 949.85 | 54.2912 | 695 | 39.7246 | 792.3 | 45.286 | 840.95 | 48.0667 | 0.037 | 0.05 | 0.103 | 0.398 | 125.0354 | 2.3822 | 0.529 | 0.05 | 0.398 | 125.0354 | 0.33976 | 0.45914 | 0.94582 | 0.13616 | 4.8577 | 0.45914 | 0.13616 | Prysmian - 33kV BS7870-4.11 Al 0908
33kV 1c Trefoil XLPE Cu - Pb Sheath - Metric
33 | 120 | Cu | 1 | XLPE | Pb |  | 365 | 20.8626 | 416.1 | 23.7833 | 441.65 | 25.2437 | 345 | 19.7194 | 393.3 | 22.4801 | 417.45 | 23.8605 | 0.153 | 0.1957 | 0.138 | 0.188 | 59.0619 | 1.1253 | 1.002 | 0.082 | 0.188 | 59.0619 | 1.405 | 1.7971 | 1.2672 | 0.064318 | 9.2011 | 0.75298 | 0.064318 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 150 | Cu | 1 | XLPE | Pb |  | 410 | 23.4346 | 467.4 | 26.7155 | 496.1 | 28.3559 | 385 | 22.0057 | 438.9 | 25.0865 | 465.85 | 26.6269 | 0.124 | 0.1589 | 0.133 | 0.2 | 62.8319 | 1.1971 | 0.983 | 0.078 | 0.2 | 62.8319 | 1.1387 | 1.4591 | 1.2213 | 0.068424 | 9.0266 | 0.71625 | 0.068424 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 185 | Cu | 1 | XLPE | Pb |  | 465 | 26.5783 | 530.1 | 30.2993 | 562.65 | 32.1598 | 430 | 24.5778 | 490.2 | 28.0187 | 520.3 | 29.7391 | 0.0991 | 0.1273 | 0.128 | 0.216 | 67.8584 | 1.2929 | 0.964 | 0.073 | 0.216 | 67.8584 | 0.91001 | 1.169 | 1.1754 | 0.073898 | 8.8522 | 0.67034 | 0.073898 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 240 | Cu | 1 | XLPE | Pb |  | 535 | 30.5794 | 609.9 | 34.8605 | 647.35 | 37.001 | 495 | 28.293 | 564.3 | 32.2541 | 598.95 | 34.2346 | 0.0754 | 0.0975 | 0.123 | 0.234 | 73.5133 | 1.4006 | 0.943 | 0.068 | 0.234 | 73.5133 | 0.69238 | 0.89532 | 1.1295 | 0.080056 | 8.6593 | 0.62443 | 0.080056 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 300 | Cu | 1 | XLPE | Pb |  | 605 | 34.5804 | 689.7 | 39.4216 | 732.05 | 41.8423 | 550 | 31.4367 | 627 | 35.8379 | 665.5 | 38.0384 | 0.0601 | 0.0784 | 0.118 | 0.255 | 80.1106 | 1.5263 | 0.839 | 0.064 | 0.255 | 80.1106 | 0.55188 | 0.71993 | 1.0836 | 0.08724 | 7.7043 | 0.5877 | 0.08724 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 400 | Cu | 1 | XLPE | Pb |  | 685 | 39.153 | 780.9 | 44.6344 | 828.85 | 47.3751 | 620 | 35.4378 | 706.8 | 40.399 | 750.2 | 42.8797 | 0.047 | 0.0623 | 0.113 | 0.283 | 88.9071 | 1.6939 | 0.773 | 0.059 | 0.283 | 88.9071 | 0.43159 | 0.57208 | 1.0376 | 0.09682 | 7.0983 | 0.54178 | 0.09682 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 500 | Cu | 1 | XLPE | Pb |  | 770 | 44.0114 | 877.8 | 50.173 | 931.7 | 53.2538 | 690 | 39.4388 | 786.6 | 44.9602 | 834.9 | 47.7209 | 0.0366 | 0.0497 | 0.111 | 0.326 | 102.4159 | 1.9513 | 0.663 | 0.057 | 0.326 | 102.4159 | 0.33609 | 0.45638 | 1.0193 | 0.11153 | 6.0882 | 0.52342 | 0.11153 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 630 | Cu | 1 | XLPE | Pb |  | 965 | 55.1572 | 1100.1 | 62.8792 | 1167.65 | 66.7402 | 755 | 43.154 | 860.7 | 49.1956 | 913.55 | 52.2164 | 0.0283 | 0.04 | 0.107 | 0.36 | 113.0973 | 2.1548 | 0.559 | 0.053 | 0.36 | 113.0973 | 0.25987 | 0.36731 | 0.98255 | 0.12316 | 5.1331 | 0.48669 | 0.12316 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 800 | Cu | 1 | XLPE | Pb |  | 955 | 54.5856 | 1088.7 | 62.2276 | 1155.55 | 66.0486 | 820 | 46.8693 | 934.8 | 53.431 | 992.2 | 56.7118 | 0.0221 | 0.0332 | 0.103 | 0.398 | 125.0354 | 2.3822 | 0.515 | 0.05 | 0.398 | 125.0354 | 0.20294 | 0.30487 | 0.94582 | 0.13616 | 4.7291 | 0.45914 | 0.13616 | Prysmian - 33kV BS7870-4.11 Cu 0909
33 | 1000 | Cu | 1 | XLPE | Pb |  | 1025 | 58.5866 | 1168.5 | 66.7887 | 1240.25 | 70.8898 | 870 | 49.7272 | 991.8 | 56.689 | 1052.7 | 60.1699 | 0.0176 | 0.0284 | 0.1 | 0.436 | 136.9734 | 2.6097 | 0.44 | 0.047 | 0.436 | 136.9734 | 0.16162 | 0.26079 | 0.91827 | 0.14916 | 4.0404 | 0.43159 | 0.14916 | Prysmian - 33kV BS7870-4.11 Cu 0909
33kV 1c Trefoil XLPE Al - Cu Screen - Metric
33 | 50 | Al | 1 | XLPE | CWS |  | 170 | 9.7168 | 193.8 | 11.0772 | 205.7 | 11.7573 | 165 | 9.431 | 188.1 | 10.7514 | 199.65 | 11.4115 | 0.641 | 0.822 | 0.152 | 0.144 | 45.2389 | 0.86192 | 1.183 | 0.094 | 0.144 | 45.2389 | 5.8861 | 7.5482 | 1.3958 | 0.049265 | 10.8632 | 0.86318 | 0.049265 | Prysmian - 33kV SAWU 35M WST 0113
33 | 70 | Al | 1 | XLPE | CWS |  | 205 | 11.7173 | 233.7 | 13.3577 | 248.05 | 14.178 | 200 | 11.4315 | 228 | 13.032 | 242 | 13.8322 | 0.443 | 0.568 | 0.144 | 0.159 | 49.9513 | 0.9517 | 0.985 | 0.087 | 0.159 | 49.9513 | 4.068 | 5.2158 | 1.3223 | 0.054397 | 9.045 | 0.7989 | 0.054397 | Prysmian - 33kV SAWU 35M WST 0113
33 | 95 | Al | 1 | XLPE | CWS |  | 245 | 14.0036 | 279.3 | 15.9641 | 296.45 | 16.9444 | 235 | 13.4321 | 267.9 | 15.3125 | 284.35 | 16.2528 | 0.32 | 0.411 | 0.137 | 0.175 | 54.9779 | 1.0475 | 0.862 | 0.08 | 0.175 | 54.9779 | 2.9385 | 3.7741 | 1.258 | 0.059871 | 7.9155 | 0.73462 | 0.059871 | Prysmian - 33kV SAWU 35M WST 0113
33 | 120 | Al | 1 | XLPE | CWS |  | 280 | 16.0041 | 319.2 | 18.2447 | 338.8 | 19.365 | 265 | 15.1468 | 302.1 | 17.2673 | 320.65 | 18.3276 | 0.253 | 0.325 | 0.132 | 0.188 | 59.0619 | 1.1253 | 0.795 | 0.076 | 0.188 | 59.0619 | 2.3232 | 2.9844 | 1.2121 | 0.064318 | 7.3003 | 0.69789 | 0.064318 | Prysmian - 33kV SAWU 35M WST 0113
33 | 150 | Al | 1 | XLPE | CWS |  | 315 | 18.0047 | 359.1 | 20.5253 | 381.15 | 21.7856 | 295 | 16.8615 | 336.3 | 19.2221 | 356.95 | 20.4024 | 0.206 | 0.265 | 0.128 | 0.201 | 63.146 | 1.2031 | 0.748 | 0.071 | 0.201 | 63.146 | 1.8916 | 2.4334 | 1.1754 | 0.068766 | 6.8687 | 0.65197 | 0.068766 | Prysmian - 33kV SAWU 35M WST 0113
33 | 185 | Al | 1 | XLPE | CWS |  | 355 | 20.291 | 404.7 | 23.1317 | 429.55 | 24.5521 | 335 | 19.1478 | 381.9 | 21.8285 | 405.35 | 23.1689 | 0.164 | 0.211 | 0.123 | 0.216 | 67.8584 | 1.2929 | 0.706 | 0.067 | 0.216 | 67.8584 | 1.506 | 1.9376 | 1.1295 | 0.073898 | 6.483 | 0.61524 | 0.073898 | Prysmian - 33kV SAWU 35M WST 0113
33 | 240 | Al | 1 | XLPE | CWS |  | 415 | 23.7204 | 473.1 | 27.0413 | 502.15 | 28.7017 | 385 | 22.0057 | 438.9 | 25.0865 | 465.85 | 26.6269 | 0.125 | 0.161 | 0.117 | 0.239 | 75.0841 | 1.4305 | 0.667 | 0.062 | 0.239 | 75.0841 | 1.1478 | 1.4784 | 1.0744 | 0.081767 | 6.1249 | 0.56933 | 0.081767 | Prysmian - 33kV SAWU 35M WST 0113
33 | 300 | Al | 1 | XLPE | CWS |  | 465 | 26.5783 | 530.1 | 30.2993 | 562.65 | 32.1598 | 430 | 24.5778 | 490.2 | 28.0187 | 520.3 | 29.7391 | 0.1 | 0.129 | 0.114 | 0.255 | 80.1106 | 1.5263 | 0.642 | 0.059 | 0.255 | 80.1106 | 0.91827 | 1.1846 | 1.0468 | 0.08724 | 5.8953 | 0.54178 | 0.08724 | Prysmian - 33kV SAWU 35M WST 0113
33 | 400 | Al | 1 | XLPE | CWS |  | 535 | 30.5794 | 609.9 | 34.8605 | 647.35 | 37.001 | 485 | 27.7215 | 552.9 | 31.6025 | 586.85 | 33.543 | 0.078 | 0.101 | 0.109 | 0.285 | 89.5354 | 1.7059 | 0.62 | 0.054 | 0.285 | 89.5354 | 0.71625 | 0.92746 | 1.0009 | 0.097504 | 5.6933 | 0.49587 | 0.097504 | Prysmian - 33kV SAWU 35M WST 0113
33 | 500 | Al | 1 | XLPE | CWS |  | 610 | 34.8662 | 695.4 | 39.7474 | 738.1 | 42.1881 | 550 | 31.4367 | 627 | 35.8379 | 665.5 | 38.0384 | 0.061 | 0.08 | 0.105 | 0.321 | 100.8451 | 1.9214 | 0.603 | 0.051 | 0.321 | 100.8451 | 0.56015 | 0.73462 | 0.96419 | 0.10982 | 5.5372 | 0.46832 | 0.10982 | Prysmian - 33kV SAWU 35M WST 0113
33 | 630 | Al | 1 | XLPE | CWS |  | 690 | 39.4388 | 786.6 | 44.9602 | 834.9 | 47.7209 | 620 | 35.4378 | 706.8 | 40.399 | 750.2 | 42.8797 | 0.047 | 0.063 | 0.102 | 0.352 | 110.5841 | 2.1069 | 0.59 | 0.048 | 0.352 | 110.5841 | 0.43159 | 0.57851 | 0.93664 | 0.12043 | 5.4178 | 0.44077 | 0.12043 | Prysmian - 33kV SAWU 35M WST 0113
33 | 800 | Al | 1 | XLPE | CWS |  | 780 | 44.583 | 889.2 | 50.8246 | 943.8 | 53.9454 | 695 | 39.7246 | 792.3 | 45.286 | 840.95 | 48.0667 | 0.037 | 0.051 | 0.098 | 0.39 | 122.5221 | 2.3344 | 0.58 | 0.045 | 0.39 | 122.5221 | 0.33976 | 0.46832 | 0.89991 | 0.13343 | 5.326 | 0.41322 | 0.13343 | Prysmian - 33kV SAWU 35M WST 0113
33 | 1000 | Al | 1 | XLPE | CWS |  | 865 | 49.4414 | 986.1 | 56.3632 | 1046.65 | 59.8241 | 765 | 43.7256 | 872.1 | 49.8472 | 925.65 | 52.908 | 0.029 | 0.042 | 0.095 | 0.429 | 134.7743 | 2.5678 | 0.573 | 0.042 | 0.429 | 134.7743 | 0.2663 | 0.38567 | 0.87236 | 0.14677 | 5.2617 | 0.38567 | 0.14677 | Prysmian - 33kV SAWU 35M WST 0113
33kV Trefoil 1c XLPE Cu - Cu Screen - Metric
33 | 50 | Cu | 1 | XLPE | CWS |  | 215 | 12.2889 | 245.1 | 14.0093 | 260.15 | 14.8696 | 210 | 12.0031 | 239.4 | 13.6835 | 254.1 | 14.5238 | 0.387 | 0.494 | 0.153 | 0.143 | 44.9248 | 0.85593 | 0.929 | 0.095 | 0.143 | 44.9248 | 3.5537 | 4.5363 | 1.405 | 0.048923 | 8.5308 | 0.87236 | 0.048923 | Prysmian - 33kV SCWU 35M WST 0113
33 | 70 | Cu | 1 | XLPE | CWS |  | 265 | 15.1468 | 302.1 | 17.2673 | 320.65 | 18.3276 | 255 | 14.5752 | 290.7 | 16.6157 | 308.55 | 17.636 | 0.268 | 0.342 | 0.144 | 0.159 | 49.9513 | 0.9517 | 0.81 | 0.087 | 0.159 | 49.9513 | 2.461 | 3.1405 | 1.3223 | 0.054397 | 7.438 | 0.7989 | 0.054397 | Prysmian - 33kV SCWU 35M WST 0113
33 | 95 | Cu | 1 | XLPE | CWS |  | 320 | 18.2905 | 364.8 | 20.8511 | 387.2 | 22.1315 | 300 | 17.1473 | 342 | 19.5479 | 363 | 20.7482 | 0.193 | 0.247 | 0.137 | 0.174 | 54.6637 | 1.0415 | 0.735 | 0.08 | 0.174 | 54.6637 | 1.7723 | 2.2681 | 1.258 | 0.059529 | 6.7493 | 0.73462 | 0.059529 | Prysmian - 33kV SCWU 35M WST 0113
33 | 120 | Cu | 1 | XLPE | CWS |  | 360 | 20.5768 | 410.4 | 23.4575 | 435.6 | 24.8979 | 340 | 19.4336 | 387.6 | 22.1543 | 411.4 | 23.5147 | 0.153 | 0.196 | 0.132 | 0.188 | 59.0619 | 1.1253 | 0.695 | 0.076 | 0.188 | 59.0619 | 1.405 | 1.7998 | 1.2121 | 0.064318 | 6.382 | 0.69789 | 0.064318 | Prysmian - 33kV SCWU 35M WST 0113
33 | 150 | Cu | 1 | XLPE | CWS |  | 405 | 23.1489 | 461.7 | 26.3897 | 490.05 | 28.0101 | 375 | 21.4341 | 427.5 | 24.4349 | 453.75 | 25.9353 | 0.124 | 0.159 | 0.128 | 0.2 | 62.8319 | 1.1971 | 0.666 | 0.072 | 0.2 | 62.8319 | 1.1387 | 1.4601 | 1.1754 | 0.068424 | 6.1157 | 0.66116 | 0.068424 | Prysmian - 33kV SCWU 35M WST 0113
33 | 185 | Cu | 1 | XLPE | CWS |  | 455 | 26.0067 | 518.7 | 29.6477 | 550.55 | 31.4682 | 420 | 24.0062 | 478.8 | 27.3671 | 508.2 | 29.0475 | 0.099 | 0.127 | 0.123 | 0.216 | 67.8584 | 1.2929 | 0.641 | 0.067 | 0.216 | 67.8584 | 0.90909 | 1.1662 | 1.1295 | 0.073898 | 5.8861 | 0.61524 | 0.073898 | Prysmian - 33kV SCWU 35M WST 0113
33 | 240 | Cu | 1 | XLPE | CWS |  | 525 | 30.0078 | 598.5 | 34.2089 | 635.25 | 36.3094 | 480 | 27.4357 | 547.2 | 31.2767 | 580.8 | 33.1972 | 0.075 | 0.098 | 0.118 | 0.234 | 73.5133 | 1.4006 | 0.618 | 0.063 | 0.234 | 73.5133 | 0.68871 | 0.89991 | 1.0836 | 0.080056 | 5.6749 | 0.57851 | 0.080056 | Prysmian - 33kV SCWU 35M WST 0113
33 | 300 | Cu | 1 | XLPE | CWS |  | 590 | 33.723 | 672.6 | 38.4443 | 713.9 | 40.8049 | 535 | 30.5794 | 609.9 | 34.8605 | 647.35 | 37.001 | 0.06 | 0.078 | 0.114 | 0.255 | 80.1106 | 1.5263 | 0.603 | 0.059 | 0.255 | 80.1106 | 0.55096 | 0.71625 | 1.0468 | 0.08724 | 5.5372 | 0.54178 | 0.08724 | Prysmian - 33kV SCWU 35M WST 0113
33 | 400 | Cu | 1 | XLPE | CWS |  | 670 | 38.2956 | 763.8 | 43.657 | 810.7 | 46.3377 | 600 | 34.2946 | 684 | 39.0959 | 726 | 41.4965 | 0.047 | 0.062 | 0.109 | 0.283 | 88.9071 | 1.6939 | 0.59 | 0.055 | 0.283 | 88.9071 | 0.43159 | 0.56933 | 1.0009 | 0.09682 | 5.4178 | 0.50505 | 0.09682 | Prysmian - 33kV SCWU 35M WST 0113
33 | 500 | Cu | 1 | XLPE | CWS |  | 760 | 43.4398 | 866.4 | 49.5214 | 919.6 | 52.5622 | 670 | 38.2956 | 763.8 | 43.657 | 810.7 | 46.3377 | 0.037 | 0.05 | 0.106 | 0.318 | 99.9026 | 1.9034 | 0.58 | 0.052 | 0.318 | 99.9026 | 0.33976 | 0.45914 | 0.97337 | 0.10879 | 5.326 | 0.4775 | 0.10879 | Prysmian - 33kV SCWU 35M WST 0113
33 | 630 | Cu | 1 | XLPE | CWS |  | 850 | 48.584 | 969 | 55.3858 | 1028.5 | 58.7867 | 750 | 42.8683 | 855 | 48.8698 | 907.5 | 51.8706 | 0.028 | 0.04 | 0.102 | 0.352 | 110.5841 | 2.1069 | 0.572 | 0.048 | 0.352 | 110.5841 | 0.25712 | 0.36731 | 0.93664 | 0.12043 | 5.2525 | 0.44077 | 0.12043 | Prysmian - 33kV SCWU 35M WST 0113
33 | 800 | Cu | 1 | XLPE | CWS |  | 940 | 53.7282 | 1071.6 | 61.2502 | 1137.4 | 65.0111 | 825 | 47.1551 | 940.5 | 53.7568 | 998.25 | 57.0577 | 0.022 | 0.034 | 0.098 | 0.39 | 122.5221 | 2.3344 | 0.566 | 0.045 | 0.39 | 122.5221 | 0.20202 | 0.31221 | 0.89991 | 0.13343 | 5.1974 | 0.41322 | 0.13343 | Prysmian - 33kV SCWU 35M WST 0113
33 | 1000 | Cu | 1 | XLPE | CWS |  | 1025 | 58.5866 | 1168.5 | 66.7887 | 1240.25 | 70.8898 | 890 | 50.8703 | 1014.6 | 57.9922 | 1076.9 | 61.5531 | 0.018 | 0.029 | 0.095 | 0.429 | 134.7743 | 2.5678 | 0.562 | 0.042 | 0.429 | 134.7743 | 0.16529 | 0.2663 | 0.87236 | 0.14677 | 5.1607 | 0.38567 | 0.14677 | Prysmian - 33kV SCWU 35M WST 0113
33kV 3c Oil Filled - Pb Sheath - Imperial
33 | 0.1 | Cu | 3 | Oil | Pb |  | 240 | 13.7178 | 273.6 | 15.6383 | 290.4 | 16.5986 | 200 | 11.4315 | 273.6 | 15.6383 | 242 | 13.8322 | 0.27558 | 0.3468 | 0.096272 | 0.37196 | 116.8547 | 2.2264 | 2.2383 | 0.13798 | 0.37196 | 116.8547 | 2.5306 | 3.1846 | 0.88404 | 0.12725 | 20.5536 | 1.267 | 0.12725 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.15 | Cu | 3 | Oil | Pb |  | 295 | 16.8615 | 336.3 | 19.2221 | 356.95 | 20.4024 | 250 | 14.2894 | 336.3 | 19.2221 | 302.5 | 17.2902 | 0.18828 | 0.2374 | 0.089708 | 0.4376 | 137.4761 | 2.6193 | 1.9726 | 0.12904 | 0.4376 | 137.4761 | 1.7289 | 2.18 | 0.82376 | 0.14971 | 18.1141 | 1.185 | 0.14971 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.2 | Cu | 3 | Oil | Pb |  | 340 | 19.4336 | 387.6 | 22.1543 | 411.4 | 23.5147 | 290 | 16.5757 | 387.6 | 22.1543 | 350.9 | 20.0566 | 0.14167 | 0.17942 | 0.084238 | 0.4923 | 154.6606 | 2.9467 | 1.6643 | 0.12292 | 0.4923 | 154.6606 | 1.3009 | 1.6475 | 0.77354 | 0.16843 | 15.2828 | 1.1288 | 0.16843 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.25 | Cu | 3 | Oil | Pb |  | 390 | 22.2915 | 444.6 | 25.4123 | 471.9 | 26.9727 | 330 | 18.862 | 444.6 | 25.4123 | 399.3 | 22.8231 | 0.11279 | 0.14331 | 0.083144 | 0.53606 | 168.4082 | 3.2086 | 1.5713 | 0.11899 | 0.53606 | 168.4082 | 1.0357 | 1.316 | 0.76349 | 0.1834 | 14.4287 | 1.0927 | 0.1834 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.3 | Cu | 3 | Oil | Pb |  | 430 | 24.5778 | 490.2 | 28.0187 | 520.3 | 29.7391 | 365 | 20.8626 | 490.2 | 28.0187 | 441.65 | 25.2437 | 0.091984 | 0.11706 | 0.079862 | 0.59076 | 185.5927 | 3.536 | 1.4804 | 0.11622 | 0.59076 | 185.5927 | 0.84466 | 1.0749 | 0.73335 | 0.20211 | 13.594 | 1.0672 | 0.20211 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.35 | Cu | 3 | Oil | Pb |  | 470 | 26.8641 | 535.8 | 30.6251 | 568.7 | 32.5056 | 405 | 23.1489 | 535.8 | 30.6251 | 490.05 | 28.0101 | 0.077783 | 0.099554 | 0.078768 | 0.62358 | 195.9034 | 3.7325 | 1.3723 | 0.11405 | 0.62358 | 195.9034 | 0.71426 | 0.91418 | 0.72331 | 0.21334 | 12.6017 | 1.0473 | 0.21334 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.4 | Cu | 3 | Oil | Pb |  | 495 | 28.293 | 564.3 | 32.2541 | 598.95 | 34.2346 | 435 | 24.8636 | 564.3 | 32.2541 | 526.35 | 30.0849 | 0.068441 | 0.088614 | 0.077674 | 0.66734 | 209.651 | 3.9944 | 1.2618 | 0.11203 | 0.66734 | 209.651 | 0.62847 | 0.81372 | 0.71326 | 0.22831 | 11.587 | 1.0287 | 0.22831 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.45 | Cu | 3 | Oil | Pb |  | 525 | 30.0078 | 598.5 | 34.2089 | 635.25 | 36.3094 | 460 | 26.2925 | 598.5 | 34.2089 | 556.6 | 31.814 | 0.061625 | 0.079862 | 0.07658 | 0.70016 | 219.9618 | 4.1908 | 1.2223 | 0.10972 | 0.70016 | 219.9618 | 0.56589 | 0.73335 | 0.70321 | 0.23954 | 11.2238 | 1.0075 | 0.23954 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.5 | Cu | 3 | Oil | Pb |  | 550 | 31.4367 | 627 | 35.8379 | 665.5 | 38.0384 | 480 | 27.4357 | 627 | 35.8379 | 580.8 | 33.1972 | 0.055805 | 0.073298 | 0.07658 | 0.73298 | 230.2725 | 4.3873 | 1.1736 | 0.10773 | 0.73298 | 230.2725 | 0.51244 | 0.67308 | 0.70321 | 0.25077 | 10.7769 | 0.98925 | 0.25077 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.55 | Cu | 3 | Oil | Pb |  | 575 | 32.8657 | 655.5 | 37.4669 | 695.75 | 39.7675 | 505 | 28.8646 | 655.5 | 37.4669 | 611.05 | 34.9262 | 0.051243 | 0.067828 | 0.075486 | 0.7658 | 240.5832 | 4.5837 | 1.1182 | 0.10597 | 0.7658 | 240.5832 | 0.47055 | 0.62285 | 0.69317 | 0.262 | 10.2684 | 0.9731 | 0.262 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33 | 0.6 | Cu | 3 | Oil | Pb |  | 600 | 34.2946 | 684 | 39.0959 | 726 | 41.4965 | 530 | 30.2936 | 684 | 39.0959 | 641.3 | 36.6552 | 0.045893 | 0.061264 | 0.074392 | 0.79862 | 250.8939 | 4.7802 | 1.0628 | 0.10421 | 0.79862 | 250.8939 | 0.42143 | 0.56257 | 0.68312 | 0.27322 | 9.7598 | 0.95696 | 0.27322 | BICC Pub448 Table 3 from ABB (Westinghouse) T&D
33kV 3c Gas Filled - Pb Sheath - Imperial
33 | 0.1 | Cu | 3 | Gas | Pb |  | 225 | 12.8605 | 256.5 | 14.6609 | 272.25 | 15.5612 | 190 | 10.86 | 217 | 12.4032 | 229.9 | 13.1405 | 0.27558 | 0.3423 | 0.088583 | 0.43745 | 137.4275 | 2.6183 | 1.787 | 0.158 | 0.43745 | 137.4275 | 2.5306 | 3.1433 | 0.81343 | 0.14966 | 16.4096 | 1.4509 | 0.14966 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.15 | Cu | 3 | Gas | Pb |  | 280 | 16.0041 | 319.2 | 18.2447 | 338.8 | 19.365 | 240 | 13.7178 | 274 | 15.6612 | 290.4 | 16.5986 | 0.18828 | 0.23294 | 0.083115 | 0.514 | 161.4773 | 3.0766 | 1.513 | 0.149 | 0.514 | 161.4773 | 1.7289 | 2.139 | 0.76322 | 0.17585 | 13.8935 | 1.3682 | 0.17585 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.2 | Cu | 3 | Gas | Pb |  | 330 | 18.862 | 376.2 | 21.5027 | 399.3 | 22.8231 | 280 | 16.0041 | 319 | 18.2333 | 338.8 | 19.365 | 0.14167 | 0.17717 | 0.080927 | 0.57962 | 182.0914 | 3.4693 | 1.344 | 0.143 | 0.57962 | 182.0914 | 1.3009 | 1.6269 | 0.74313 | 0.1983 | 12.3416 | 1.3131 | 0.1983 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.25 | Cu | 3 | Gas | Pb |  | 375 | 21.4341 | 427.5 | 24.4349 | 453.75 | 25.9353 | 320 | 18.2905 | 365 | 20.8626 | 387.2 | 22.1315 | 0.11279 | 0.14217 | 0.077647 | 0.68898 | 216.4483 | 4.1239 | 1.227 | 0.138 | 0.68898 | 216.4483 | 1.0357 | 1.3055 | 0.71301 | 0.23571 | 11.2672 | 1.2672 | 0.23571 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.3 | Cu | 3 | Gas | Pb |  | 420 | 24.0062 | 478.8 | 27.3671 | 508.2 | 29.0475 | 360 | 20.5768 | 410 | 23.4346 | 435.6 | 24.8979 | 0.091984 | 0.11702 | 0.076553 | 0.75459 | 237.0624 | 4.5166 | 1.138 | 0.135 | 0.75459 | 237.0624 | 0.84466 | 1.0745 | 0.70297 | 0.25816 | 10.45 | 1.2397 | 0.25816 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.35 | Cu | 3 | Gas | Pb |  | 450 | 25.721 | 513 | 29.3219 | 544.5 | 31.1224 | 385 | 22.0057 | 439 | 25.0922 | 465.85 | 26.6269 | 0.077783 | 0.102 | 0.075 | 0.799 | 251.0133 | 4.7824 | 1.068 | 0.132 | 0.799 | 251.0133 | 0.71426 | 0.93664 | 0.68871 | 0.27335 | 9.8072 | 1.2121 | 0.27335 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.4 | Cu | 3 | Gas | Pb |  | 495 | 28.293 | 564.3 | 32.2541 | 598.95 | 34.2346 | 420 | 24.0062 | 479 | 27.3785 | 508.2 | 29.0475 | 0.068441 | 0.088145 | 0.073272 | 0.86395 | 271.4193 | 5.1712 | 1.011 | 0.129 | 0.86395 | 271.4193 | 0.62847 | 0.80941 | 0.67284 | 0.29558 | 9.2837 | 1.1846 | 0.29558 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.45 | Cu | 3 | Gas | Pb |  | 520 | 29.722 | 592.8 | 33.8831 | 629.2 | 35.9636 | 440 | 25.1494 | 502 | 28.6932 | 532.4 | 30.4307 | 0.061625 | 0.08 | 0.073 | 0.906 | 284.6283 | 5.4229 | 0.963 | 0.127 | 0.906 | 284.6283 | 0.56589 | 0.73462 | 0.67034 | 0.30996 | 8.843 | 1.1662 | 0.30996 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.5 | Cu | 3 | Gas | Pb |  | 550 | 31.4367 | 627 | 35.8379 | 665.5 | 38.0384 | 470 | 26.8641 | 536 | 30.6365 | 568.7 | 32.5056 | 0.055805 | 0.073053 | 0.072178 | 0.95144 | 298.9048 | 5.6949 | 0.922 | 0.125 | 0.95144 | 298.9048 | 0.51244 | 0.67083 | 0.6628 | 0.32551 | 8.4665 | 1.1478 | 0.32551 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.55 | Cu | 3 | Gas | Pb |  | 575 | 32.8657 | 655.5 | 37.4669 | 695.75 | 39.7675 | 490 | 28.0073 | 559 | 31.9511 | 592.9 | 33.8888 | 0.051243 | 0.066 | 0.071 | 1.001 | 314.4734 | 5.9915 | 0.887 | 0.123 | 1.001 | 314.4734 | 0.47055 | 0.60606 | 0.65197 | 0.34246 | 8.1451 | 1.1295 | 0.34246 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33 | 0.6 | Cu | 3 | Gas | Pb |  | 590 | 33.723 | 672.6 | 38.4443 | 713.9 | 40.8049 | 500 | 28.5788 | 570 | 32.5799 | 605 | 34.5804 | 0.045893 | 0.06157 | 0.071 | 1.0389 | 326.3903 | 6.2186 | 0.856 | 0.121 | 1.0389 | 326.3903 | 0.42143 | 0.56539 | 0.65197 | 0.35544 | 7.8604 | 1.1111 | 0.35544 | BICC 1948 Table 57. ABB Westinghouse for R0X0
33kV 3c PILC - Imperial
33 | 0.1 | Cu | 3 | Paper | Pb |  | 205 | 11.7173 | 233.7 | 13.3577 | 248.05 | 14.178 | 145 | 8.2879 | 572.3 | 32.7113 | 175.45 | 10.0283 | 0.27558 | 0.31824 | 0.15748 | 0.21872 | 68.7138 | 1.3092 | 1.421 | 0.16599 | 0.21872 | 68.7138 | 2.5306 | 2.9223 | 1.4461 | 0.074829 | 13.0487 | 1.5242 | 0.074829 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.15 | Cu | 3 | Paper | Pb |  | 255 | 14.5752 | 290.7 | 16.6157 | 308.55 | 17.636 | 175 | 10.0026 | 573.3 | 32.7685 | 211.75 | 12.1031 | 0.18828 | 0.21763 | 0.11374 | 0.26247 | 82.4565 | 1.571 | 1.242 | 0.15512 | 0.26247 | 82.4565 | 1.7289 | 1.9984 | 1.0444 | 0.089795 | 11.4053 | 1.4244 | 0.089795 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.2 | Cu | 3 | Paper | Pb |  | 295 | 16.8615 | 336.3 | 19.2221 | 356.95 | 20.4024 | 205 | 11.7173 | 574.3 | 32.8257 | 248.05 | 14.178 | 0.14167 | 0.16404 | 0.10936 | 0.29528 | 92.7636 | 1.7674 | 1.1289 | 0.14784 | 0.29528 | 92.7636 | 1.3009 | 1.5064 | 1.0042 | 0.10102 | 10.3663 | 1.3576 | 0.10102 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.25 | Cu | 3 | Paper | Pb |  | 335 | 19.1478 | 381.9 | 21.8285 | 405.35 | 23.1689 | 230 | 13.1463 | 575.3 | 32.8828 | 278.3 | 15.907 | 0.11279 | 0.13123 | 0.10389 | 0.32808 | 103.0706 | 1.9638 | 1.0483 | 0.14244 | 0.32808 | 103.0706 | 1.0357 | 1.2051 | 0.95402 | 0.11224 | 9.6261 | 1.308 | 0.11224 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.3 | Cu | 3 | Paper | Pb |  | 370 | 21.1483 | 421.8 | 24.1091 | 447.7 | 25.5895 | 255 | 14.5752 | 576.3 | 32.94 | 308.55 | 17.636 | 0.091984 | 0.10805 | 0.10061 | 0.36089 | 113.3777 | 2.1601 | 0.98671 | 0.13817 | 0.36089 | 113.3777 | 0.84466 | 0.99219 | 0.9239 | 0.12347 | 9.0607 | 1.2687 | 0.12347 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.35 | Cu | 3 | Paper | Pb |  | 400 | 22.8631 | 456 | 26.0639 | 484 | 27.6643 | 275 | 15.7184 | 577.3 | 32.9971 | 332.75 | 19.0192 | 0.077783 | 0.094 | 0.098 | 0.38 | 119.3805 | 2.2745 | 0.93749 | 0.13465 | 0.38 | 119.3805 | 0.71426 | 0.86318 | 0.89991 | 0.13001 | 8.6087 | 1.2365 | 0.13001 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.4 | Cu | 3 | Paper | Pb |  | 435 | 24.8636 | 495.9 | 28.3445 | 526.35 | 30.0849 | 300 | 17.1473 | 578.3 | 33.0543 | 363 | 20.7482 | 0.068441 | 0.081584 | 0.096238 | 0.40464 | 127.1204 | 2.422 | 0.89683 | 0.13168 | 0.40464 | 127.1204 | 0.62847 | 0.74916 | 0.88373 | 0.13843 | 8.2354 | 1.2092 | 0.13843 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.45 | Cu | 3 | Paper | Pb |  | 450 | 25.721 | 513 | 29.3219 | 544.5 | 31.1224 | 310 | 17.7189 | 579.3 | 33.1114 | 375.1 | 21.4398 | 0.061625 | 0.074 | 0.094 | 0.424 | 133.2035 | 2.5379 | 0.86244 | 0.12912 | 0.424 | 133.2035 | 0.56589 | 0.67952 | 0.86318 | 0.14506 | 7.9196 | 1.1857 | 0.14506 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.5 | Cu | 3 | Paper | Pb |  | 480 | 27.4357 | 547.2 | 31.2767 | 580.8 | 33.1972 | 335 | 19.1478 | 580.3 | 33.1686 | 405.35 | 23.1689 | 0.055805 | 0.067585 | 0.092957 | 0.43745 | 137.4275 | 2.6183 | 0.83279 | 0.12687 | 0.43745 | 137.4275 | 0.51244 | 0.62062 | 0.8536 | 0.14966 | 7.6473 | 1.165 | 0.14966 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.55 | Cu | 3 | Paper | Pb |  | 505 | 28.8646 | 575.7 | 32.9057 | 611.05 | 34.9262 | 350 | 20.0052 | 581.3 | 33.2258 | 423.5 | 24.2063 | 0.051243 | 0.061 | 0.087 | 0.463 | 145.4557 | 2.7713 | 0.80685 | 0.12486 | 0.463 | 145.4557 | 0.47055 | 0.56015 | 0.7989 | 0.1584 | 7.4091 | 1.1466 | 0.1584 | BICC 1948 Table 18. ABB Westinghouse for R0X0
33 | 0.6 | Cu | 3 | Paper | Pb |  | 530 | 30.2936 | 604.2 | 34.5347 | 641.3 | 36.6552 | 365 | 20.8626 | 582.3 | 33.2829 | 441.65 | 25.2437 | 0.045893 | 0.056 | 0.083497 | 0.48 | 150.7964 | 2.8731 | 0.78388 | 0.12306 | 0.48 | 150.7964 | 0.42143 | 0.51423 | 0.76673 | 0.16422 | 7.1982 | 1.1301 | 0.16422 | BICC 1948 Table 18. ABB Westinghouse for R0X0

## 66kV
66kV Underground cable ratings and parameters datasheet (IMP/001/013)
Version: | 1.2
| Conductors |  |  | Construction |  |  | Current Rating (Laid Direct) | [5 empty] | Current Rating (Ducted) | [5 empty] | Positive & Negative Sequence (Ohmic) | [5 empty] | Zero Sequence (Ohmic) |  |  |  | Positive & Negative Sequence (100MVA Base) |  |  |  | Zero Sequence (100MVA Base)
Voltage (kV) | mm2/in2 | Material | No. | Insulation | Sheath | Protection | Continuous |  | Cyclic |  | Emergency |  | Continuous |  | Cyclic |  | Emergency |  | DC Resistance Ω/km (20°C) | AC Resistance at max insulator temp Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | Charging Current A/km | Resistance Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | DC Resistance %/km (20°C) | AC Resistance at max insulator temp %/km | Reactance %/km | Susceptance %/km | Resistance %/km | Reactance %/km | Susceptance %/km
U | [6 empty] | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Rdc | R1=R2 | X1=X2 | C1=C2 | B1=B2 | IC | R0 | X0 | C0 | B0 | Rdc | R1=R2 | X1=X2 | B1=B2 | R0 | X0 | B0 | Source
66kV 1c Trefoil XLPE Al - Pb Sheath - Metric
66 | 300 | Al | 1 | XLPE | Pb |  | 460 | 52.5851 | 524.4 | 59.947 | 556.6 | 63.6279 | 435 | 49.7272 | 495.9 | 56.689 | 526.35 | 60.1699 | 0.1 | 0.128 | 0.133 | 0.19 | 59.6903 | 2.2745 | 0.375 | 0.087 | 0.19 | 59.6903 | 0.22957 | 0.29385 | 0.30533 | 0.26001 | 0.86088 | 0.19972 | 0.26001 | BICC 1991 + CBI electric for R0 X0
66 | 400 | Al | 1 | XLPE | Pb |  | 525 | 60.0156 | 598.5 | 68.4177 | 635.25 | 72.6188 | 488 | 55.7859 | 556.32 | 63.5959 | 590.48 | 67.5009 | 0.0778 | 0.1 | 0.128 | 0.205 | 64.4026 | 2.4541 | 0.3528 | 0.063 | 0.205 | 64.4026 | 0.1786 | 0.22957 | 0.29385 | 0.28054 | 0.80992 | 0.14463 | 0.28054 | BICC 1991 + CBI electric for R0 X0
66 | 500 | Al | 1 | XLPE | Pb |  | 590 | 67.4461 | 672.6 | 76.8885 | 713.9 | 81.6097 | 545 | 62.3019 | 621.3 | 71.0241 | 659.45 | 75.3853 | 0.0605 | 0.079 | 0.123 | 0.225 | 70.6858 | 2.6935 | 0.3355 | 0.059 | 0.225 | 70.6858 | 0.13889 | 0.18136 | 0.28237 | 0.30791 | 0.7702 | 0.13545 | 0.30791 | BICC 1991 + CBI electric for R0 X0
66 | 630 | Al | 1 | XLPE | Pb |  | 670 | 76.5913 | 763.8 | 87.3141 | 810.7 | 92.6755 | 609 | 69.6181 | 694.26 | 79.3646 | 736.89 | 84.2378 | 0.0469 | 0.062 | 0.118 | 0.25 | 78.5398 | 2.9928 | 0.3219 | 0.054 | 0.25 | 78.5398 | 0.10767 | 0.14233 | 0.27089 | 0.34212 | 0.73898 | 0.12397 | 0.34212 | BICC 1991 + CBI electric for R0 X0
66 | 800 | Al | 1 | XLPE | Pb |  | 755 | 86.3081 | 860.7 | 98.3912 | 913.55 | 104.4328 | 675 | 77.1629 | 769.5 | 87.9657 | 816.75 | 93.3671 | 0.0367 | 0.05 | 0.114 | 0.27 | 84.823 | 3.2322 | 0.3117 | 0.065 | 0.27 | 84.823 | 0.084252 | 0.11478 | 0.26171 | 0.36949 | 0.71556 | 0.14922 | 0.36949 | BICC 1991 + CBI electric for R0 X0
66 | 1000 | Al | 1 | XLPE | Pb |  | 830 | 94.8817 | 946.2 | 108.1652 | 1004.3 | 114.8069 | 737 | 84.2504 | 840.18 | 96.0455 | 891.77 | 101.943 | 0.0291 | 0.041 | 0.11 | 0.295 | 92.677 | 3.5315 | 0.3041 | 0.061 | 0.295 | 92.677 | 0.066804 | 0.094123 | 0.25253 | 0.4037 | 0.69812 | 0.14004 | 0.4037 | BICC 1991 + CBI electric for R0 X0
66kV 1c Trefoil XLPE Cu - Pb Sheath - Metric
66 | 300 | Cu | 1 | XLPE | Pb |  | 585 | 66.8745 | 666.9 | 76.2369 | 707.85 | 80.9181 | 531 | 60.7015 | 605.34 | 69.1997 | 642.51 | 73.4488 | 0.0601 | 0.078 | 0.133 | 0.19 | 59.6903 | 2.2745 | 0.3351 | 0.087 | 0.19 | 59.6903 | 0.13797 | 0.17906 | 0.30533 | 0.26001 | 0.76928 | 0.19972 | 0.26001 | BICC 1991 + CBI electric for R0 X0
66 | 400 | Cu | 1 | XLPE | Pb |  | 660 | 75.4481 | 752.4 | 86.0109 | 798.6 | 91.2922 | 587 | 67.1031 | 669.18 | 76.4975 | 710.27 | 81.1948 | 0.047 | 0.062 | 0.128 | 0.205 | 64.4026 | 2.4541 | 0.322 | 0.063 | 0.205 | 64.4026 | 0.1079 | 0.14233 | 0.29385 | 0.28054 | 0.73921 | 0.14463 | 0.28054 | BICC 1991 + CBI electric for R0 X0
66 | 500 | Cu | 1 | XLPE | Pb |  | 740 | 84.5934 | 843.6 | 96.4364 | 895.4 | 102.358 | 649 | 74.1907 | 739.86 | 84.5774 | 785.29 | 89.7707 | 0.0366 | 0.049 | 0.123 | 0.225 | 70.6858 | 2.6935 | 0.3116 | 0.059 | 0.225 | 70.6858 | 0.084022 | 0.11249 | 0.28237 | 0.30791 | 0.71534 | 0.13545 | 0.30791 | BICC 1991 + CBI electric for R0 X0
66 | 630 | Cu | 1 | XLPE | Pb |  | 830 | 94.8817 | 946.2 | 108.1652 | 1004.3 | 114.8069 | 714 | 81.6212 | 813.96 | 93.0481 | 863.94 | 98.7616 | 0.0283 | 0.04 | 0.118 | 0.25 | 78.5398 | 2.9928 | 0.3033 | 0.054 | 0.25 | 78.5398 | 0.064968 | 0.091827 | 0.27089 | 0.34212 | 0.69628 | 0.12397 | 0.34212 | BICC 1991 + CBI electric for R0 X0
66 | 800 | Cu | 1 | XLPE | Pb |  | 910 | 104.027 | 1037.4 | 118.5907 | 1101.1 | 125.8726 | 781 | 89.2803 | 890.34 | 101.7795 | 945.01 | 108.0292 | 0.0221 | 0.033 | 0.114 | 0.27 | 84.823 | 3.2322 | 0.2971 | 0.065 | 0.27 | 84.823 | 0.050735 | 0.075758 | 0.26171 | 0.36949 | 0.68205 | 0.14922 | 0.36949 | BICC 1991 + CBI electric for R0 X0
66 | 1000 | Cu | 1 | XLPE | Pb |  | 990 | 113.1722 | 1128.6 | 129.0163 | 1197.9 | 136.9384 | 839 | 95.9106 | 956.46 | 109.3381 | 1015.19 | 116.0518 | 0.0176 | 0.028 | 0.11 | 0.295 | 92.677 | 3.5315 | 0.2926 | 0.061 | 0.295 | 92.677 | 0.040404 | 0.064279 | 0.25253 | 0.4037 | 0.67172 | 0.14004 | 0.4037 | BICC 1991 + CBI electric for R0 X0
66kV 3c Oil Filled Cu - Pb Sheath - Imperial
66 | 0.1 | Cu | 3 | Oil | Pb |  | 240 | 27.4357 | 273.6 | 31.2767 | 290.4 | 33.1972 | 210 | 24.0062 | 239.4 | 27.3671 | 254.1 | 29.0475 | 0.27558 | 0.3468 | 0.11596 | 0.26256 | 82.4857 | 3.1726 | 1.5864 | 0.1517 | 0.26256 | 82.4857 | 0.63264 | 0.79614 | 0.26622 | 0.35931 | 3.6419 | 0.34826 | 0.35931 | BICC and Westinghouse for R0X0
66 | 0.15 | Cu | 3 | Oil | Pb |  | 295 | 33.723 | 336.3 | 38.4443 | 356.95 | 40.8049 | 260 | 29.722 | 296.4 | 33.8831 | 314.6 | 35.9636 | 0.18828 | 0.2374 | 0.10612 | 0.31726 | 99.6702 | 3.829 | 1.3593 | 0.14333 | 0.31726 | 99.6702 | 0.43223 | 0.54499 | 0.24361 | 0.43416 | 3.1206 | 0.32905 | 0.43416 | BICC and Westinghouse for R0X0
66 | 0.2 | Cu | 3 | Oil | Pb |  | 345 | 39.4388 | 393.3 | 44.9602 | 417.45 | 47.7209 | 300 | 34.2946 | 342 | 39.0959 | 363 | 41.4965 | 0.14167 | 0.17832 | 0.10174 | 0.36102 | 113.4178 | 4.376 | 1.2182 | 0.13767 | 0.36102 | 113.4178 | 0.32524 | 0.40937 | 0.23357 | 0.49405 | 2.7966 | 0.31606 | 0.49405 | BICC and Westinghouse for R0X0
66 | 0.25 | Cu | 3 | Oil | Pb |  | 390 | 44.583 | 444.6 | 50.8246 | 471.9 | 53.9454 | 340 | 38.8672 | 387.6 | 44.3086 | 411.4 | 47.0293 | 0.11279 | 0.14222 | 0.097366 | 0.40478 | 127.1654 | 4.8136 | 1.1189 | 0.13344 | 0.40478 | 127.1654 | 0.25893 | 0.32649 | 0.22352 | 0.55393 | 2.5687 | 0.30634 | 0.55393 | BICC and Westinghouse for R0X0
66 | 0.3 | Cu | 3 | Oil | Pb |  | 435 | 49.7272 | 495.9 | 56.689 | 526.35 | 60.1699 | 375 | 42.8683 | 427.5 | 48.8698 | 453.75 | 51.8706 | 0.091984 | 0.11706 | 0.094084 | 0.4376 | 137.4761 | 5.2512 | 1.0438 | 0.13008 | 0.4376 | 137.4761 | 0.21117 | 0.26873 | 0.21599 | 0.59885 | 2.3963 | 0.29862 | 0.59885 | BICC and Westinghouse for R0X0
66 | 0.35 | Cu | 3 | Oil | Pb |  | 475 | 54.2998 | 541.5 | 61.9018 | 574.75 | 65.7027 | 415 | 47.4409 | 473.1 | 54.0826 | 502.15 | 57.4035 | 0.077783 | 0.099554 | 0.091896 | 0.48136 | 151.2237 | 5.7982 | 0.98429 | 0.1273 | 0.48136 | 151.2237 | 0.17857 | 0.22854 | 0.21096 | 0.65873 | 2.2596 | 0.29224 | 0.65873 | BICC and Westinghouse for R0X0
66 | 0.4 | Cu | 3 | Oil | Pb |  | 505 | 57.7293 | 575.7 | 65.8113 | 611.05 | 69.8524 | 445 | 50.8703 | 507.3 | 57.9922 | 538.45 | 61.5531 | 0.068441 | 0.08752 | 0.088614 | 0.52512 | 164.9713 | 6.2358 | 0.93546 | 0.12494 | 0.52512 | 164.9713 | 0.15712 | 0.20092 | 0.20343 | 0.71862 | 2.1475 | 0.28683 | 0.71862 | BICC and Westinghouse for R0X0
66 | 0.45 | Cu | 3 | Oil | Pb |  | 535 | 61.1587 | 609.9 | 69.7209 | 647.35 | 74.002 | 470 | 53.7282 | 535.8 | 61.2502 | 568.7 | 65.0111 | 0.061625 | 0.079862 | 0.08752 | 0.547 | 171.8451 | 0.6564 | 0.89441 | 0.1229 | 0.547 | 171.8451 | 0.14147 | 0.18334 | 0.20092 | 0.74856 | 2.0533 | 0.28214 | 0.74856 | BICC and Westinghouse for R0X0
66 | 0.5 | Cu | 3 | Oil | Pb |  | 565 | 64.5882 | 644.1 | 73.6305 | 683.65 | 78.1517 | 495 | 56.5861 | 564.3 | 64.5082 | 598.95 | 68.4692 | 0.055805 | 0.072204 | 0.086426 | 0.56888 | 178.7189 | 6.7828 | 0.85922 | 0.1211 | 0.56888 | 178.7189 | 0.12811 | 0.16576 | 0.19841 | 0.7785 | 1.9725 | 0.27801 | 0.7785 | BICC and Westinghouse for R0X0
66 | 0.55 | Cu | 3 | Oil | Pb |  | 585 | 66.8745 | 666.9 | 76.2369 | 707.85 | 80.9181 | 515 | 58.8724 | 587.1 | 67.1145 | 623.15 | 71.2356 | 0.051243 | 0.067828 | 0.085332 | 0.6017 | 189.0296 | 7.2204 | 0.82858 | 0.11949 | 0.6017 | 189.0296 | 0.11764 | 0.15571 | 0.1959 | 0.82341 | 1.9022 | 0.27432 | 0.82341 | BICC and Westinghouse for R0X0
66 | 0.6 | Cu | 3 | Oil | Pb |  | 620 | 70.8755 | 706.8 | 80.7981 | 750.2 | 85.7594 | 540 | 61.7303 | 615.6 | 70.3725 | 653.4 | 74.6937 | 0.045893 | 0.061264 | 0.084238 | 0.63452 | 199.3403 | 7.5486 | 0.80156 | 0.11805 | 0.63452 | 199.3403 | 0.10536 | 0.14064 | 0.19338 | 0.86833 | 1.8401 | 0.271 | 0.86833 | BICC and Westinghouse for R0X0
66kV 1c Trefoil Oil Filled Cu - Pb Sheath - Imperial
66 | 0.1 | Cu | 1 | Oil | Pb |  | 250 | 28.5788 | 285 | 32.5799 | 302.5 | 34.5804 | 245 | 28.0073 | 279.3 | 31.9283 | 296.45 | 33.8888 | 0.26869 | 0.33914 | 0.11378 | 0.44854 | 140.913 | 5.3606 | 1.0725 | 0.061863 | 0.44854 | 140.913 | 0.61682 | 0.77856 | 0.26119 | 0.61382 | 2.4621 | 0.14202 | 0.61382 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.15 | Cu | 1 | Oil | Pb |  | 310 | 35.4378 | 353.4 | 40.399 | 375.1 | 42.8797 | 295 | 33.723 | 336.3 | 38.4443 | 356.95 | 40.8049 | 0.18106 | 0.22755 | 0.11049 | 0.48136 | 151.2237 | 5.7982 | 0.92233 | 0.059116 | 0.48136 | 151.2237 | 0.41565 | 0.52239 | 0.25366 | 0.65873 | 2.1174 | 0.13571 | 0.65873 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.2 | Cu | 1 | Oil | Pb |  | 355 | 40.582 | 404.7 | 46.2634 | 429.55 | 49.1042 | 340 | 38.8672 | 387.6 | 44.3086 | 411.4 | 47.0293 | 0.13686 | 0.17285 | 0.10721 | 0.52512 | 164.9713 | 6.2358 | 0.82872 | 0.057242 | 0.52512 | 164.9713 | 0.31419 | 0.39681 | 0.24612 | 0.71862 | 1.9025 | 0.13141 | 0.71862 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.25 | Cu | 1 | Oil | Pb |  | 400 | 45.7261 | 456 | 52.1278 | 484 | 55.3286 | 380 | 43.4398 | 433.2 | 49.5214 | 459.8 | 52.5622 | 0.11006 | 0.13784 | 0.1094 | 0.4923 | 154.6606 | 5.9076 | 0.76271 | 0.055829 | 0.4923 | 154.6606 | 0.25265 | 0.31645 | 0.25115 | 0.6737 | 1.7509 | 0.12817 | 0.6737 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.3 | Cu | 1 | Oil | Pb |  | 445 | 50.8703 | 507.3 | 57.9922 | 538.45 | 61.5531 | 415 | 47.4409 | 473.1 | 54.0826 | 502.15 | 57.4035 | 0.09031 | 0.11378 | 0.10721 | 0.51418 | 161.5344 | 6.1264 | 0.7127 | 0.0547 | 0.51418 | 161.5344 | 0.20732 | 0.26119 | 0.24612 | 0.70364 | 1.6361 | 0.12557 | 0.70364 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.35 | Cu | 1 | Oil | Pb |  | 480 | 54.8714 | 547.2 | 62.5534 | 580.8 | 66.3944 | 445 | 50.8703 | 507.3 | 57.9922 | 538.45 | 61.5531 | 0.077597 | 0.09846 | 0.10502 | 0.547 | 171.8451 | 6.564 | 0.67298 | 0.053764 | 0.547 | 171.8451 | 0.17814 | 0.22603 | 0.2411 | 0.74856 | 1.5449 | 0.12343 | 0.74856 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.4 | Cu | 1 | Oil | Pb |  | 510 | 58.3008 | 581.4 | 66.4629 | 617.1 | 70.544 | 475 | 54.2998 | 541.5 | 61.9018 | 574.75 | 65.7027 | 0.067336 | 0.085332 | 0.10284 | 0.57982 | 182.1558 | 6.8922 | 0.64036 | 0.052966 | 0.57982 | 182.1558 | 0.15458 | 0.1959 | 0.23608 | 0.79347 | 1.4701 | 0.12159 | 0.79347 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.45 | Cu | 1 | Oil | Pb |  | 540 | 61.7303 | 615.6 | 70.3725 | 653.4 | 74.6937 | 500 | 57.1577 | 570 | 65.1598 | 605 | 69.1608 | 0.060629 | 0.077674 | 0.10174 | 0.6017 | 189.0296 | 7.2204 | 0.61291 | 0.052272 | 0.6017 | 189.0296 | 0.13919 | 0.17831 | 0.23357 | 0.82341 | 1.4071 | 0.12 | 0.82341 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.5 | Cu | 1 | Oil | Pb |  | 565 | 64.5882 | 644.1 | 73.6305 | 683.65 | 78.1517 | 520 | 59.444 | 592.8 | 67.7661 | 629.2 | 71.9272 | 0.054766 | 0.070016 | 0.10174 | 0.62358 | 195.9034 | 7.4392 | 0.58935 | 0.051659 | 0.62358 | 195.9034 | 0.12572 | 0.16073 | 0.23357 | 0.85336 | 1.353 | 0.11859 | 0.85336 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.55 | Cu | 1 | Oil | Pb |  | 595 | 68.0176 | 678.3 | 77.5401 | 719.95 | 82.3013 | 550 | 62.8734 | 627 | 71.6757 | 665.5 | 76.0769 | 0.048847 | 0.062358 | 0.099554 | 0.64546 | 202.7772 | 7.7674 | 0.56882 | 0.05111 | 0.64546 | 202.7772 | 0.11214 | 0.14315 | 0.22854 | 0.8833 | 1.3058 | 0.11733 | 0.8833 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.6 | Cu | 1 | Oil | Pb |  | 620 | 70.8755 | 706.8 | 80.7981 | 750.2 | 85.7594 | 565 | 64.5882 | 644.1 | 73.6305 | 683.65 | 78.1517 | 0.045237 | 0.059076 | 0.09846 | 0.66734 | 209.651 | 7.9862 | 0.55071 | 0.050615 | 0.66734 | 209.651 | 0.10385 | 0.13562 | 0.22603 | 0.91324 | 1.2642 | 0.11619 | 0.91324 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.65 | Cu | 1 | Oil | Pb |  | 640 | 73.1618 | 729.6 | 83.4045 | 774.4 | 88.5258 | 585 | 66.8745 | 666.9 | 76.2369 | 707.85 | 80.9181 | 0.042064 | 0.0547 | 0.09846 | 0.68922 | 216.5248 | 8.205 | 0.53455 | 0.050163 | 0.68922 | 216.5248 | 0.096566 | 0.12557 | 0.22603 | 0.94318 | 1.2272 | 0.11516 | 0.94318 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.75 | Cu | 1 | Oil | Pb |  | 680 | 77.7344 | 775.2 | 88.6173 | 822.8 | 94.0587 | 620 | 70.8755 | 706.8 | 80.7981 | 750.2 | 85.7594 | 0.036594 | 0.048136 | 0.096272 | 0.73298 | 230.2725 | 8.752 | 0.50684 | 0.049365 | 0.73298 | 230.2725 | 0.084009 | 0.11051 | 0.22101 | 1.0031 | 1.1635 | 0.11333 | 1.0031 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 0.85 | Cu | 1 | Oil | Pb |  | 715 | 81.7355 | 815.1 | 93.1784 | 865.15 | 98.8999 | 650 | 74.305 | 741 | 84.7077 | 786.5 | 89.909 | 0.031978 | 0.042666 | 0.095178 | 0.77674 | 244.0201 | 9.299 | 0.48378 | 0.048678 | 0.77674 | 244.0201 | 0.073411 | 0.097948 | 0.2185 | 1.063 | 1.1106 | 0.11175 | 1.063 | BICC Pub 448 (R0X0 sheath from Westinghouse )
66 | 1 | Cu | 1 | Oil | Pb |  | 775 | 88.5944 | 883.5 | 100.9976 | 937.75 | 107.1992 | 690 | 78.8776 | 786.6 | 89.9205 | 834.9 | 95.4419 | 0.025972 | 0.036102 | 0.091896 | 0.84238 | 264.6415 | 10.0648 | 0.4554 | 0.0478 | 0.84238 | 264.6415 | 0.059622 | 0.082879 | 0.21096 | 1.1528 | 1.0455 | 0.10973 | 1.1528 | BICC Pub 448 (R0X0 sheath from Westinghouse )

## 132kV
132kV Underground cable ratings and parameters datasheet (IMP/001/013)
Version: | 1.2
| Conductors |  |  | Construction |  |  | Current Rating (Laid Direct) | [5 empty] | Current Rating (Ducted) | [5 empty] | Positive & Negative Sequence (Ohmic) | [5 empty] | Zero Sequence (Ohmic) |  |  |  | Positive & Negative Sequence (100MVA Base) |  |  |  | Zero Sequence (100MVA Base)
Voltage (kV) | mm2/in2 | Material | No. | Insulation | Sheath | Protection | Continuous |  | Cyclic |  | Emergency |  | Continuous |  | Cyclic |  | Emergency |  | DC Resistance Ω/km (20°C) | AC Resistance at max insulator temp Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | Charging Current A/km | Resistance Ω/km | Reactance Ω/km | Capacitance µF/km | Susceptance µS | DC Resistance %/km (20°C) | AC Resistance at max insulator temp %/km | Reactance %/km | Susceptance %/km | Resistance %/km | Reactance %/km | Susceptance %/km
U | [6 empty] | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Amps | MVA | Rdc | R1=R2 | X1=X2 | C1=C2 | B1=B2 | IC | R0 | X0 | C0 | B0 | Rdc | R1=R2 | X1=X2 | B1=B2 | R0 | X0 | B0 | Source
132kV 1c Trefoil XLPE Al - Pb Sheath - Metric
132 | 300 | Al | 1 | XLPE | Pb |  | 455 | 104.027 | 518.7 | 118.5907 | 550.55 | 125.8726 | 405 | 92.5954 | 461.7 | 105.5588 | 490.05 | 112.0405 | 0.1 | 0.128 | 0.153 | 0.13 | 40.8407 | 3.1125 | 0.375 | 0.0969 | 0.13 | 40.8407 | 0.057392 | 0.073462 | 0.08781 | 0.71161 | 0.21522 | 0.055613 | 0.71161 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 400 | Al | 1 | XLPE | Pb |  | 515 | 117.7448 | 587.1 | 134.2291 | 623.15 | 142.4712 | 450 | 102.8838 | 513 | 117.2876 | 544.5 | 124.4894 | 0.0778 | 0.1 | 0.146 | 0.14 | 43.9823 | 3.3519 | 0.3528 | 0.0877 | 0.14 | 43.9823 | 0.044651 | 0.057392 | 0.083792 | 0.76635 | 0.20248 | 0.050333 | 0.76635 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 500 | Al | 1 | XLPE | Pb |  | 580 | 132.6058 | 661.2 | 151.1706 | 701.8 | 160.453 | 496 | 113.4008 | 565.44 | 129.2769 | 600.16 | 137.215 | 0.0605 | 0.079 | 0.138 | 0.16 | 50.2655 | 3.8307 | 0.3355 | 0.0831 | 0.16 | 50.2655 | 0.034722 | 0.04534 | 0.079201 | 0.87583 | 0.19255 | 0.047693 | 0.87583 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 630 | Al | 1 | XLPE | Pb |  | 655 | 149.7531 | 746.7 | 170.7185 | 792.55 | 181.2013 | 545 | 124.6037 | 621.3 | 142.0483 | 659.45 | 150.7705 | 0.0469 | 0.062 | 0.133 | 0.17 | 53.4071 | 4.0702 | 0.3219 | 0.0788 | 0.17 | 53.4071 | 0.026917 | 0.035583 | 0.076331 | 0.93056 | 0.18475 | 0.045225 | 0.93056 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 800 | Al | 1 | XLPE | Pb |  | 735 | 168.0436 | 837.9 | 191.5697 | 889.35 | 203.3327 | 592 | 135.3494 | 674.88 | 154.2983 | 716.32 | 163.7727 | 0.0367 | 0.049 | 0.126 | 0.195 | 61.2611 | 4.6687 | 0.3117 | 0.074 | 0.195 | 61.2611 | 0.021063 | 0.028122 | 0.072314 | 1.0674 | 0.17889 | 0.04247 | 1.0674 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 1000 | Al | 1 | XLPE | Pb |  | 810 | 185.1909 | 923.4 | 211.1176 | 980.1 | 224.081 | 637 | 145.6378 | 726.18 | 166.027 | 770.77 | 176.2217 | 0.0291 | 0.041 | 0.122 | 0.21 | 65.9734 | 5.0279 | 0.3041 | 0.0702 | 0.21 | 65.9734 | 0.016701 | 0.023531 | 0.070018 | 1.1495 | 0.17453 | 0.040289 | 1.1495 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132kV 1c Trefoil XLPE Cu - Pb Sheath - Metric
132 | 300 | Cu | 1 | XLPE | Pb |  | 575 | 131.4627 | 655.5 | 149.8674 | 695.75 | 159.0698 | 488 | 111.5718 | 556.32 | 127.1918 | 590.48 | 135.0019 | 0.0601 | 0.078 | 0.153 | 0.13 | 40.8407 | 3.1125 | 0.3351 | 0.0961 | 0.13 | 40.8407 | 0.034493 | 0.044766 | 0.08781 | 0.71161 | 0.19232 | 0.055154 | 0.71161 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 400 | Cu | 1 | XLPE | Pb |  | 650 | 148.61 | 741 | 169.4154 | 786.5 | 179.8181 | 532 | 121.6315 | 606.48 | 138.66 | 643.72 | 147.1742 | 0.047 | 0.062 | 0.146 | 0.14 | 43.9823 | 3.3519 | 0.322 | 0.0879 | 0.14 | 43.9823 | 0.026974 | 0.035583 | 0.083792 | 0.76635 | 0.1848 | 0.050448 | 0.76635 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 500 | Cu | 1 | XLPE | Pb |  | 725 | 165.7573 | 826.5 | 188.9633 | 877.25 | 200.5663 | 578 | 132.1485 | 658.92 | 150.6493 | 699.38 | 159.8997 | 0.0366 | 0.049 | 0.138 | 0.16 | 50.2655 | 3.8307 | 0.3116 | 0.0828 | 0.16 | 50.2655 | 0.021006 | 0.028122 | 0.079201 | 0.87583 | 0.17883 | 0.047521 | 0.87583 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 630 | Cu | 1 | XLPE | Pb |  | 815 | 186.334 | 929.1 | 212.4208 | 986.15 | 225.4642 | 624 | 142.6656 | 711.36 | 162.6387 | 755.04 | 172.6253 | 0.0283 | 0.04 | 0.133 | 0.17 | 53.4071 | 4.0702 | 0.3033 | 0.0788 | 0.17 | 53.4071 | 0.016242 | 0.022957 | 0.076331 | 0.93056 | 0.17407 | 0.045225 | 0.93056 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 800 | Cu | 1 | XLPE | Pb |  | 890 | 203.4813 | 1014.6 | 231.9687 | 1076.9 | 246.2124 | 666 | 152.2681 | 759.24 | 173.5856 | 805.86 | 184.2443 | 0.0221 | 0.032 | 0.126 | 0.195 | 61.2611 | 4.6687 | 0.2971 | 0.0748 | 0.195 | 61.2611 | 0.012684 | 0.018365 | 0.072314 | 1.0674 | 0.17051 | 0.042929 | 1.0674 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132 | 1000 | Cu | 1 | XLPE | Pb |  | 960 | 219.4855 | 1094.4 | 250.2134 | 1161.6 | 265.5774 | 705 | 161.1846 | 803.7 | 183.7505 | 853.05 | 195.0334 | 0.0176 | 0.027 | 0.122 | 0.21 | 65.9734 | 5.0279 | 0.2926 | 0.0701 | 0.21 | 65.9734 | 0.010101 | 0.015496 | 0.070018 | 1.1495 | 0.16793 | 0.040232 | 1.1495 | BICC 1991 + CBI X0, R0 from Nexans Sheath (800mm2)
132kV 1c Trefoil Oil Filled Cu - Pb Sheath - Imperial
132 | 0.1 | Cu | 1 | Oil | Pb |  | 245 | 56.0145 | 279.3 | 63.8566 | 296.45 | 67.7776 | 235 | 53.7282 | 267.9 | 61.2502 | 284.35 | 65.0111 | 0.26967 | 0.33914 | 0.1269 | 0.2735 | 85.9226 | 6.564 | 0.80043 | 0.085512 | 0.2735 | 85.9226 | 0.15477 | 0.19464 | 0.072833 | 1.4971 | 0.45938 | 0.049077 | 1.4971 | BICC Pub448 (R0X0 sheath from Westinghouse )
132 | 0.15 | Cu | 1 | Oil | Pb |  | 300 | 68.5892 | 342 | 78.1917 | 363 | 82.9929 | 285 | 65.1598 | 324.9 | 74.2821 | 344.85 | 78.8433 | 0.18106 | 0.22755 | 0.12253 | 0.31726 | 99.6702 | 7.5486 | 0.69032 | 0.081056 | 0.31726 | 99.6702 | 0.10391 | 0.1306 | 0.070321 | 1.7367 | 0.39619 | 0.04652 | 1.7367 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.2 | Cu | 1 | Oil | Pb |  | 345 | 78.8776 | 393.3 | 89.9205 | 417.45 | 95.4419 | 330 | 75.4481 | 376.2 | 86.0109 | 399.3 | 91.2922 | 0.13752 | 0.17285 | 0.11815 | 0.31726 | 99.6702 | 7.5486 | 0.62151 | 0.078036 | 0.31726 | 99.6702 | 0.078923 | 0.099203 | 0.06781 | 1.7367 | 0.3567 | 0.044786 | 1.7367 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.25 | Cu | 1 | Oil | Pb |  | 390 | 89.166 | 444.6 | 101.6492 | 471.9 | 107.8908 | 365 | 83.4502 | 416.1 | 95.1332 | 441.65 | 100.9748 | 0.11006 | 0.13784 | 0.12143 | 0.30632 | 96.2333 | 7.3298 | 0.57289 | 0.075771 | 0.30632 | 96.2333 | 0.063164 | 0.079112 | 0.069694 | 1.6768 | 0.3288 | 0.043486 | 1.6768 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.3 | Cu | 1 | Oil | Pb |  | 430 | 98.3112 | 490.2 | 112.0748 | 520.3 | 118.9566 | 400 | 91.4523 | 456 | 104.2556 | 484 | 110.6573 | 0.09031 | 0.11378 | 0.11925 | 0.31726 | 99.6702 | 7.5486 | 0.53601 | 0.073969 | 0.31726 | 99.6702 | 0.051831 | 0.065298 | 0.068438 | 1.7367 | 0.30763 | 0.042452 | 1.7367 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.35 | Cu | 1 | Oil | Pb |  | 460 | 105.1701 | 524.4 | 119.8939 | 556.6 | 127.2559 | 430 | 98.3112 | 490.2 | 112.0748 | 520.3 | 118.9566 | 0.077597 | 0.09846 | 0.11596 | 0.33914 | 106.544 | 8.0956 | 0.50668 | 0.072479 | 0.33914 | 106.544 | 0.044535 | 0.056508 | 0.066554 | 1.8564 | 0.2908 | 0.041597 | 1.8564 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.4 | Cu | 1 | Oil | Pb |  | 495 | 113.1722 | 564.3 | 129.0163 | 598.95 | 136.9384 | 460 | 105.1701 | 524.4 | 119.8939 | 556.6 | 127.2559 | 0.067336 | 0.085332 | 0.11378 | 0.36102 | 113.4178 | 8.6426 | 0.48258 | 0.071213 | 0.36102 | 113.4178 | 0.038645 | 0.048974 | 0.065298 | 1.9762 | 0.27696 | 0.04087 | 1.9762 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.45 | Cu | 1 | Oil | Pb |  | 520 | 118.888 | 592.8 | 135.5323 | 629.2 | 143.8544 | 480 | 109.7427 | 547.2 | 125.1067 | 580.8 | 132.7887 | 0.060629 | 0.07658 | 0.11268 | 0.37196 | 116.8547 | 8.8614 | 0.46227 | 0.070114 | 0.37196 | 116.8547 | 0.034797 | 0.043951 | 0.064671 | 2.0361 | 0.26531 | 0.04024 | 2.0361 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.5 | Cu | 1 | Oil | Pb |  | 545 | 124.6037 | 621.3 | 142.0483 | 659.45 | 150.7705 | 505 | 115.4585 | 575.7 | 131.6227 | 611.05 | 139.7048 | 0.054766 | 0.070016 | 0.11049 | 0.3829 | 120.2916 | 9.0802 | 0.44483 | 0.069146 | 0.3829 | 120.2916 | 0.031431 | 0.040184 | 0.063415 | 2.096 | 0.2553 | 0.039684 | 2.096 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.55 | Cu | 1 | Oil | Pb |  | 575 | 131.4627 | 655.5 | 149.8674 | 695.75 | 159.0698 | 530 | 121.1743 | 604.2 | 138.1387 | 641.3 | 146.6209 | 0.04888 | 0.062358 | 0.10831 | 0.40478 | 127.1654 | 9.7366 | 0.42963 | 0.068281 | 0.40478 | 127.1654 | 0.028053 | 0.035789 | 0.062159 | 2.2157 | 0.24657 | 0.039188 | 2.2157 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.6 | Cu | 1 | Oil | Pb |  | 595 | 136.0353 | 678.3 | 155.0802 | 719.95 | 164.6027 | 545 | 124.6037 | 621.3 | 142.0483 | 659.45 | 150.7705 | 0.04527 | 0.057982 | 0.10721 | 0.41572 | 130.6023 | 9.9554 | 0.4162 | 0.067501 | 0.41572 | 130.6023 | 0.025981 | 0.033277 | 0.061531 | 2.2756 | 0.23886 | 0.038741 | 2.2756 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.65 | Cu | 1 | Oil | Pb |  | 615 | 140.6079 | 701.1 | 160.293 | 744.15 | 170.1355 | 565 | 129.1763 | 644.1 | 147.261 | 683.65 | 156.3034 | 0.042064 | 0.0547 | 0.10721 | 0.42666 | 134.0392 | 10.1742 | 0.40421 | 0.066792 | 0.42666 | 134.0392 | 0.024142 | 0.031393 | 0.061531 | 2.3355 | 0.23199 | 0.038333 | 2.3355 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.75 | Cu | 1 | Oil | Pb |  | 655 | 149.7531 | 746.7 | 170.7185 | 792.55 | 181.2013 | 590 | 134.8921 | 672.6 | 153.777 | 713.9 | 163.2195 | 0.036594 | 0.048136 | 0.10502 | 0.44854 | 140.913 | 10.7212 | 0.38364 | 0.065542 | 0.44854 | 140.913 | 0.021002 | 0.027626 | 0.060275 | 2.4553 | 0.22018 | 0.037616 | 2.4553 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 0.85 | Cu | 1 | Oil | Pb |  | 690 | 157.7552 | 786.6 | 179.8409 | 834.9 | 190.8838 | 620 | 141.751 | 706.8 | 161.5962 | 750.2 | 171.5188 | 0.031978 | 0.042666 | 0.10284 | 0.48136 | 151.2237 | 11.487 | 0.36651 | 0.064468 | 0.48136 | 151.2237 | 0.018353 | 0.024487 | 0.05902 | 2.6349 | 0.21035 | 0.037 | 2.6349 | BICC Pub 448 (R0X0 sheath from Westinghouse )
132 | 1 | Cu | 1 | Oil | Pb |  | 745 | 170.3299 | 849.3 | 194.1761 | 901.45 | 206.0992 | 665 | 152.0394 | 758.1 | 173.3249 | 804.65 | 183.9677 | 0.025972 | 0.035008 | 0.099554 | 0.52512 | 164.9713 | 12.581 | 0.3454 | 0.0631 | 0.52512 | 164.9713 | 0.014906 | 0.020092 | 0.057136 | 2.8745 | 0.19823 | 0.036214 | 2.8745 | BICC Pub 448 (R0X0 sheath from Westinghouse )