## Introduction
Network Headroom Report 2024
Summary Page
Published April 2024
The data contained in this workbook is an accompaniment to Northern Powergrid's 2024 Network Development Report and can also be viewed alongside the 2024 NDP Metholodology. The workbook can be used to identify areas of the network with headroom availability up to, and including, 2050. This can be broken down into each Distribution Future Energy Scenario (DFES) - Consumer Transformation, Leading the Way, Falling Short and System Transformation - as well as Northern Powergrid's Best View Scenario (which supersedes the Planning Scenario). This can be viewed for every Bulk Supply Point (BSP) and Primary Substation. The Generation Headroom calculations are completed by finding the difference in the forecast minimum demand, based on the DFES 2023 data, the results of the latest fault level survey, and the forecast reverse power flow capacity, at each substation. This takes into account the forecast generation capacity based on the DFES 2023 data. The reverse power flow forecast takes into account the current reverse power flow limits and any changes which are scheduled to take place in the future, driven by anticipated investment. The Demand Headroom calculations are completed by finding the difference in the forecast demand, based on the DFES 2023 data, and the forecast firm capacity, at each substation. The firm capacity forecast takes into account the current firm capacity and any changes which are scheduled to take place in the future, driven by anticipated investment outcomes. Netherlands Way, Wetherby and Seaham are new substations so therefore have no demand forecasts. This results in forecast headrooms being equal to their proposed firm capacities. The forecast substation headrooms are currently under review and will be addressed in the next update of the NDP. The results should be only used as a guide and will be updated in the next refresh of the data, due in 2025.
Contents
Worksheet |  | Description
Demand Headroom Capacity |  | Details of the demand headroom capacity (in MW) for each BSP and Primary substation for each of the DFES scenarios and Northern Powergrid's Best View scenario.
Generation Headroom Capacity |  | Details of the generation headroom capacity (in MW) for each BSP and Primary substation for each of the DFES scenarios and Northern Powergrid's Best View scenario.
EISD Table |  | Details of the Earliest In-Service Date for Demand and Generation at each GSP, scenario-independent, as advised by National Grid.
DOCUMENT CONTROL
Approvals
Role | Approver | Date
Author | Dr Richard Mandeya | 2024-04-26
Reviewer | Dr Neal Wade | 2024-04-29
Manager Approval | Dr Gillian Williamson | 2024-04-29
Version Control
Version | Comment | Date
V1.0 | First issue for Stakeholder Consultation | 2024-03-28
V1.1 | Second issue final publication | 2024-04-29

## Demand Headroom
Version 1.1 | [7 empty] | Demand Headroom Capacity (MW)
| Please filter on your selected substation | [6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2035 | 2040 | 2045 | 2050
Licence Area | Substation Name | Voltage (kV) | Supply Voltage (kV) | BSP Group | GSP | Substation Location | Scenario Name | [11 empty] | Bulk Supply Point or Primary
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Consumer Transformation | 18.469 | 18.322 | 65.908 | 65.29 | 65.11 | 64.864 | 64.498 | 61.994 | 52.459 | 45.46 | 38.966 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Consumer Transformation | 31.058 | 29.197 | 26.543 | 23.408 | 21.105 | 18.679 | 15.736 | -15.991 | -41.536 | -60.607 | -78.282 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Consumer Transformation | 122.331 | 115.709 | 113.77 | 111.676 | 110.223 | 108.583 | 106.422 | 94.998 | 66.707 | 46.024 | 27.937 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Consumer Transformation | 9.077 | 6.055 | 2.762 | -1.19 | -4.006 | -6.943 | -10.523 | -26.565 | -59.783 | -85.719 | -110.482 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 68.212 | 65.511 | 63.822 | 61.776 | 60.341 | 58.824 | 56.923 | 48.331 | 31.373 | 18.947 | 7.642 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Consumer Transformation | 17.33 | 17.502 | 17.516 | 17.384 | 17.425 | 17.383 | 17.229 | 15.356 | 8.953 | 4.548 | 0.827 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Consumer Transformation | 29.847 | 28.367 | 26.35 | 24.024 | 22.079 | 20.045 | 17.607 | 72.314 | 53.537 | 39.125 | 25.956 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Consumer Transformation | 43.008 | 41.472 | 39.292 | 36.896 | 35.338 | 33.659 | 31.508 | 21.424 | 0.234 | -15.095 | -29.167 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 45.273 | 40.966 | 40.127 | 39.119 | 38.439 | 37.62 | 28.218 | -1.389 | -16.207 | -26.418 | -35.089 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Consumer Transformation | 70.951 | 68.698 | 67.526 | 66.042 | 65.095 | 64.117 | 62.887 | 57.665 | 43.612 | 32.458 | 21.819 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Consumer Transformation | 40.092 | 38.05 | 36.291 | 34.101 | 32.651 | 31.072 | 29.04 | 14.444 | -5.97 | -20.769 | -34.264 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Consumer Transformation | 34.474 | 26.047 | 17.548 | -0.036 | -7.985 | -16.421 | -26.651 | -119.334 | -214.403 | -285.432 | -348.857 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Consumer Transformation | 90.328 | 89.833 | 89.095 | 88.202 | 87.6 | 86.964 | 86.173 | 82.567 | 75.427 | 69.958 | 64.683 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Consumer Transformation | 53.841 | 53.064 | 51.896 | 50.399 | 49.289 | 48.078 | 46.629 | 38.725 | 16.283 | -2.191 | -19.39 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Consumer Transformation | 40.949 | 37.996 | 34.918 | 31.272 | 28.356 | 25.228 | 21.466 | 2.439 | -29.781 | -53.06 | -73.644 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Consumer Transformation | 63.098 | 62.985 | 62.578 | 61.945 | 61.786 | 61.586 | 61.267 | 59.475 | 49.568 | 41.919 | 34.669 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 42.019 | 41.729 | 41.215 | 40.541 | 40.086 | 39.588 | 38.933 | 35.821 | 28.656 | 23.286 | 18.348 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Consumer Transformation | 17.148 | 16.261 | 14.87 | 13.181 | 12.075 | 10.876 | 9.365 | 2.087 | -10.791 | -19.605 | -27.611 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Consumer Transformation | 57.621 | 55.804 | 53.053 | 49.779 | 47.722 | 45.574 | 42.915 | 31.101 | 7.225 | -10.296 | -26.775 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Consumer Transformation | 49.991 | 49.057 | 47.526 | 84.58 | 83.045 | 81.395 | 79.331 | 69.387 | 51.377 | 38.175 | 26.48 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Consumer Transformation | 37.872 | 35.446 | 33.649 | 31.296 | 29.655 | 27.886 | 25.596 | 14.764 | -12.526 | -33.771 | -53.426 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Consumer Transformation | 59.427 | 57.903 | 55.725 | 53.199 | 51.254 | 49.208 | 46.719 | 62.213 | 42.011 | 27.246 | 13.997 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Consumer Transformation | 89.01 | 88.464 | 87.549 | 86.396 | 85.619 | 84.812 | 83.798 | 79.41 | 68.777 | 60.513 | 52.816 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Consumer Transformation | 81.807 | 81 | 79.87 | 78.534 | 77.422 | 76.26 | 74.864 | 68.54 | 59.197 | 52.462 | 46.434 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Consumer Transformation | 90.944 | 90.03 | 88.783 | 87.384 | 86.36 | 85.29 | 83.99 | 78.054 | 66.582 | 57.963 | 49.986 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Consumer Transformation | 46.141 | 45.585 | 44.739 | 43.619 | 42.442 | 41.005 | 39.204 | 27.029 | 9.867 | -0.303 | -7.04 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Consumer Transformation | 55.872 | 54.947 | 53.641 | 52.097 | 50.956 | 49.74 | 48.279 | 41.058 | 27.388 | 17.007 | 7.384 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 62.72 | 62.877 | 62.952 | 63 | 63.135 | 63.241 | 63.28 | 63.279 | 58.466 | 54.588 | 51.033 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 33.31 | 28.047 | 22.435 | 18.23 | 15.127 | 11.937 | 8.085 | -8.798 | -41.622 | -66.278 | -88.599 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Consumer Transformation | 40.381 | 40.083 | 39.476 | 38.687 | 38.13 | 37.443 | 36.503 | 30.595 | 14.16 | 2.254 | -7.715 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Consumer Transformation | 53.891 | 51.664 | 48.992 | 46.595 | 44.658 | 42.635 | 40.082 | 28.99 | 8.266 | -7.27 | -21.042 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Consumer Transformation | 44.366 | 42.777 | 40.319 | 37.386 | 35.302 | 33.119 | 30.383 | 18.344 | -6.947 | -26.017 | -43.489 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Consumer Transformation | 113.613 | 111.537 | 110.939 | 109.94 | 109.385 | 108.564 | 107.349 | 72.925 | 48.44 | 31.331 | 17.285 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Consumer Transformation | 80.169 | 80.155 | 80.01 | 79.75 | 79.593 | 79.378 | 79.072 | 76.885 | 71.013 | 66.544 | 62.593 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Consumer Transformation | 67.871 | 66.679 | 65.092 | 63.45 | 62.328 | 61.153 | 59.676 | 53.215 | 39.438 | 29.243 | 19.814 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Consumer Transformation | 25.452 | 25.518 | 25.468 | 25.308 | 25.234 | 25.135 | 24.965 | 23.894 | 16.904 | 11.066 | 5.731 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 55.166 | 54.68 | 51.754 | 50.916 | 50.016 | 48.984 | 47.738 | 40.162 | 29.229 | 21.854 | 16.264 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Consumer Transformation | 49.284 | 45.782 | 43.357 | 40.833 | 39.132 | 37.346 | 35.101 | 25.25 | 6.114 | -7.758 | -20.518 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 4.458 | 4.141 | 3.446 | 2.477 | 2.088 | 1.617 | 0.97 | -2.983 | -17.871 | -29.406 | -40.163 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Consumer Transformation | 40.428 | 40.433 | 40.435 | 40.433 | 106.629 | 106.622 | 106.611 | 106.528 | 106.395 | 106.244 | 106.09 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 69.456 | 66.112 | 65.527 | 64.88 | 64.278 | 63.632 | 62.92 | 58.835 | 53.168 | 48.594 | 44.573 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Consumer Transformation | 54.604 | 53.885 | 52.981 | 51.878 | 50.82 | 49.622 | 48.237 | 39.547 | 25.305 | 14.927 | 6.242 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Consumer Transformation | 82.633 | 82.183 | 81.599 | 80.923 | 80.316 | 79.692 | 78.981 | 75.644 | 70.421 | 66.157 | 62.252 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Consumer Transformation | 23.986 | 20.096 | 17.695 | 14.802 | 12.563 | 10.188 | 7.159 | -6.611 | -36.054 | -58.332 | -78.217 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Consumer Transformation | 46.554 | 45.254 | 43.224 | 40.772 | 39.055 | 37.217 | 34.889 | 23.979 | 0.963 | -16.214 | -31.787 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Consumer Transformation | 45.15 | 42.646 | 41.004 | 38.878 | 37.563 | 36.09 | 34.171 | 24.291 | 3.408 | -11.078 | -23.983 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 27.805 | 25.794 | 22.695 | 18.953 | 16.42 | 13.711 | 10.299 | -5.564 | -33.578 | -53.275 | -71.537 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Consumer Transformation | 67.792 | 66.987 | 65.865 | 64.487 | 63.644 | 62.729 | 61.667 | 55.694 | 40.532 | 28.536 | 17.054 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Consumer Transformation | 33.853 | 31.515 | 28.304 | 24.663 | 22.099 | 19.406 | 16.17 | 1.068 | -24.54 | -42.796 | -59.607 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Consumer Transformation | 26.969 | 21.602 | 16.068 | 9.915 | 4.817 | -0.487 | -6.855 | -35.68 | -85.583 | -122.75 | -156.114 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Consumer Transformation | 53.928 | 48.248 | 45.182 | 42.035 | 39.604 | 37.089 | 34.009 | 20.816 | -0.823 | -16.255 | -30.024 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Consumer Transformation | 43.708 | 42.025 | 39.729 | 37.064 | 34.908 | 32.682 | 30.013 | 18.202 | -1.658 | -17.219 | -31.916 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Consumer Transformation | 56.759 | 56.13 | 55.005 | 53.565 | 52.467 | 51.301 | 49.798 | 42.959 | 25.81 | 12.516 | 0.656 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Falling Short | 18.223 | 18.203 | 66.105 | 65.915 | 65.629 | 65.257 | 64.843 | 62.38 | 59.447 | 57.305 | 56.136 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Falling Short | 31.268 | 30.126 | 28.739 | 27.084 | 25.073 | 22.742 | 20.432 | -8.16 | -17.281 | -23.593 | -27.881 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Falling Short | 122.554 | 116.581 | 115.765 | 114.755 | 113.376 | 111.664 | 109.894 | 101.017 | 92.715 | 87.386 | 84.929 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Falling Short | 9.135 | 6.994 | 5.311 | 3.271 | 0.775 | -2.117 | -4.94 | -17.499 | -27.604 | -34.745 | -40.032 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 68.47 | 66.347 | 65.668 | 64.793 | 63.649 | 62.27 | 60.917 | 55.044 | 50.67 | 48.11 | 46.799 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Falling Short | 16.879 | 16.858 | 16.777 | 16.623 | 16.388 | 16.073 | 15.694 | 13.064 | 9.55 | 6.693 | 4.943 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Falling Short | 29.827 | 28.697 | 27.379 | 25.861 | 24.068 | 22.028 | 20.012 | 76.704 | 68.859 | 63.075 | 58.78 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Falling Short | 43.485 | 42.878 | 42.113 | 41.173 | 39.919 | 38.388 | 36.874 | 29.975 | 24.398 | 21.056 | 19.338 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 44.946 | 40.786 | 40.273 | 39.631 | 38.809 | 37.817 | 28.424 | -0.76 | -8.141 | -13.735 | -16.916 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Falling Short | 70.915 | 68.982 | 68.481 | 67.819 | 66.959 | 65.93 | 64.94 | 60.885 | 58.249 | 56.708 | 55.645 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Falling Short | 40.152 | 38.718 | 38.057 | 37.157 | 35.945 | 34.455 | 32.964 | 21.286 | 15.406 | 11.743 | 9.897 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Falling Short | 35.831 | 29.826 | 25.384 | 12.296 | 5.519 | -2.429 | -10.383 | -90.845 | -123.235 | -144.947 | -157.71 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Falling Short | 90.299 | 90.014 | 89.652 | 89.208 | 88.661 | 88.024 | 87.398 | 84.543 | 82.13 | 80.377 | 79.062 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Falling Short | 52.96 | 52.029 | 50.956 | 49.707 | 48.263 | 46.649 | 44.994 | 36.408 | 27.644 | 20.37 | 14.555 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Falling Short | 41.121 | 38.894 | 37.106 | 34.975 | 32.405 | 29.423 | 26.39 | 11.325 | -2.936 | -13.159 | -19.376 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Falling Short | 62.818 | 62.837 | 62.777 | 62.622 | 62.365 | 62.027 | 61.678 | 59.912 | 58.182 | 57.036 | 56.35 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 41.971 | 41.843 | 41.641 | 41.356 | 40.968 | 40.493 | 40.022 | 37.829 | 36.02 | 34.911 | 34.297 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Falling Short | 17.315 | 16.987 | 16.502 | 15.855 | 14.994 | 13.937 | 12.873 | 7.807 | 3.242 | 0.274 | -1.176 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Falling Short | 58.156 | 57.437 | 56.447 | 55.186 | 53.559 | 51.601 | 49.699 | 41.615 | 35.756 | 32.35 | 30.578 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Falling Short | 49.781 | 49.097 | 48.198 | 86.068 | 84.651 | 82.972 | 81.287 | 73.341 | 66.431 | 61.572 | 58.537 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Falling Short | 37.85 | 35.936 | 35.193 | 34.165 | 32.801 | 31.149 | 29.518 | 22.141 | 16.418 | 13.093 | 11.31 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Falling Short | 59.607 | 58.674 | 57.53 | 56.164 | 54.479 | 52.501 | 50.548 | 68.661 | 61.257 | 56.122 | 52.827 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Falling Short | 89.098 | 88.862 | 88.507 | 88.028 | 87.4 | 86.643 | 85.914 | 82.921 | 80.992 | 79.988 | 79.452 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Falling Short | 81.799 | 81.195 | 80.467 | 79.607 | 78.583 | 77.41 | 76.252 | 70.932 | 66.604 | 63.607 | 61.455 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Falling Short | 91.21 | 90.723 | 90.138 | 89.446 | 88.592 | 87.595 | 86.615 | 82.24 | 78.814 | 76.632 | 75.279 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Falling Short | 45.782 | 45.182 | 44.445 | 43.529 | 42.378 | 40.971 | 39.368 | 29.307 | 16.914 | 7.61 | 3.194 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Falling Short | 55.486 | 54.664 | 53.72 | 52.635 | 51.37 | 49.943 | 48.501 | 41.384 | 34.565 | 29.055 | 24.747 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 62.396 | 62.482 | 62.545 | 62.574 | 62.546 | 62.476 | 62.397 | 61.893 | 61.277 | 60.853 | 60.565 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 36.886 | 34.46 | 32.192 | 30.139 | 27.578 | 24.56 | 21.637 | 9.492 | 1.384 | -3.327 | -6.215 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Falling Short | 40.197 | 39.995 | 39.685 | 39.24 | 38.601 | 37.781 | 36.881 | 31.815 | 26.332 | 22.604 | 21.026 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Falling Short | 55.082 | 53.996 | 52.843 | 51.631 | 50.074 | 48.207 | 46.41 | 39.014 | 34.206 | 31.579 | 30.127 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Falling Short | 44.731 | 43.982 | 42.964 | 41.666 | 39.983 | 37.956 | 35.996 | 27.724 | 21.954 | 18.671 | 16.854 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Falling Short | 113.14 | 111.138 | 110.929 | 110.488 | 109.762 | 108.762 | 107.575 | 74.554 | 65.66 | 59.471 | 57.112 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Falling Short | 79.486 | 79.208 | 78.878 | 78.483 | 78.016 | 77.481 | 76.905 | 73.586 | 69.764 | 66.383 | 63.72 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Falling Short | 68.359 | 67.837 | 67.227 | 66.521 | 65.598 | 64.49 | 63.415 | 58.877 | 55.693 | 53.889 | 52.876 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Falling Short | 25.231 | 25.232 | 25.188 | 25.085 | 24.924 | 24.717 | 24.501 | 23.359 | 22.271 | 21.584 | 21.158 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Falling Short | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Falling Short | 54.601 | 53.889 | 50.82 | 49.874 | 48.781 | 47.538 | 46.201 | 38.631 | 30.102 | 23.133 | 18.477 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Falling Short | 50.024 | 47.505 | 46.57 | 45.489 | 44.086 | 42.4 | 40.758 | 33.844 | 29.012 | 26.247 | 24.732 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 4.221 | 4.112 | 3.9 | 3.569 | 3.101 | 2.513 | 1.886 | -1.502 | -4.976 | -7.316 | -8.512 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Falling Short | 40.329 | 40.269 | 40.206 | 40.14 | 106.271 | 106.198 | 106.124 | 105.716 | 105.261 | 104.775 | 104.276 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 68.725 | 64.995 | 64.045 | 63.054 | 62.012 | 60.917 | 59.783 | 53.711 | 47.171 | 40.942 | 35.319 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Falling Short | 53.804 | 52.795 | 51.701 | 50.488 | 49.138 | 47.647 | 46.046 | 36.796 | 26.034 | 16.881 | 10.307 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Falling Short | 82.227 | 81.642 | 81.004 | 80.309 | 79.544 | 78.716 | 77.891 | 73.925 | 70.2 | 66.823 | 63.744 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Falling Short | 24.277 | 21.112 | 20.032 | 18.65 | 16.839 | 14.655 | 12.522 | 3.228 | -3.648 | -7.605 | -9.706 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Falling Short | 46.789 | 46.201 | 45.382 | 44.316 | 42.915 | 41.217 | 39.537 | 31.962 | 25.992 | 22.402 | 20.551 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Falling Short | 45.112 | 43.206 | 42.661 | 41.861 | 40.748 | 39.348 | 37.907 | 30.707 | 23.787 | 19.307 | 17.339 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 28.069 | 27.212 | 26.008 | 24.446 | 22.422 | 19.968 | 17.543 | 6.257 | -3.689 | -10.289 | -14.052 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Falling Short | 67.432 | 66.763 | 66.008 | 65.143 | 64.16 | 63.072 | 61.943 | 55.83 | 49.178 | 43.628 | 39.298 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Falling Short | 34.291 | 32.994 | 31.439 | 29.618 | 27.405 | 24.833 | 22.276 | 10.336 | -0.198 | -7.703 | -12.668 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Falling Short | 27.985 | 24.095 | 20.997 | 17.404 | 13.058 | 8.029 | 3.088 | -19.186 | -36.854 | -48.404 | -56.02 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Falling Short | 54.928 | 50.384 | 49.019 | 47.46 | 45.491 | 43.149 | 40.878 | 31.428 | 24.953 | 21.231 | 19.22 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Falling Short | 43.729 | 42.49 | 41.049 | 39.394 | 37.45 | 35.258 | 33.124 | 23.633 | 16.027 | 10.376 | 5.794 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Falling Short | 56.683 | 56.317 | 55.77 | 55.032 | 54.051 | 52.856 | 51.682 | 46.571 | 42.821 | 40.645 | 39.47 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Leading the Way | 18.47 | 18.276 | 65.8 | 65.136 | 64.916 | 64.606 | 63.874 | 53.151 | 44.754 | 39.097 | 40.512 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Leading the Way | 31.137 | 29.232 | 26.487 | 23.311 | 21.064 | 18.652 | 15.095 | -33.672 | -57.001 | -73.376 | -73.341 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Leading the Way | 122.421 | 115.756 | 113.654 | 111.428 | 109.911 | 108.145 | 105.085 | 71.972 | 46.862 | 29.774 | 32.797 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Leading the Way | 9.152 | 6.098 | 2.721 | -1.254 | -3.943 | -6.789 | -11.122 | -51.13 | -82.031 | -104.916 | -104.698 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 68.275 | 65.582 | 63.865 | 61.808 | 60.434 | 58.952 | 56.6 | 35.868 | 20.68 | 10.428 | 11.822 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Leading the Way | 17.315 | 17.442 | 17.391 | 17.195 | 17.162 | 17.019 | 16.582 | 9.613 | 4.236 | 0.877 | 1.82 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Leading the Way | 29.886 | 28.393 | 26.319 | 23.942 | 22.037 | 20.012 | 17.163 | 60.608 | 43.315 | 30.683 | 29.435 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Leading the Way | 43.127 | 41.596 | 39.352 | 36.942 | 35.459 | 33.831 | 31.193 | 5.093 | -13.833 | -26.39 | -23.962 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 45.288 | 40.914 | 39.951 | 38.825 | 38.01 | 36.996 | 27.122 | -12.44 | -25.283 | -33.691 | -33.084 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Leading the Way | 70.982 | 68.722 | 67.517 | 66.009 | 65.125 | 64.193 | 62.502 | 45.884 | 32.799 | 23.122 | 24.3 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Leading the Way | 40.122 | 38.043 | 36.204 | 33.962 | 32.548 | 30.975 | 28.384 | -1.382 | -19.695 | -31.933 | -29.943 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Leading the Way | 34.642 | 26.09 | 17.204 | -0.745 | -8.744 | -17.444 | -30.375 | -185.794 | -271.607 | -331.994 | -331.518 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Leading the Way | 90.344 | 89.842 | 89.088 | 88.194 | 87.625 | 87.015 | 86.077 | 77.326 | 70.758 | 66.037 | 66.157 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Leading the Way | 53.843 | 52.976 | 51.686 | 50.104 | 48.955 | 47.67 | 45.598 | 20.898 | 0.082 | -16.41 | -17.119 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Leading the Way | 40.961 | 37.927 | 34.682 | 30.869 | 27.845 | 24.518 | 19.896 | -18.289 | -47.216 | -67.13 | -68.492 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Leading the Way | 63.121 | 62.975 | 62.526 | 61.883 | 61.737 | 61.538 | 60.893 | 49.677 | 40.889 | 34.712 | 36.801 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 42.031 | 41.723 | 41.18 | 40.498 | 40.073 | 39.601 | 38.8 | 30.012 | 23.525 | 19.013 | 19.859 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Leading the Way | 17.171 | 16.254 | 14.805 | 13.074 | 11.972 | 10.745 | 8.846 | -7.102 | -18.471 | -25.553 | -24.639 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Leading the Way | 57.723 | 55.935 | 53.163 | 49.878 | 47.917 | 45.82 | 42.416 | 13.308 | -8.089 | -22.423 | -20.43 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Leading the Way | 50.007 | 49.047 | 47.444 | 84.42 | 82.887 | 81.196 | 78.62 | 56.998 | 40.802 | 29.672 | 29.957 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Leading the Way | 37.916 | 35.438 | 33.544 | 31.138 | 29.598 | 27.915 | 24.926 | -7.838 | -32.953 | -51.229 | -48.891 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Leading the Way | 59.484 | 57.959 | 55.724 | 53.15 | 51.23 | 49.161 | 46.153 | 48.801 | 30.657 | 18.229 | 18.537 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Leading the Way | 89.032 | 88.48 | 87.543 | 86.374 | 85.649 | 84.882 | 83.542 | 70.797 | 61.084 | 54.152 | 55.197 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Leading the Way | 81.884 | 81.089 | 79.946 | 78.606 | 77.527 | 76.376 | 74.795 | 63.224 | 54.737 | 48.962 | 48.575 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Leading the Way | 91.005 | 90.095 | 88.815 | 87.393 | 86.4 | 85.341 | 83.757 | 69.857 | 59.376 | 51.981 | 52.255 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Leading the Way | 46.057 | 45.388 | 44.342 | 42.949 | 41.43 | 39.535 | 37.005 | 17.654 | 3.739 | -3.822 | -4.845 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Leading the Way | 55.891 | 54.932 | 53.566 | 51.98 | 50.829 | 49.574 | 47.779 | 31.883 | 19.437 | 10.433 | 9.679 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 62.742 | 62.878 | 62.917 | 62.955 | 63.1 | 63.216 | 63.127 | 57.781 | 53.459 | 50.228 | 51.826 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 33.827 | 28.795 | 23.072 | 18.771 | 15.756 | 12.599 | 7.708 | -31.722 | -61.554 | -82.171 | -80.087 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Leading the Way | 40.38 | 40.007 | 39.259 | 38.323 | 37.648 | 36.788 | 35.202 | 16.764 | 2.433 | -7.236 | -5.468 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Leading the Way | 54.114 | 51.988 | 49.285 | 46.881 | 45.066 | 43.145 | 40.088 | 14.381 | -4.222 | -16.96 | -14.987 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Leading the Way | 44.448 | 42.857 | 40.339 | 37.369 | 35.406 | 33.313 | 29.882 | -0.923 | -23.787 | -39.624 | -37.347 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Leading the Way | 113.574 | 111.316 | 110.44 | 109.182 | 108.354 | 107.162 | 104.871 | 49.58 | 28.399 | 14.662 | 17.932 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Leading the Way | 80.161 | 80.119 | 79.932 | 79.628 | 79.427 | 79.148 | 78.63 | 72.323 | 67.141 | 63.391 | 63.334 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Leading the Way | 67.983 | 66.816 | 65.198 | 63.559 | 62.505 | 61.38 | 59.596 | 42.694 | 30.258 | 21.705 | 23.162 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Leading the Way | 25.453 | 25.487 | 25.396 | 25.212 | 25.142 | 25.041 | 24.634 | 16.938 | 10.468 | 5.375 | 6.376 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Leading the Way | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Leading the Way | 55.131 | 54.585 | 51.558 | 50.583 | 49.531 | 48.292 | 46.669 | 34.481 | 25.139 | 19.077 | 17.457 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Leading the Way | 49.44 | 45.991 | 43.537 | 41.008 | 39.402 | 37.683 | 34.936 | 11.279 | -5.741 | -16.959 | -14.915 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 4.479 | 4.116 | 3.339 | 2.292 | 1.88 | 1.357 | 0.139 | -16.463 | -29.866 | -39.477 | -37.82 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Leading the Way | 40.428 | 40.433 | 40.435 | 40.433 | 106.63 | 106.623 | 106.613 | 106.51 | 106.379 | 106.23 | 106.098 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 69.442 | 66.08 | 65.463 | 64.773 | 64.125 | 63.416 | 62.547 | 56.559 | 51.416 | 47.37 | 45.114 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Leading the Way | 54.555 | 53.753 | 52.721 | 51.47 | 50.226 | 48.781 | 46.971 | 31.598 | 19.057 | 10.082 | 7.423 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Leading the Way | 82.639 | 82.185 | 81.588 | 80.898 | 80.293 | 79.66 | 78.836 | 72.947 | 68.074 | 64.214 | 63.026 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Leading the Way | 24.077 | 20.172 | 17.685 | 14.748 | 12.636 | 10.361 | 6.601 | -29.211 | -55.683 | -74.088 | -71.175 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Leading the Way | 46.578 | 45.241 | 43.125 | 40.612 | 38.957 | 37.151 | 34.178 | 6.321 | -14.342 | -28.51 | -26.509 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Leading the Way | 45.169 | 42.616 | 40.876 | 38.663 | 37.31 | 35.742 | 33.16 | 8.065 | -10.203 | -21.795 | -19.594 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 27.839 | 25.747 | 22.518 | 18.71 | 16.247 | 13.558 | 9.403 | -25.758 | -50.971 | -67.302 | -65.52 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Leading the Way | 67.776 | 66.877 | 65.65 | 64.209 | 63.319 | 62.332 | 60.827 | 43.934 | 29.974 | 19.443 | 18.703 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Leading the Way | 33.926 | 31.533 | 28.21 | 24.504 | 21.956 | 19.218 | 15.277 | -15.805 | -38.714 | -53.858 | -53.805 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Leading the Way | 27.289 | 21.926 | 16.244 | 10.011 | 5.052 | -0.211 | -7.726 | -67.942 | -113.581 | -145.737 | -146.066 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Leading the Way | 54.128 | 48.525 | 45.421 | 42.24 | 39.905 | 37.432 | 33.782 | 6.728 | -12.66 | -25.436 | -24.099 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Leading the Way | 43.785 | 42.107 | 39.784 | 37.13 | 35.09 | 32.966 | 30 | 5.709 | -12.79 | -26.596 | -27.697 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Leading the Way | 56.791 | 56.144 | 54.966 | 53.485 | 52.435 | 51.293 | 49.249 | 29.062 | 13.562 | 2.475 | 4.315 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - System Transformation | 18.254 | 18.122 | 65.849 | 65.467 | 65.074 | 64.603 | 64.025 | 60.296 | 53.856 | 46.421 | 36.23 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - System Transformation | 30.717 | 28.94 | 26.707 | 24.205 | 21.673 | 19.004 | 16.149 | -16.153 | -33.44 | -52.259 | -77.381 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - System Transformation | 121.802 | 115.068 | 113.372 | 111.683 | 109.915 | 107.939 | 105.691 | 93.041 | 72.695 | 52.315 | 25.801 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - System Transformation | 8.574 | 5.55 | 2.674 | -0.576 | -3.753 | -7.062 | -10.587 | -27.82 | -51.602 | -77.587 | -112.606 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 68.012 | 65.339 | 63.918 | 62.295 | 60.73 | 59.082 | 57.313 | 48.608 | 37.37 | 25.334 | 8.714 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - System Transformation | 17.032 | 17.06 | 16.989 | 16.821 | 16.601 | 16.284 | 15.854 | 12.464 | 6.763 | 1.225 | -5.423 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - System Transformation | 29.548 | 28.023 | 26.159 | 24.095 | 21.972 | 19.752 | 17.412 | 71.712 | 57.548 | 42.94 | 24.281 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - System Transformation | 42.644 | 41.148 | 39.363 | 37.546 | 35.776 | 33.886 | 31.806 | 21.223 | 6.671 | -8.409 | -28.638 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 44.941 | 40.593 | 39.842 | 39.007 | 38.057 | 36.951 | 27.332 | -3.533 | -15.773 | -27.076 | -40.099 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - System Transformation | 70.718 | 68.439 | 67.422 | 66.222 | 65.095 | 63.926 | 62.692 | 56.755 | 47.868 | 36.901 | 20.673 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - System Transformation | 39.766 | 37.725 | 36.249 | 34.531 | 32.84 | 31.017 | 29.009 | 13.825 | -0.288 | -14.999 | -34.923 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - System Transformation | 33.555 | 25.263 | 17.935 | 2.105 | -6.4 | -15.432 | -25.124 | -118.081 | -184.355 | -252.626 | -342.003 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - System Transformation | 90.193 | 89.703 | 89.074 | 88.356 | 87.649 | 86.906 | 86.105 | 82.112 | 76.936 | 71.283 | 63.711 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - System Transformation | 53.232 | 52.28 | 51.091 | 49.703 | 48.228 | 46.623 | 44.843 | 34.763 | 16.481 | -3.151 | -28.014 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - System Transformation | 40.54 | 37.601 | 34.879 | 31.803 | 28.633 | 25.24 | 21.558 | 2.037 | -22.171 | -45.276 | -73.541 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - System Transformation | 62.824 | 62.677 | 62.372 | 61.959 | 61.605 | 61.198 | 60.7 | 57.761 | 50.958 | 43.006 | 31.898 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 41.864 | 41.546 | 41.09 | 40.545 | 40.014 | 39.44 | 38.797 | 35.447 | 30.026 | 24.655 | 17.63 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - System Transformation | 17.039 | 16.284 | 15.226 | 13.99 | 12.723 | 11.362 | 9.876 | 2.154 | -5.79 | -14.489 | -26.503 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - System Transformation | 57.378 | 55.731 | 53.551 | 51.093 | 48.789 | 46.392 | 43.854 | 31.534 | 17.291 | 0.114 | -25.133 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - System Transformation | 49.645 | 48.603 | 47.146 | 84.404 | 82.646 | 80.764 | 78.729 | 68.125 | 54.557 | 41.059 | 23.596 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - System Transformation | 37.545 | 35.099 | 33.57 | 31.717 | 29.886 | 27.925 | 25.764 | 14.473 | -4.482 | -24.646 | -52.43 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - System Transformation | 59.115 | 57.549 | 55.587 | 53.426 | 51.284 | 49.03 | 46.635 | 61.722 | 47.115 | 32.182 | 12.815 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - System Transformation | 88.917 | 88.403 | 87.652 | 86.754 | 85.891 | 84.996 | 84.047 | 79.476 | 72.853 | 65.009 | 53.553 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - System Transformation | 81.636 | 80.885 | 79.923 | 78.812 | 77.599 | 76.327 | 74.991 | 68.408 | 62.053 | 55.207 | 46.414 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - System Transformation | 90.815 | 89.961 | 88.932 | 87.834 | 86.731 | 85.577 | 84.348 | 78.31 | 70.671 | 62.395 | 51.183 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - System Transformation | 45.84 | 45.138 | 44.206 | 43.045 | 41.688 | 40.066 | 38.154 | 25.523 | 9.994 | -0.631 | -10.162 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - System Transformation | 55.486 | 54.459 | 53.202 | 51.803 | 50.381 | 48.869 | 47.233 | 38.619 | 27.456 | 15.927 | 1.662 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 62.451 | 62.488 | 62.495 | 62.506 | 62.494 | 62.444 | 62.333 | 61.428 | 57.206 | 52.819 | 47.184 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 32.52 | 27.258 | 22.507 | 19.156 | 15.83 | 12.389 | 8.828 | -8.065 | -27.216 | -50.744 | -84.787 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - System Transformation | 40.026 | 39.609 | 39.027 | 38.348 | 37.585 | 36.672 | 35.58 | 28.655 | 16.38 | 4.499 | -10.539 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - System Transformation | 53.459 | 51.13 | 48.737 | 46.673 | 44.609 | 42.455 | 40.184 | 29.344 | 15.193 | 0.318 | -20.027 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - System Transformation | 44.033 | 42.459 | 40.364 | 38.005 | 35.713 | 33.316 | 30.774 | 18.422 | 2.012 | -16.368 | -42.334 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - System Transformation | 113.042 | 110.771 | 110.2 | 109.415 | 108.497 | 107.285 | 105.699 | 69.476 | 50.137 | 32.867 | 12.322 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - System Transformation | 79.779 | 79.58 | 79.285 | 78.906 | 78.494 | 78.011 | 77.443 | 73.763 | 67.807 | 61.956 | 55.113 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - System Transformation | 67.599 | 66.393 | 65.045 | 63.748 | 62.504 | 61.2 | 59.797 | 53.101 | 43.73 | 33.647 | 19.898 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - System Transformation | 25.29 | 25.305 | 25.249 | 25.126 | 24.964 | 24.766 | 24.519 | 22.869 | 17.887 | 12.144 | 4.202 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - System Transformation | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - System Transformation | 54.828 | 54.188 | 51.141 | 50.191 | 49.08 | 47.824 | 46.414 | 37.901 | 27.875 | 20.094 | 12.849 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - System Transformation | 48.914 | 45.411 | 43.365 | 41.373 | 39.47 | 37.478 | 35.356 | 25.144 | 12.888 | -0.916 | -20.364 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 4.249 | 3.978 | 3.496 | 2.871 | 2.266 | 1.569 | 0.749 | -4.359 | -14.055 | -25.651 | -42.262 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - System Transformation | 40.378 | 40.347 | 40.311 | 40.27 | 106.423 | 106.372 | 106.316 | 105.971 | 105.524 | 105.06 | 104.596 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 69.065 | 65.492 | 64.676 | 63.802 | 62.892 | 61.923 | 60.891 | 54.955 | 48.009 | 41.244 | 34.054 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - System Transformation | 54.167 | 53.246 | 52.179 | 50.957 | 49.621 | 48.129 | 46.451 | 36.263 | 22.094 | 10.099 | -2.04 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - System Transformation | 82.388 | 81.822 | 81.157 | 80.421 | 79.663 | 78.878 | 78.063 | 73.975 | 69.207 | 64.541 | 59.384 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - System Transformation | 23.563 | 19.605 | 17.471 | 15.058 | 12.636 | 10.076 | 7.316 | -6.532 | -27.094 | -48.333 | -76.961 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - System Transformation | 46.229 | 44.93 | 43.199 | 41.233 | 39.315 | 37.277 | 35.065 | 23.764 | 7.991 | -8.67 | -31.507 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - System Transformation | 44.852 | 42.406 | 41.105 | 39.516 | 37.916 | 36.152 | 34.166 | 23.302 | 8.976 | -5.561 | -24.823 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 27.421 | 25.626 | 23.191 | 20.365 | 17.434 | 14.317 | 10.961 | -6.174 | -23.679 | -43.421 | -70.81 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - System Transformation | 67.454 | 66.658 | 65.711 | 64.638 | 63.536 | 62.343 | 61.018 | 53.408 | 42.332 | 29.696 | 13.329 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - System Transformation | 33.492 | 31.316 | 28.684 | 25.833 | 22.947 | 19.915 | 16.689 | 0.463 | -15.965 | -34.525 | -59.517 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - System Transformation | 26.406 | 21.262 | 16.569 | 11.532 | 6.185 | 0.591 | -5.287 | -34.093 | -67.1 | -102.934 | -150.451 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - System Transformation | 53.581 | 47.953 | 45.34 | 42.761 | 40.162 | 37.464 | 34.647 | 21.539 | 7.973 | -7.143 | -28.206 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - System Transformation | 43.341 | 41.592 | 39.463 | 37.115 | 34.774 | 32.361 | 29.825 | 17.614 | 2.238 | -13.712 | -34.114 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - System Transformation | 56.463 | 55.759 | 54.727 | 53.491 | 52.229 | 50.887 | 49.443 | 42.091 | 30.376 | 17.459 | -0.496 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NPg Best View | 18.537 | 18.487 | 66.075 | 65.491 | 65.209 | 64.853 | 64.384 | 61.714 | 52.804 | 46.243 | 39.868 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NPg Best View | 31.518 | 30.017 | 27.742 | 24.999 | 23.131 | 21.107 | 18.689 | -10.593 | -33.873 | -51.336 | -67.949 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NPg Best View | 122.962 | 116.8 | 115.165 | 113.328 | 112.001 | 110.426 | 108.387 | 97.57 | 71.699 | 52.705 | 35.379 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NPg Best View | 9.687 | 7.175 | 4.439 | 1.079 | -1.074 | -3.382 | -6.166 | -19.69 | -50.353 | -74.445 | -97.808 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 68.513 | 66.058 | 64.637 | 62.885 | 61.764 | 60.546 | 59.05 | 51.777 | 36.304 | 24.906 | 14.294 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NPg Best View | 17.498 | 17.814 | 17.926 | 17.853 | 17.91 | 17.83 | 17.583 | 15.363 | 9.73 | 5.872 | 2.283 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NPg Best View | 30.211 | 29.024 | 27.329 | 25.34 | 23.773 | 22.089 | 20.101 | 76.264 | 59.325 | 46.231 | 33.941 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NPg Best View | 43.525 | 42.378 | 40.487 | 38.404 | 37.091 | 35.662 | 33.91 | 25.23 | 5.632 | -8.565 | -21.925 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 45.489 | 41.368 | 40.549 | 39.557 | 38.675 | 37.615 | 27.955 | -2.039 | -15.257 | -24.346 | -32.735 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NPg Best View | 71.219 | 69.19 | 68.267 | 67.053 | 66.394 | 65.685 | 64.783 | 60.67 | 47.534 | 37.031 | 26.961 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NPg Best View | 40.389 | 38.634 | 37.094 | 35.177 | 33.921 | 32.529 | 30.803 | 18.111 | -0.71 | -14.375 | -27.232 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NPg Best View | 35.808 | 28.483 | 21.105 | 4.604 | -2.155 | -9.588 | -18.49 | -104.624 | -190.07 | -254.31 | -313.723 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NPg Best View | 90.438 | 90.051 | 89.405 | 88.629 | 88.125 | 87.588 | 86.947 | 83.838 | 77.154 | 72.006 | 66.951 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NPg Best View | 53.994 | 53.43 | 52.311 | 50.947 | 49.731 | 48.41 | 46.899 | 39.071 | 17.736 | 0.049 | -16.849 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NPg Best View | 41.42 | 38.84 | 36.137 | 32.843 | 30.278 | 27.408 | 23.976 | 6.102 | -22.385 | -43.045 | -62.31 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NPg Best View | 63.192 | 63.206 | 62.836 | 62.295 | 62.096 | 61.864 | 61.55 | 59.94 | 50.395 | 42.997 | 35.868 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 42.147 | 41.965 | 41.544 | 40.978 | 40.624 | 40.227 | 39.717 | 37.054 | 30.341 | 25.309 | 20.588 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NPg Best View | 17.304 | 16.577 | 15.298 | 13.76 | 12.744 | 11.626 | 10.273 | 3.621 | -8.008 | -15.969 | -23.558 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NPg Best View | 58.06 | 56.604 | 54.263 | 51.437 | 49.878 | 48.199 | 46.147 | 36.361 | 14.758 | -1.194 | -16.51 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NPg Best View | 50.295 | 49.629 | 48.371 | 85.713 | 84.47 | 83.07 | 81.325 | 72.402 | 56.175 | 44.215 | 33.191 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NPg Best View | 38.262 | 36.178 | 34.719 | 32.751 | 31.507 | 30.131 | 28.389 | 19.19 | -6.309 | -26.247 | -45.016 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NPg Best View | 59.835 | 58.655 | 56.837 | 54.672 | 53.117 | 51.417 | 49.364 | 66.336 | 48.249 | 34.95 | 22.625 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NPg Best View | 89.17 | 88.769 | 88.024 | 87.062 | 86.502 | 85.905 | 85.159 | 81.642 | 71.803 | 64.107 | 56.873 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NPg Best View | 82.037 | 81.414 | 80.496 | 79.385 | 78.529 | 77.603 | 76.496 | 71.07 | 62.679 | 56.601 | 51 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NPg Best View | 91.37 | 90.756 | 89.797 | 88.669 | 87.921 | 87.093 | 86.063 | 80.949 | 70.376 | 62.381 | 54.812 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NPg Best View | 46.347 | 45.923 | 45.1 | 43.906 | 42.53 | 40.754 | 38.496 | 24.865 | 10.943 | 3.032 | -3.222 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NPg Best View | 56.129 | 55.423 | 54.283 | 52.913 | 51.889 | 50.76 | 49.412 | 42.655 | 30.059 | 20.432 | 11.195 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NPg Best View | 63.009 | 63.359 | 63.562 | 63.717 | 63.899 | 64.039 | 64.104 | 64.22 | 59.572 | 55.816 | 52.339 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NPg Best View | 35.836 | 31.904 | 27.371 | 23.888 | 21.53 | 19.026 | 16.033 | 2.622 | -26.543 | -48.574 | -68.699 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NPg Best View | 40.663 | 40.609 | 40.074 | 39.363 | 38.659 | 37.789 | 36.677 | 30.477 | 15.602 | 4.786 | -4.842 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NPg Best View | 55.182 | 53.708 | 51.784 | 49.995 | 48.793 | 47.468 | 45.764 | 37.289 | 18.887 | 5.002 | -7.449 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NPg Best View | 44.95 | 43.811 | 41.849 | 39.441 | 37.948 | 36.332 | 34.322 | 24.592 | 1.504 | -16.01 | -32.289 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NPg Best View | 114.013 | 112.24 | 111.762 | 110.784 | 110.052 | 108.931 | 107.33 | 72.015 | 50.085 | 34.785 | 21.184 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NPg Best View | 80.374 | 80.52 | 80.479 | 80.31 | 80.176 | 79.948 | 79.592 | 77.273 | 71.959 | 67.887 | 64.057 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NPg Best View | 68.396 | 67.539 | 66.257 | 64.896 | 64.068 | 63.174 | 62.062 | 56.814 | 44.152 | 34.732 | 25.893 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NPg Best View | 25.528 | 25.679 | 25.67 | 25.572 | 25.502 | 25.405 | 25.249 | 24.279 | 17.525 | 11.858 | 6.613 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NPg Best View | 25.883 | 25.893 | 25.901 | 25.907 | 25.912 | 25.916 | 25.917 | 25.918 | 25.918 | 25.918 | 25.918 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NPg Best View | 55.355 | 55.018 | 52.18 | 51.398 | 50.469 | 49.335 | 47.936 | 39.885 | 30.599 | 24.378 | 19.095 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NPg Best View | 49.987 | 46.941 | 44.947 | 42.826 | 41.548 | 40.166 | 38.452 | 30.386 | 12.908 | 0.169 | -11.757 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 4.516 | 4.313 | 3.613 | 2.699 | 2.192 | 1.605 | 0.882 | -3.111 | -17.222 | -28.213 | -38.8 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NPg Best View | 40.458 | 40.491 | 40.515 | 40.533 | 106.745 | 106.749 | 106.743 | 106.668 | 106.539 | 106.391 | 106.239 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NPg Best View | 69.445 | 66.09 | 65.383 | 64.568 | 63.739 | 62.823 | 61.752 | 56.892 | 51.519 | 47.15 | 43.103 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NPg Best View | 54.905 | 54.414 | 53.632 | 52.602 | 51.488 | 50.14 | 48.502 | 39.03 | 26.568 | 17.454 | 9.083 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NPg Best View | 82.79 | 82.474 | 82.023 | 81.49 | 81.008 | 80.492 | 79.893 | 76.919 | 72.115 | 68.152 | 64.448 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NPg Best View | 24.643 | 21.243 | 19.374 | 17.033 | 15.421 | 13.651 | 11.411 | 0.035 | -26.951 | -47.476 | -66.13 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NPg Best View | 46.998 | 46.043 | 44.375 | 42.297 | 40.998 | 39.55 | 37.733 | 28.442 | 7.388 | -8.363 | -22.983 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NPg Best View | 45.388 | 43.127 | 41.644 | 39.716 | 38.487 | 37.066 | 35.271 | 25.929 | 7.029 | -6.093 | -18.417 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 28.447 | 26.945 | 24.386 | 21.198 | 19.286 | 17.144 | 14.453 | 0.846 | -24.246 | -41.94 | -58.932 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NPg Best View | 67.917 | 67.234 | 66.162 | 64.848 | 63.971 | 63.002 | 61.889 | 55.841 | 41.549 | 30.176 | 18.933 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NPg Best View | 34.449 | 32.542 | 29.771 | 26.559 | 24.45 | 22.155 | 19.42 | 6.062 | -16.847 | -33.253 | -48.907 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NPg Best View | 28.041 | 23.465 | 18.738 | 13.409 | 9.194 | 4.717 | -0.539 | -25.396 | -70.475 | -104.254 | -135.284 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NPg Best View | 54.89 | 49.81 | 47.435 | 44.894 | 43.208 | 41.376 | 39.109 | 28.557 | 9.529 | -4.133 | -16.579 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NPg Best View | 44.112 | 42.764 | 40.844 | 38.588 | 36.905 | 35.146 | 33.085 | 23.171 | 4.882 | -9.535 | -23.331 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NPg Best View | 57.115 | 56.769 | 55.94 | 54.807 | 54.04 | 53.175 | 52.041 | 46.379 | 30.564 | 18.216 | 7.018 | BSP
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Consumer Transformation | 13.052 | 12.781 | 12.536 | 12.446 | 12.428 | 12.407 | 12.37 | 12.158 | 10.56 | 9.256 | 8.025 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Consumer Transformation | 12.282 | 10.658 | 10.572 | 10.423 | 10.337 | 10.211 | 10.03 | 8.72 | 5.769 | 3.804 | 2.257 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Consumer Transformation | 11.495 | 11.216 | 10.843 | 10.389 | 9.916 | 9.427 | 8.856 | 6.25 | 1.67 | -1.921 | -5.084 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Consumer Transformation | 6.04 | 4.71 | 4.748 | 4.718 | 4.699 | 4.652 | 4.557 | 3.981 | 1.837 | 0.282 | -1.013 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 15.357 | 14.951 | 14.447 | 13.967 | 13.601 | 13.227 | 12.77 | 10.866 | 7.3 | 4.576 | 2.081 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 17.144 | 17.137 | 17.11 | 17.076 | 17.069 | 17.059 | 17.036 | 16.924 | 16.274 | 15.748 | 15.241 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Consumer Transformation | 9.011 | 8.478 | 7.756 | 6.928 | 6.331 | 5.719 | 5 | 1.837 | -3.833 | -8.12 | -12.214 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Consumer Transformation | 17.214 | 17.256 | 17.266 | 17.249 | 17.269 | 17.285 | 17.286 | 17.281 | 16.016 | 14.971 | 13.994 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Consumer Transformation | 1.043 | 0.852 | 0.573 | 0.231 | -0.08 | -0.404 | -0.791 | -2.572 | -6.547 | -9.76 | -12.652 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Consumer Transformation | 3.403 | 2.926 | 3.07 | 3.179 | 3.311 | 3.432 | 3.533 | 3.896 | 3.277 | 2.802 | 2.347 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Consumer Transformation | 11.999 | 11.752 | 11.379 | 10.929 | 10.617 | 10.292 | 9.896 | 9.218 | 6.091 | 3.703 | 1.389 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Consumer Transformation | 2.616 | 2.296 | 1.885 | 1.478 | 1.156 | 0.795 | 0.322 | -1.985 | -5.857 | -8.432 | -10.642 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Consumer Transformation | 3.331 | 3.327 | 3.312 | 3.288 | 3.27 | 3.249 | 3.22 | 3.068 | 2.743 | 2.494 | 2.269 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Consumer Transformation | 15.727 | 15.536 | 15.237 | 14.877 | 14.665 | 14.446 | 14.175 | 13.02 | 9.984 | 7.637 | 5.375 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Consumer Transformation | 13.069 | 12.559 | 12.52 | 12.459 | 12.44 | 12.418 | 12.385 | 12.215 | 11.338 | 10.593 | 9.861 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Consumer Transformation | 10.628 | 10.633 | 10.59 | 10.501 | 10.46 | 10.406 | 10.323 | 9.845 | 7.864 | 6.433 | 5.199 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Consumer Transformation | 15.567 | 15.225 | 14.741 | 14.179 | 13.748 | 13.296 | 12.751 | 10.214 | 6.313 | 3.61 | 1.223 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Consumer Transformation | 8.364 | 8.393 | 8.398 | 8.379 | 8.374 | 8.359 | 8.326 | 8.031 | 6.684 | 5.677 | 4.845 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Consumer Transformation | 5.835 | 5.704 | 5.505 | 5.243 | 5.068 | 4.884 | 4.668 | 3.603 | 0.06 | -2.978 | -5.928 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Consumer Transformation | 21.434 | 21.393 | 21.293 | 21.151 | 21.05 | 20.943 | 20.802 | 20.223 | 18.936 | 17.959 | 17.072 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Consumer Transformation | 3.689 | 3.56 | 3.395 | 3.207 | 3.088 | 2.964 | 2.827 | 2.114 | 0.247 | -1.377 | -2.985 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Consumer Transformation | 11.535 | 11.073 | 10.418 | 9.644 | 9.082 | 8.487 | 7.772 | 4.362 | -1.65 | -6.047 | -10.091 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Consumer Transformation | 9.37 | 8.918 | 8.309 | 7.66 | 7.17 | 6.658 | 6.026 | 3.464 | -1.12 | -4.545 | -7.636 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Consumer Transformation | 14.653 | 14.377 | 14.018 | 13.659 | 13.379 | 13.092 | 12.74 | 11.282 | 9.066 | 7.494 | 6.066 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Consumer Transformation | 3.012 | 2.969 | 2.815 | 2.575 | 2.475 | 2.342 | 2.145 | 0.884 | -2.749 | -5.294 | -7.553 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Consumer Transformation | 5.393 | 5.177 | 4.87 | 4.501 | 4.207 | 3.895 | 3.522 | 1.717 | -1.009 | -2.92 | -4.586 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 15.169 | 15.137 | 15.076 | 14.99 | 14.931 | 14.863 | 14.775 | 14.37 | 12.988 | 11.909 | 10.962 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 4.304 | 1.337 | 1.291 | 1.177 | 1.104 | 0.986 | 0.801 | -0.501 | -4.683 | -7.696 | -10.174 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Consumer Transformation | 7.45 | 7.347 | 7.156 | 6.887 | 6.701 | 6.477 | 6.192 | 4.384 | 0.353 | -2.483 | -4.888 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Consumer Transformation | 11.684 | 11.393 | 10.945 | 10.397 | 10.024 | 9.638 | 9.162 | 7.063 | 2.268 | -1.503 | -5.028 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Consumer Transformation | 5.797 | 5.359 | 4.702 | 3.911 | 3.31 | 2.672 | 1.889 | -1.853 | -8.905 | -14.133 | -18.798 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Consumer Transformation | 6.88 | 6.864 | 6.844 | 6.819 | 6.797 | 6.775 | 6.751 | 6.638 | 6.319 | 6.038 | 5.764 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Consumer Transformation | 3.7 | 3.664 | 3.612 | 3.55 | 3.492 | 3.429 | 3.349 | 2.938 | 2.218 | 1.673 | 1.188 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Consumer Transformation | 11.578 | 11.178 | 10.597 | 9.91 | 9.474 | 9.019 | 8.463 | 6.027 | 1.275 | -2.314 | -5.796 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 13.548 | 13.46 | 13.368 | 13.264 | 13.158 | 13.051 | 12.943 | 12.398 | 11.164 | 9.949 | 8.729 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Consumer Transformation | 4.614 | 4.499 | 4.338 | 4.151 | 4.005 | 3.855 | 3.675 | 2.901 | 1.773 | 0.953 | 0.195 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 9.41 | 9.078 | 8.57 | 7.964 | 7.553 | 7.122 | 6.578 | 4.224 | -0.679 | -4.372 | -7.834 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Consumer Transformation | 11.54 | 11.268 | 10.85 | 10.354 | 9.953 | 9.528 | 8.992 | 6.567 | 2.239 | -0.929 | -3.712 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Consumer Transformation | 9.323 | 9.357 | 9.339 | 9.278 | 9.293 | 9.293 | 9.266 | 8.992 | 7.247 | 5.929 | 4.713 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Consumer Transformation | 10.219 | 10.208 | 10.134 | 10.016 | 9.929 | 9.826 | 9.666 | 9.022 | 7.826 | 6.989 | 6.228 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Consumer Transformation | 17.455 | 17.277 | 17.028 | 16.735 | 16.501 | 16.251 | 15.947 | 14.501 | 12.601 | 11.393 | 10.407 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Consumer Transformation | 7.673 | 22.187 | 21.915 | 21.6 | 21.345 | 21.081 | 20.753 | 19.3 | 15.886 | 13.187 | 10.762 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Consumer Transformation | 10.132 | 9.702 | 9.075 | 8.319 | 7.706 | 7.084 | 6.349 | 20.361 | 14.197 | 9.2 | 4.539 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Consumer Transformation | 3.848 | 3.713 | 3.538 | 3.369 | 3.254 | 3.137 | 2.99 | 2.442 | 1.599 | 1.011 | 0.44 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Consumer Transformation | 5.872 | 4.918 | 3.756 | 2.614 | 1.653 | 0.651 | -0.536 | -5.228 | -11.654 | -16.315 | -20.294 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Consumer Transformation | 3.749 | 3.358 | 2.811 | 2.148 | 1.445 | 0.704 | -0.201 | -4.373 | -11.615 | -17.449 | -22.658 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Consumer Transformation | 5.022 | 4.435 | 3.594 | 2.59 | 1.787 | 0.962 | -0.018 | 19.749 | 11.713 | 5.345 | -0.562 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Consumer Transformation | 4.092 | 4.161 | 4.221 | 4.269 | 4.315 | 4.354 | 4.383 | 4.438 | 4.209 | 4.08 | 3.995 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Consumer Transformation | 7.95 | 7.495 | 6.808 | 5.968 | 5.324 | 4.62 | 3.752 | 16.23 | 8.888 | 3.889 | -0.336 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Consumer Transformation | 12.827 | 12.919 | 12.998 | 13.055 | 13.106 | 13.149 | 13.182 | 13.24 | 12.431 | 11.852 | 11.385 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Consumer Transformation | 9.528 | 9.679 | 9.821 | 9.952 | 10.075 | 10.192 | 10.303 | 10.754 | 10.857 | 10.951 | 11.038 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Consumer Transformation | 11.114 | 11.217 | 11.294 | 11.37 | 11.467 | 11.55 | 11.607 | 11.77 | 10.058 | 8.717 | 7.514 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Consumer Transformation | 9.024 | 9.095 | 9.139 | 9.165 | 9.211 | 9.249 | 9.267 | 9.333 | 8.57 | 7.99 | 7.445 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Consumer Transformation | 10.767 | 10.469 | 10.019 | 9.49 | 9.107 | 8.687 | 8.158 | 5.48 | 1.31 | -1.378 | -3.634 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Consumer Transformation | 5.101 | 5.039 | 4.949 | 4.846 | 4.739 | 4.628 | 4.491 | 3.935 | 3.6 | 3.423 | 3.301 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Consumer Transformation | 7.652 | 7.635 | 7.599 | 7.549 | 7.509 | 7.464 | 7.405 | 7.109 | 6.586 | 6.122 | 5.665 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Consumer Transformation | 13.023 | 12.516 | 11.878 | 11.247 | 10.752 | 10.238 | 9.604 | 6.808 | 1.618 | -2.263 | -5.711 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Consumer Transformation | 0.818 | 0.819 | 0.809 | 0.792 | 0.777 | 0.759 | 0.732 | 0.576 | 0.232 | -0.035 | -0.277 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Consumer Transformation | 2.402 | 2.17 | 1.867 | 1.527 | 1.252 | 0.967 | 0.623 | -0.846 | -2.836 | -4.289 | -5.65 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 9.586 | 9.369 | 9.02 | 8.584 | 8.301 | 7.99 | 7.601 | 5.669 | 2.185 | -0.154 | -2.285 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Consumer Transformation | 8.383 | 8.231 | 8.038 | 7.872 | 7.758 | 7.631 | 7.449 | 6.653 | 4.281 | 2.441 | 0.769 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Consumer Transformation | 5.194 | 4.882 | 4.46 | 3.977 | 3.627 | 3.261 | 2.826 | 0.822 | -3.211 | -6.379 | -9.387 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Consumer Transformation | 4.201 | 4.23 | 4.252 | 4.266 | 4.28 | 4.288 | 4.289 | 4.24 | 3.953 | 3.758 | 3.609 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Consumer Transformation | 21.91 | 21.723 | 21.464 | 21.186 | 21.012 | 20.833 | 20.609 | 19.643 | 17.012 | 14.965 | 13.055 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Consumer Transformation | 7.444 | 7.5 | 7.528 | 7.546 | 7.601 | 7.647 | 7.672 | 7.741 | 6.596 | 5.687 | 4.826 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Consumer Transformation | 12.954 | 12.591 | 12.153 | 11.759 | 11.452 | 11.133 | 10.733 | 9.034 | 5.762 | 3.284 | 1.07 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Consumer Transformation | 8.453 | 8.43 | 8.33 | 8.169 | 8.046 | 7.905 | 7.7 | 6.731 | 4.122 | 2.122 | 0.322 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Consumer Transformation | 2.12 | 1.32 | 0.239 | -0.909 | -1.686 | -2.491 | -3.48 | -7.752 | -15.78 | -21.656 | -27.099 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Consumer Transformation | 0.989 | 0.859 | 0.696 | 0.499 | 0.309 | 0.107 | -0.125 | -0.835 | -1.622 | -2.28 | -2.897 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Consumer Transformation | 2.866 | 2.756 | 2.599 | 2.395 | 2.217 | 2.016 | 1.776 | 0.345 | -2.557 | -4.774 | -6.718 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Consumer Transformation | 12.957 | 12.89 | 12.742 | 12.536 | 12.364 | 12.183 | 11.948 | 12.044 | 10.234 | 8.887 | 7.731 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Consumer Transformation | 14.47 | 14.262 | 14.92 | 14.491 | 14.187 | 13.871 | 13.472 | 11.745 | 8.019 | 5.128 | 2.421 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Consumer Transformation | 22.186 | 22.192 | 22.107 | 21.91 | 21.704 | 21.417 | 21.027 | 18.147 | 12.552 | 9.079 | 6.646 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Consumer Transformation | 9.79 | 9.497 | 9.091 | 8.613 | 8.225 | 7.82 | 7.34 | 12.12 | 7.92 | 4.589 | 1.487 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Consumer Transformation | 1.893 | 1.559 | 1.116 | 0.605 | 0.258 | -0.104 | -0.539 | -2.333 | -5.187 | -7.326 | -9.412 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Consumer Transformation | 7.966 | 7.58 | 6.945 | 6.16 | 5.713 | 5.254 | 4.684 | 2.258 | -4.237 | -9.371 | -14.383 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Consumer Transformation | 5.244 | 2.942 | 2.925 | 2.876 | 2.835 | 2.778 | 2.691 | 2.212 | 0.8 | -0.267 | -1.175 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Consumer Transformation | 7.447 | 6.97 | 6.283 | 5.494 | 4.907 | 4.298 | 3.543 | 0.326 | -5.144 | -9.165 | -12.859 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Consumer Transformation | 3.351 | 3.077 | 17.361 | 16.867 | 16.456 | 16.022 | 15.481 | 12.973 | 7.787 | 3.873 | 0.486 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Consumer Transformation | -0.464 | -0.609 | -0.813 | -1.058 | -1.266 | -1.478 | -1.731 | -2.84 | -5.017 | -6.814 | -8.511 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Consumer Transformation | 2.558 | 2.567 | 2.555 | 2.522 | 2.511 | 2.493 | 2.462 | 2.26 | 1.442 | 0.859 | 0.356 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Consumer Transformation | 10.336 | 10.038 | 9.576 | 9.02 | 8.604 | 8.175 | 7.645 | 5.432 | 1.296 | -1.809 | -4.643 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Consumer Transformation | 8.228 | 7.849 | 7.279 | 6.605 | 6.185 | 5.739 | 5.181 | 2.649 | -2.407 | -6.092 | -9.574 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Consumer Transformation | 11.222 | 11.097 | 10.892 | 10.641 | 10.452 | 10.247 | 9.985 | 8.738 | 6.826 | 5.522 | 4.361 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Consumer Transformation | 3.621 | 2.712 | 2.729 | 2.688 | 2.688 | 2.659 | 2.585 | 1.935 | -0.578 | -2.371 | -3.867 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Consumer Transformation | 14.901 | 14.822 | 14.708 | 14.554 | 14.413 | 14.251 | 14.057 | 12.818 | 10.309 | 8.478 | 6.919 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Consumer Transformation | 4.442 | 4.35 | 4.221 | 4.07 | 3.955 | 3.838 | 3.7 | 3.093 | 1.835 | 0.836 | -0.106 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Consumer Transformation | 2.05 | 1.978 | 1.864 | 1.726 | 1.629 | 1.528 | 1.401 | 0.861 | -0.439 | -1.445 | -2.37 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Consumer Transformation | 14.954 | 14.596 | 14.072 | 13.443 | 12.986 | 12.497 | 11.896 | 8.969 | 3.534 | -0.501 | -4.199 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Consumer Transformation | 2.735 | 2.577 | 4.286 | 3.902 | 3.582 | 3.235 | 2.78 | 0.725 | -4.091 | -7.869 | -11.278 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Consumer Transformation | 14.809 | 14.736 | 14.594 | 14.404 | 14.343 | 14.273 | 14.179 | 13.656 | 11.371 | 9.615 | 7.927 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Consumer Transformation | 4.417 | 4.309 | 4.162 | 3.991 | 3.841 | 3.686 | 3.502 | 2.691 | 1.267 | 0.156 | -0.859 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Consumer Transformation | 4.585 | 4.062 | 3.32 | 2.459 | 1.781 | 1.071 | 0.205 | -3.584 | -9.18 | -13.215 | -16.967 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Consumer Transformation | 11.533 | 11.142 | 10.6 | 9.983 | 9.536 | 9.077 | 8.525 | 6.186 | 2.245 | -0.739 | -3.632 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Consumer Transformation | 12.139 | 10.532 | 10.416 | 10.204 | 10.056 | 9.833 | 9.515 | 7.286 | 3.395 | 1.157 | -0.358 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Consumer Transformation | 0.81 | 0.412 | -0.017 | -0.343 | -0.621 | -0.905 | -1.255 | -2.657 | -4.15 | -5.057 | -5.812 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Consumer Transformation | 7.273 | 6.504 | 5.472 | 4.31 | 3.477 | 2.625 | 1.627 | -2.62 | -9.145 | -13.874 | -18.367 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Consumer Transformation | 9.176 | 9.174 | 9.165 | 9.151 | 9.138 | 9.121 | 9.098 | 8.966 | 8.79 | 8.617 | 8.443 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Consumer Transformation | 1.687 | 1.486 | 1.182 | 0.786 | 0.363 | -0.149 | -0.791 | -5.045 | -10.678 | -13.84 | -15.766 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Consumer Transformation | 10.342 | 9.912 | 9.378 | 8.863 | 8.518 | 8.157 | 7.713 | 5.636 | 0.584 | -3.316 | -6.912 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Consumer Transformation | 8.719 | 8.306 | 7.682 | 6.925 | 6.417 | 5.877 | 5.213 | 2.054 | -3.573 | -7.587 | -11.248 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Consumer Transformation | 1.328 | 1.231 | 1.093 | 0.919 | 0.755 | 0.564 | 0.33 | -1.118 | -3.006 | -4.139 | -4.941 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Consumer Transformation | 7.178 | 6.826 | 6.298 | 5.668 | 5.196 | 4.711 | 4.122 | 1.618 | -3.777 | -8.053 | -12.074 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Consumer Transformation | 0.945 | 0.904 | 0.781 | 0.599 | 0.533 | 0.453 | 0.331 | -0.248 | -2.593 | -4.357 | -5.969 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Consumer Transformation | 1.499 | 1.499 | 1.498 | 1.497 | 1.496 | 1.495 | 1.493 | 1.484 | 1.468 | 1.453 | 1.438 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 24.078 | 24.112 | 24.1 | 24.046 | 24.055 | 24.058 | 24.039 | 23.952 | 22.383 | 21.138 | 19.938 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 33.847 | 33.795 | 33.7 | 33.579 | 33.506 | 33.426 | 33.317 | 32.894 | 31.879 | 31.113 | 30.377 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 20.491 | 20.406 | 20.283 | 20.136 | 20.002 | 19.865 | 19.7 | 19.022 | 18.162 | 17.544 | 17 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 14.614 | 14.375 | 14.046 | 13.68 | 13.415 | 13.129 | 12.779 | 11.007 | 7.997 | 5.866 | 3.98 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Consumer Transformation | 13.516 | 13.189 | 12.737 | 13.197 | 12.691 | 12.178 | 11.579 | 9.048 | 5.208 | 2.362 | -0.144 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Consumer Transformation | 10.367 | 9.275 | 8.788 | 8.19 | 7.805 | 7.404 | 6.908 | 4.963 | 1.102 | -1.88 | -4.775 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Consumer Transformation | 1.431 | 15.19 | 14.868 | 14.488 | 14.108 | 13.69 | 13.183 | 10.513 | 6.62 | 3.848 | 1.574 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Consumer Transformation | 10.491 | 9.755 | 8.999 | 8.491 | 8.166 | 7.832 | 7.42 | 5.604 | 1.306 | -1.982 | -5.061 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Consumer Transformation | 15.372 | 15.34 | 15.294 | 15.235 | 15.2 | 15.163 | 15.121 | 14.883 | 13.995 | 13.182 | 12.372 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Consumer Transformation | 3.65 | 2.605 | 1.147 | -0.538 | -1.858 | -3.216 | -4.833 | -10.841 | -19.883 | -26.786 | -33.17 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Consumer Transformation | 5.989 | 5.248 | 4.309 | 3.377 | 2.733 | 2.077 | 1.288 | -1.911 | -6.958 | -10.452 | -13.703 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Consumer Transformation | 4.404 | 4.416 | 4.331 | 4.172 | 4.212 | 4.238 | 4.231 | 4.03 | 0.975 | -1.564 | -4.173 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 17.14 | 14.114 | 13.827 | 13.488 | 13.218 | 12.941 | 12.625 | 11.428 | 9.193 | 7.273 | 5.38 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Consumer Transformation | 14.752 | 14.722 | 14.671 | 14.598 | 14.529 | 14.445 | 14.344 | 13.665 | 12.282 | 11.272 | 10.419 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Consumer Transformation | 9.249 | 9.051 | 8.803 | 8.499 | 8.19 | 7.837 | 7.425 | 4.777 | 0.755 | -2.056 | -4.296 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Consumer Transformation | 11.721 | 11.707 | 11.634 | 11.513 | 11.483 | 11.447 | 11.387 | 11.099 | 8.896 | 7.112 | 5.366 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Consumer Transformation | 11.291 | 11.336 | 11.344 | 11.321 | 11.343 | 11.357 | 11.354 | 11.321 | 10.514 | 9.917 | 9.345 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 3.778 | 3.611 | 3.414 | 3.176 | 2.919 | 2.622 | 2.28 | 0.004 | -3.216 | -5.436 | -7.157 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Consumer Transformation | 14.724 | 14.644 | 14.513 | 14.343 | 14.267 | 14.178 | 14.069 | 13.361 | 11.196 | 9.517 | 7.953 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Consumer Transformation | 10.613 | 10.295 | 9.801 | 9.205 | 8.866 | 8.513 | 8.077 | 6.227 | 1.879 | -1.391 | -4.553 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Consumer Transformation | 9.487 | 9.366 | 9.131 | 8.817 | 8.698 | 8.562 | 8.382 | 7.385 | 3.754 | 1.002 | -1.589 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Consumer Transformation | 7.071 | 6.707 | 6.143 | 5.457 | 4.972 | 4.454 | 3.8 | 0.721 | -4.543 | -8.194 | -11.414 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Consumer Transformation | 4.379 | 3.895 | 3.224 | 2.462 | 1.879 | 1.256 | 0.504 | 14.159 | 8.844 | 5.097 | 1.84 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Consumer Transformation | 10.989 | 10.983 | 10.932 | 10.853 | 10.756 | 10.617 | 10.415 | 9.092 | 7.469 | 6.698 | 6.34 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Consumer Transformation | 15.358 | 15.033 | 14.53 | 13.918 | 13.569 | 13.212 | 12.776 | 10.935 | 6.736 | 3.508 | 0.322 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Consumer Transformation | 8.818 | 8.344 | 7.655 | 6.824 | 6.161 | 5.437 | 4.543 | -0.082 | -7.171 | -11.998 | -16.083 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Consumer Transformation | 3.271 | 3.153 | 2.991 | 3.303 | 3.149 | 2.99 | 2.798 | 1.942 | 0.589 | -0.46 | -1.438 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Consumer Transformation | 7.087 | 6.855 | 6.481 | 6.031 | 5.658 | 5.274 | 4.793 | 9.772 | 4.836 | 0.929 | -2.549 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Consumer Transformation | 4.124 | 3.915 | 3.61 | 3.263 | 3.046 | 2.824 | 2.553 | 1.425 | -0.772 | -2.43 | -4.06 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 12.309 | 12.297 | 12.258 | 12.194 | 12.162 | 12.124 | 12.07 | 11.764 | 10.681 | 9.783 | 8.911 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 25.325 | 25.288 | 25.229 | 25.148 | 25.098 | 25.045 | 24.981 | 24.652 | 23.41 | 22.382 | 21.39 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Consumer Transformation | 14.598 | 14.422 | 14.187 | 13.911 | 13.654 | 13.382 | 13.057 | 11.584 | 9.848 | 8.714 | 7.824 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Consumer Transformation | 12.689 | 12.75 | 12.787 | 12.799 | 12.823 | 12.842 | 12.846 | 12.844 | 11.855 | 11.071 | 10.35 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Consumer Transformation | 19.976 | 19.94 | 19.884 | 19.804 | 19.751 | 19.696 | 19.634 | 19.414 | 18.706 | 18.065 | 17.424 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Consumer Transformation | 6.863 | 6.51 | 5.97 | 5.319 | 4.902 | 4.471 | 3.94 | 1.96 | -1.379 | -3.778 | -6.085 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 21.09 | 21.088 | 21.007 | 20.864 | 20.818 | 20.756 | 20.651 | 20.082 | 17.488 | 15.493 | 13.619 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Consumer Transformation | 13.999 | 13.927 | 13.794 | 13.626 | 13.592 | 13.553 | 13.498 | 13.184 | 10.634 | 8.557 | 6.535 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Consumer Transformation | 4.246 | 4.146 | 3.991 | 3.807 | 3.692 | 3.571 | 3.418 | 2.732 | 1.381 | 0.387 | -0.555 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Consumer Transformation | 0.966 | 0.928 | 0.878 | 0.819 | 0.767 | 0.707 | 0.638 | 0.214 | -0.368 | -0.795 | -1.154 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Consumer Transformation | 16.23 | 16.156 | 16.026 | 15.846 | 15.725 | 15.586 | 15.416 | 14.448 | 11.868 | 9.879 | 8.069 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 22.15 | 21.943 | 21.626 | 21.243 | 20.932 | 20.609 | 20.208 | 18.475 | 15.26 | 12.846 | 10.734 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 26.319 | 26.217 | 26.059 | 25.866 | 25.738 | 25.605 | 25.442 | 24.732 | 22.932 | 21.517 | 20.209 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Consumer Transformation | 2.37 | 2.225 | 2.036 | 1.828 | 1.623 | 1.412 | 1.162 | 0.057 | -1.676 | -3.087 | -4.356 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Consumer Transformation | 2.285 | 2.072 | 1.771 | 1.398 | 1.187 | 0.951 | 0.667 | -1.013 | -5.693 | -9.411 | -12.958 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Consumer Transformation | 14.342 | 14.296 | 14.206 | 14.082 | 13.989 | 13.869 | 13.711 | 12.803 | 11.389 | 10.496 | 9.815 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Consumer Transformation | 4.588 | 4.498 | 4.364 | 4.208 | 4.093 | 3.973 | 3.826 | 3.186 | 1.728 | 0.571 | -0.485 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Consumer Transformation | 14.492 | 14.473 | 14.432 | 14.389 | 14.37 | 14.338 | 14.283 | 13.96 | 12.814 | 11.929 | 11.151 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Consumer Transformation | 9.128 | 9.257 | 9.365 | 9.451 | 9.547 | 9.632 | 9.703 | 10.901 | 10.44 | 10.158 | 9.939 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Consumer Transformation | 1.167 | 0.817 | 0.32 | -0.263 | -0.745 | -1.248 | -1.854 | -4.575 | -8.029 | -10.351 | -12.354 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 16.833 | 16.799 | 16.735 | 16.647 | 16.6 | 16.547 | 16.481 | 16.112 | 14.917 | 13.985 | 13.113 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 16.766 | 16.726 | 16.656 | 16.562 | 16.5 | 16.425 | 16.328 | 15.699 | 14.443 | 13.586 | 12.864 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Consumer Transformation | 4.384 | 3.962 | 3.37 | 2.679 | 2.13 | 1.554 | 0.86 | 12.537 | 7.628 | 3.918 | 0.544 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Consumer Transformation | 14.345 | 14.247 | 14.096 | 13.903 | 13.795 | 13.679 | 13.543 | 12.85 | 10.695 | 8.964 | 7.332 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Consumer Transformation | 7.796 | 7.204 | 6.459 | 5.728 | 5.098 | 4.449 | 3.645 | 17.265 | 11.59 | 7.283 | 3.449 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Consumer Transformation | 4.912 | 4.835 | 4.697 | 4.529 | 4.431 | 4.31 | 4.139 | 3.151 | -0.262 | -2.861 | -5.147 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Consumer Transformation | 10.362 | 10.059 | 9.568 | 8.956 | 8.541 | 8.116 | 7.597 | 5.342 | -0.542 | -5.288 | -9.786 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Consumer Transformation | 0.144 | 0.06 | -0.06 | -0.212 | -0.314 | -0.425 | -0.557 | -1.232 | -2.88 | -4.203 | -5.447 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Consumer Transformation | 13.268 | 12.956 | 12.5 | 11.979 | 11.586 | 11.175 | 10.665 | 8.409 | 4.305 | 1.275 | -1.47 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Consumer Transformation | 17.499 | 17.494 | 17.472 | 17.432 | 17.405 | 17.372 | 17.326 | 17.059 | 15.969 | 15.136 | 14.404 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Consumer Transformation | 12.596 | 12.376 | 12.078 | 11.735 | 11.563 | 11.383 | 11.174 | 10.139 | 7.297 | 4.95 | 2.525 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Consumer Transformation | 6.931 | 6.817 | 6.647 | 6.431 | 6.255 | 6.066 | 5.84 | 4.639 | 1.662 | -0.736 | -2.892 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Consumer Transformation | 9.406 | 9.291 | 9.096 | 8.83 | 8.65 | 8.434 | 8.163 | 6.34 | 1.959 | -1.327 | -4.179 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Consumer Transformation | 15.303 | 15.287 | 15.27 | 15.25 | 15.227 | 15.203 | 15.175 | 16.014 | 15.807 | 15.584 | 15.361 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Consumer Transformation | 16.38 | 16.287 | 16.129 | 15.927 | 15.749 | 15.561 | 15.321 | 14.268 | 12.216 | 10.668 | 9.294 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Consumer Transformation | 12.822 | 12.664 | 12.422 | 12.122 | 11.905 | 11.683 | 11.418 | 10.426 | 7.766 | 5.549 | 3.46 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Consumer Transformation | 10.34 | 9.824 | 9.229 | 8.728 | 8.428 | 8.118 | 7.736 | 6.118 | 2.416 | -0.362 | -3.033 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Consumer Transformation | 9.409 | 8.89 | 8.19 | 7.449 | 6.922 | 6.373 | 5.684 | 2.806 | -2.256 | -6.016 | -9.525 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Consumer Transformation | 2.197 | 2.245 | 2.284 | 2.314 | 2.345 | 2.37 | 2.387 | 2.421 | 2.232 | 2.127 | 2.06 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Consumer Transformation | 9.635 | 8.919 | 8.105 | 7.423 | 6.92 | 6.404 | 5.772 | 20.068 | 14.23 | 9.676 | 5.471 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Consumer Transformation | 4.567 | 4.384 | 4.09 | 3.691 | 3.422 | 3.108 | 2.716 | 0.38 | -5.301 | -9.565 | -13.367 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Consumer Transformation | 3.3 | 2.882 | 2.3 | 1.619 | 1.09 | 0.552 | -0.086 | -2.741 | -7.488 | -11.225 | -14.788 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Consumer Transformation | 23.136 | 23.115 | 23.008 | 22.826 | 22.783 | 22.73 | 22.644 | 22.197 | 19.126 | 16.669 | 14.327 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Consumer Transformation | 6.325 | 6.142 | 5.887 | 5.582 | 5.352 | 5.106 | 4.816 | 3.364 | 0.725 | -1.298 | -3.183 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Consumer Transformation | 6.75 | 6.741 | 6.724 | 6.702 | 6.689 | 6.675 | 6.655 | 6.567 | 6.381 | 6.245 | 6.119 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Consumer Transformation | 11.527 | 10.843 | 9.833 | 8.634 | 7.871 | 7.081 | 6.129 | 2.21 | -5.122 | -10.722 | -16.198 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Consumer Transformation | 21.177 | 21.216 | 21.217 | 21.171 | 21.09 | 20.951 | 20.749 | 19.12 | 17.092 | 16.203 | 15.913 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Consumer Transformation | 11.203 | 10.956 | 10.575 | 10.121 | 9.835 | 9.535 | 9.161 | 7.484 | 3.601 | 0.705 | -2.006 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Consumer Transformation | 12.645 | 12.514 | 12.305 | 12.009 | 11.676 | 11.258 | 10.735 | 7.335 | 2.114 | -1.142 | -3.357 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Consumer Transformation | 0.143 | 0.049 | -0.089 | -0.26 | -0.417 | -0.589 | -0.802 | -1.91 | -3.782 | -5.178 | -6.401 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Consumer Transformation | 6.88 | 1.007 | 0.651 | 0.237 | -0.088 | -0.425 | -0.829 | 6.082 | 3.323 | 1.332 | -0.481 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Consumer Transformation | 3.576 | 3.28 | 2.867 | 2.387 | 2.038 | 1.677 | 1.244 | -0.683 | -4.068 | -6.722 | -9.308 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Consumer Transformation | 12.389 | 12.192 | 11.896 | 11.528 | 11.188 | 10.768 | 10.228 | 6.573 | 1.011 | -2.193 | -4.308 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Consumer Transformation | 5.466 | 5.206 | 4.817 | 4.387 | 4.12 | 3.83 | 3.458 | 1.914 | -0.888 | -2.823 | -4.576 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Consumer Transformation | 0.973 | 0.728 | 0.433 | 0.176 | 0.01 | -0.161 | -0.375 | -1.237 | -2.722 | -3.759 | -4.763 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Consumer Transformation | 12.662 | 12.504 | 12.233 | 11.891 | 11.711 | 11.517 | 11.263 | 10.111 | 7.194 | 5 | 2.915 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Consumer Transformation | 7.188 | 7.25 | 7.294 | 7.326 | 7.365 | 7.396 | 7.408 | 7.435 | 6.179 | 5.199 | 4.325 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Consumer Transformation | 13.482 | 13.413 | 13.276 | 13.083 | 13.022 | 12.952 | 12.857 | 12.321 | 9.858 | 7.936 | 6.072 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Consumer Transformation | 6.917 | 6.518 | 5.971 | 5.337 | 4.779 | 4.197 | 3.495 | 0.344 | -4.02 | -7.324 | -10.33 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Consumer Transformation | 9.736 | 9.693 | 9.558 | 9.341 | 9.204 | 9.003 | 8.72 | 6.623 | 2.95 | 0.787 | -0.746 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Consumer Transformation | 14.74 | 14.777 | 14.809 | 14.835 | 14.861 | 14.886 | 14.908 | 14.995 | 14.874 | 14.78 | 14.693 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Consumer Transformation | 5.552 | 5.531 | 5.494 | 5.45 | 5.425 | 5.397 | 5.357 | 5.181 | 4.891 | 4.687 | 4.477 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Consumer Transformation | 14.005 | 14.041 | 14.053 | 14.037 | 14.038 | 14.035 | 14.019 | 13.937 | 12.793 | 11.908 | 11.111 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Consumer Transformation | 3.989 | 3.669 | 3.171 | 2.561 | 2.187 | 1.799 | 1.324 | -0.677 | -4.684 | -7.628 | -10.412 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Consumer Transformation | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Consumer Transformation | 8.695 | 7.583 | 6.883 | 6.06 | 5.465 | 4.857 | 4.129 | 1.087 | -5.129 | -10.009 | -14.575 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Consumer Transformation | 8.631 | 7.995 | 7.118 | 6.166 | 22.658 | 22.029 | 21.251 | 17.963 | 11.951 | 7.507 | 3.188 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Consumer Transformation | 3.25 | 3.346 | 3.413 | 3.443 | 3.469 | 3.485 | 3.48 | 3.361 | 1.523 | 0.019 | -1.3 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Consumer Transformation | 1.829 | 1.503 | 1.043 | 0.491 | -0.076 | -0.655 | -1.344 | -4.24 | -9.495 | -13.785 | -17.586 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Consumer Transformation | 14.378 | 14.188 | 13.908 | 13.586 | 13.338 | 13.082 | 12.766 | 11.401 | 8.165 | 5.615 | 3.288 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Consumer Transformation | 5.59 | 5.072 | 4.289 | 3.346 | 2.72 | 2.061 | 1.255 | -2.37 | -8.738 | -13.399 | -17.893 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Consumer Transformation | 4.896 | 3.902 | 3.525 | 3.128 | 2.864 | 2.574 | 2.195 | 0.378 | -3.586 | -6.495 | -9.098 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Consumer Transformation | 14.913 | 14.695 | 14.371 | 14.001 | 13.784 | 13.559 | 13.276 | 12.192 | 9.868 | 8.07 | 6.308 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Consumer Transformation | 3.481 | 3.151 | 2.65 | 2.055 | 1.665 | 1.249 | 0.723 | 13.002 | 8.38 | 5.03 | 1.914 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Consumer Transformation | 6.748 | 6.486 | 6.121 | 5.672 | 5.364 | 5.03 | 4.639 | 2.497 | -1.993 | -5.349 | -8.436 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Consumer Transformation | 8.212 | 7.741 | 7.06 | 6.258 | 5.719 | 5.161 | 4.482 | 1.583 | -3.244 | -6.607 | -9.819 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Consumer Transformation | 5.881 | 5.499 | 4.974 | 4.371 | 3.844 | 3.306 | 2.666 | -0.021 | -3.535 | -6.002 | -8.139 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Consumer Transformation | 1.022 | 0.201 | -0.772 | -1.635 | -2.34 | -3.066 | -3.966 | -7.806 | -15.382 | -21.197 | -26.311 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Consumer Transformation | 9.643 | 9.085 | 8.356 | 7.618 | 7.18 | 6.728 | 6.171 | 3.819 | -1.289 | -5.146 | -8.881 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Consumer Transformation | 10.587 | 10.065 | 9.393 | 8.726 | 8.214 | 7.664 | 6.975 | 3.638 | -1.771 | -5.47 | -8.637 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Consumer Transformation | 12.37 | 12.379 | 12.337 | 12.24 | 12.175 | 12.076 | 11.933 | 10.785 | 8.066 | 6.36 | 5.101 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Consumer Transformation | 8.581 | 8.453 | 8.256 | 8.018 | 7.84 | 7.651 | 7.409 | 6.324 | 3.974 | 2.159 | 0.496 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Consumer Transformation | 2.89 | 2.83 | 2.704 | 2.527 | 2.429 | 2.304 | 2.137 | 1.002 | -1.32 | -2.774 | -3.945 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Consumer Transformation | 12.824 | 12.593 | 12.235 | 11.805 | 11.521 | 11.226 | 10.86 | 9.306 | 5.938 | 3.37 | 0.946 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Consumer Transformation | 18.282 | 18.192 | 18.031 | 17.823 | 17.65 | 17.47 | 17.241 | 16.265 | 14.493 | 13.144 | 11.932 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Consumer Transformation | 15.444 | 15.337 | 15.169 | 14.955 | 14.855 | 14.75 | 14.628 | 14.022 | 11.806 | 10.003 | 8.184 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Consumer Transformation | 2.761 | 2.457 | 2.01 | 1.416 | 0.896 | 0.257 | -0.535 | -4.674 | -10.421 | -14.099 | -16.858 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Consumer Transformation | 9.818 | 9.875 | 9.896 | 9.877 | 9.889 | 9.888 | 9.864 | 9.626 | 8.008 | 6.825 | 5.796 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Consumer Transformation | 6.133 | 5.993 | 5.781 | 5.513 | 5.349 | 5.16 | 4.929 | 3.683 | 1.046 | -0.904 | -2.633 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Consumer Transformation | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Consumer Transformation | 6.743 | 6.151 | 5.383 | 4.588 | 4.065 | 3.51 | 2.819 | -0.191 | -5.084 | -8.535 | -11.791 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Consumer Transformation | 14.343 | 14.022 | 13.544 | 12.965 | 12.631 | 12.283 | 11.86 | 9.964 | 5.867 | 2.701 | -0.414 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Consumer Transformation | 3.101 | 2.929 | 2.693 | 2.42 | 2.216 | 2.006 | 1.754 | 0.694 | -1.168 | -2.646 | -4.083 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Consumer Transformation | 8.807 | 8.513 | 8.094 | 7.543 | 7.058 | 6.459 | 5.725 | 0.519 | -7.787 | -12.938 | -16.719 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Consumer Transformation | 13.018 | 12.504 | 11.885 | 11.301 | 10.879 | 10.441 | 9.899 | 7.546 | 3.269 | 0.084 | -2.894 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Consumer Transformation | 4.978 | 4.884 | 4.753 | 4.602 | 4.482 | 4.359 | 4.213 | 3.583 | 2.341 | 1.34 | 0.411 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Consumer Transformation | 6.013 | 5.52 | 4.822 | 3.999 | 3.406 | 2.797 | 2.068 | -0.981 | -7.151 | -12.052 | -16.801 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Consumer Transformation | 9.926 | 9.602 | 9.091 | 8.47 | 8.05 | 7.616 | 7.081 | 4.905 | -0.043 | -3.865 | -7.383 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Consumer Transformation | 15.523 | 15.207 | 14.809 | 14.417 | 14.11 | 13.799 | 13.426 | 11.917 | 8.978 | 6.725 | 4.681 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Consumer Transformation | 6.052 | 5.821 | 5.421 | 4.907 | 4.615 | 4.302 | 3.902 | 2.173 | -2.006 | -5.116 | -8.055 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Consumer Transformation | 12.886 | 12.435 | 11.841 | 11.16 | 10.492 | 9.79 | 8.95 | 5.199 | -0.223 | -4.304 | -7.844 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Consumer Transformation | 12.779 | 12.719 | 12.612 | 12.464 | 12.402 | 12.334 | 12.25 | 11.872 | 10.376 | 9.167 | 7.991 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Consumer Transformation | 9.269 | 8.884 | 8.343 | 7.731 | 7.308 | 6.855 | 6.303 | 3.797 | -0.043 | -2.668 | -5.061 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Consumer Transformation | 11.378 | 11.401 | 11.373 | 11.294 | 11.24 | 11.155 | 11.025 | 10.06 | 8.054 | 6.841 | 5.96 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Consumer Transformation | 5.58 | 5.518 | 5.351 | 5.094 | 4.961 | 4.785 | 4.54 | 2.953 | -0.648 | -3.009 | -4.975 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Consumer Transformation | 28.572 | 28.492 | 28.363 | 28.192 | 28.054 | 27.894 | 27.696 | 26.521 | 24.601 | 23.322 | 22.279 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Consumer Transformation | 3.155 | 2.944 | 2.678 | 2.366 | 2.13 | 1.881 | 1.605 | 0.063 | -3.879 | -7.338 | -10.639 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Consumer Transformation | 1.898 | 1.858 | 1.797 | 1.723 | 1.66 | 1.595 | 1.515 | 1.168 | 0.718 | 0.372 | 0.045 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Consumer Transformation | 11.602 | 11.266 | 10.815 | 10.306 | 9.943 | 9.565 | 9.113 | 7.105 | 3.136 | 0.052 | -2.904 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Consumer Transformation | 9.904 | 9.912 | 9.874 | 9.797 | 9.781 | 9.751 | 9.694 | 9.323 | 7.743 | 6.553 | 5.463 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Consumer Transformation | 10.722 | 10.654 | 10.498 | 10.263 | 10.139 | 10.004 | 9.831 | 8.907 | 4.087 | 0.043 | -3.728 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Consumer Transformation | 1.808 | 1.741 | 1.644 | 1.517 | 1.419 | 1.307 | 1.174 | 0.46 | -0.929 | -1.962 | -2.871 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Consumer Transformation | 11.889 | 11.911 | 11.887 | 11.8 | 11.67 | 11.475 | 11.208 | 8.943 | 5.1 | 2.97 | 1.753 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Consumer Transformation | 15.668 | 15.62 | 15.544 | 15.464 | 15.415 | 15.355 | 15.268 | 14.795 | 13.564 | 12.697 | 11.934 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Consumer Transformation | 7.716 | 6.496 | 5.81 | 5.002 | 4.365 | 3.705 | 2.919 | -0.378 | -6.522 | -11.406 | -15.994 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Consumer Transformation | 11.956 | 11.848 | 11.656 | 11.417 | 11.249 | 11.074 | 10.845 | 9.887 | 7.66 | 5.944 | 4.388 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Consumer Transformation | 15.95 | 16.027 | 16.016 | 15.91 | 15.736 | 15.455 | 15.044 | 11.555 | 6.759 | 4.517 | 3.609 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Consumer Transformation | 8.707 | 8.303 | 7.669 | 6.906 | 6.475 | 6.019 | 5.443 | 2.782 | -3.341 | -7.881 | -12.184 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Consumer Transformation | 4.245 | 4.186 | 4.098 | 3.993 | 3.917 | 3.837 | 3.739 | 3.301 | 2.544 | 1.959 | 1.401 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Consumer Transformation | 8.767 | 8.355 | 7.798 | 7.214 | 6.886 | 6.541 | 6.106 | 4.257 | -0.057 | -3.282 | -6.31 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 14.463 | 14.298 | 14.038 | 13.7 | 13.475 | 13.229 | 12.933 | 11.397 | 7.582 | 4.551 | 1.694 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 13.453 | 13.334 | 13.131 | 12.842 | 12.647 | 12.43 | 12.17 | 10.68 | 6.004 | 2.179 | -1.426 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Consumer Transformation | 12.308 | 12.32 | 12.297 | 12.241 | 12.214 | 12.175 | 12.109 | 11.676 | 10.054 | 8.93 | 7.99 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Consumer Transformation | 8.127 | 8.165 | 8.158 | 8.113 | 8.143 | 8.168 | 8.179 | 8.188 | 6.876 | 5.794 | 4.721 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Consumer Transformation | 17.505 | 17.371 | 17.165 | 16.915 | 16.753 | 16.583 | 16.375 | 15.463 | 13.858 | 12.742 | 11.692 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Consumer Transformation | 4.959 | 4.962 | 4.95 | 4.921 | 4.884 | 4.833 | 4.766 | 4.247 | 3.294 | 2.543 | 1.905 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Consumer Transformation | 2.15 | 1.649 | 1.003 | 0.361 | -0.048 | -0.469 | -0.991 | -3.23 | -8.105 | -11.779 | -15.237 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Consumer Transformation | 11.44 | 11.026 | 10.489 | 9.939 | 9.539 | 9.129 | 8.63 | 6.521 | 2.176 | -1.125 | -4.156 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Consumer Transformation | 10 | 9.484 | 8.774 | 8.01 | 7.521 | 6.995 | 6.341 | 3.108 | -2.96 | -7.115 | -10.77 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 13.005 | 13.027 | 13.013 | 12.959 | 12.906 | 12.824 | 12.701 | 11.734 | 9.971 | 8.993 | 8.387 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Consumer Transformation | 16.033 | 15.814 | 15.472 | 15.06 | 14.801 | 14.532 | 14.198 | 12.786 | 10.06 | 8.042 | 6.118 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Consumer Transformation | 12.841 | 12.731 | 12.531 | 12.264 | 12.039 | 11.8 | 11.49 | 10.138 | 6.968 | 4.512 | 2.367 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Consumer Transformation | 9.381 | 9.124 | 8.717 | 8.221 | 7.892 | 7.531 | 7.072 | 4.792 | 0.528 | -2.403 | -4.992 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Consumer Transformation | 11.541 | 9.833 | 9.592 | 9.276 | 9.085 | 8.887 | 8.631 | 7.649 | 5.004 | 2.909 | 0.902 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Consumer Transformation | 4.113 | 3.987 | 3.817 | 3.629 | 3.468 | 3.3 | 3.096 | 2.217 | 0.859 | -0.156 | -1.077 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Consumer Transformation | 13.895 | 13.429 | 12.766 | 12.013 | 11.46 | 10.885 | 10.172 | 7.113 | 2.155 | -1.529 | -5.023 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Consumer Transformation | 2.146 | 1.783 | 1.203 | 0.499 | -0.034 | -0.587 | -1.278 | -4.194 | -10.682 | -15.71 | -20.25 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Consumer Transformation | 14.574 | 14.285 | 13.868 | 13.402 | 13.075 | 12.733 | 12.306 | 10.453 | 7.217 | 4.868 | 2.669 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Consumer Transformation | 7.596 | 7.139 | 6.484 | 5.743 | 5.266 | 4.772 | 4.163 | 1.567 | -4.003 | -8.237 | -12.338 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Consumer Transformation | 18.619 | 18.678 | 18.657 | 18.557 | 18.522 | 18.465 | 18.361 | 17.663 | 13.914 | 10.951 | 8.279 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Consumer Transformation | 12.532 | 12.379 | 12.165 | 11.923 | 11.719 | 11.504 | 11.239 | 10.045 | 8.075 | 6.748 | 5.658 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Consumer Transformation | 3.311 | 2.967 | 2.462 | 1.856 | 1.413 | 0.944 | 0.368 | -2.329 | -7.191 | -10.858 | -14.282 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Consumer Transformation | 3.371 | 2.435 | 1.211 | -0.163 | -1.574 | -3.028 | -4.752 | -12.227 | -22.07 | -29.43 | -35.625 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Consumer Transformation | 3.879 | 3.43 | 2.824 | 2.186 | 1.682 | 1.158 | 0.51 | 14.953 | 9.429 | 5.056 | 1.097 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Consumer Transformation | 12.472 | 11.956 | 11.249 | 10.445 | 9.899 | 9.344 | 8.687 | 5.921 | 1.12 | -2.546 | -6.159 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Consumer Transformation | 21.734 | 18.78 | 18.889 | 18.975 | 19.054 | 19.131 | 19.206 | 19.4 | 19.199 | 19.037 | 18.895 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Consumer Transformation | 3.464 | 3.174 | 2.77 | 2.266 | 1.835 | 1.315 | 0.683 | -2.909 | -8.101 | -11.45 | -14.048 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Consumer Transformation | 12.599 | 12.471 | 12.249 | 11.973 | 11.899 | 11.815 | 11.701 | 11.093 | 7.843 | 5.183 | 2.5 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Consumer Transformation | 14.045 | 14.115 | 14.164 | 14.198 | 14.26 | 14.317 | 14.364 | 14.541 | 14.258 | 14.041 | 13.809 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Consumer Transformation | 15.001 | 15.046 | 15.067 | 15.061 | 15.082 | 15.098 | 15.1 | 15.088 | 14.293 | 13.666 | 13.07 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Consumer Transformation | 9.622 | 9.043 | 8.209 | 7.233 | 6.55 | 5.848 | 5.002 | 1.416 | -4.471 | -8.789 | -12.891 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Consumer Transformation | 15.789 | 15.7 | 15.563 | 15.386 | 15.304 | 15.213 | 15.105 | 14.457 | 12.016 | 9.988 | 8.025 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Consumer Transformation | 5.503 | 5.428 | 5.268 | 5.04 | 4.95 | 4.85 | 4.714 | 4.006 | 0.459 | -2.372 | -5.067 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Consumer Transformation | 13.995 | 13.813 | 13.53 | 13.186 | 12.93 | 12.659 | 12.32 | 10.812 | 8.059 | 6.097 | 4.333 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Consumer Transformation | 18.289 | 14.827 | 14.751 | 14.664 | 14.602 | 14.533 | 14.435 | 14.116 | 13.742 | 13.526 | 13.35 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Consumer Transformation | 11.555 | 11.318 | 10.991 | 10.629 | 10.383 | 10.125 | 9.813 | 8.386 | 5.905 | 4.078 | 2.329 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Consumer Transformation | 2.514 | 2.31 | 2.017 | 1.665 | 1.4 | 1.106 | 0.748 | -1.22 | -4.234 | -6.206 | -7.836 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Consumer Transformation | 10.876 | 10.49 | 9.955 | 9.38 | 9.021 | 8.652 | 8.197 | 6.343 | 3.099 | 0.74 | -1.633 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Consumer Transformation | 10.027 | 9.703 | 9.2 | 8.599 | 8.231 | 7.844 | 7.356 | 6.354 | 2.418 | -0.472 | -3.2 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Consumer Transformation | 5.756 | 5.549 | 5.239 | 4.818 | 4.437 | 3.989 | 3.445 | 0.376 | -5.232 | -9.309 | -12.66 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Consumer Transformation | 16.366 | 16.218 | 16.013 | 15.771 | 15.566 | 15.354 | 15.101 | 13.928 | 11.878 | 10.265 | 8.792 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Consumer Transformation | 8.851 | 7.05 | 6.578 | 5.981 | 5.556 | 5.073 | 4.499 | 8.174 | 1.172 | -4.03 | -8.521 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Consumer Transformation | 3.793 | 3.639 | 3.427 | 3.184 | 2.984 | 2.778 | 2.531 | 1.47 | -0.053 | -1.208 | -2.295 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Consumer Transformation | 14.348 | 14.031 | 13.553 | 12.985 | 12.578 | 12.157 | 11.64 | 9.472 | 6.033 | 3.634 | 1.445 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Consumer Transformation | -0.33 | -0.564 | -0.892 | -0.277 | -0.608 | -0.958 | -1.385 | -3.214 | -6.314 | -8.672 | -10.779 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Consumer Transformation | 9.18 | 8.836 | 8.34 | 7.758 | 7.314 | 6.852 | 6.295 | 3.804 | -1.124 | -4.964 | -8.571 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Consumer Transformation | 7.709 | 7.391 | 6.893 | 6.287 | 5.883 | 5.454 | 4.91 | 2.45 | -2.471 | -6.079 | -9.43 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Consumer Transformation | 4.98 | 4.486 | 3.782 | 2.945 | 2.332 | 1.693 | 0.922 | -2.446 | -9.236 | -14.59 | -19.748 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Consumer Transformation | 16.065 | 15.737 | 15.241 | 14.646 | 14.218 | 13.761 | 13.188 | 10.699 | 6.682 | 3.885 | 1.347 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Consumer Transformation | 7.887 | 7.935 | 7.928 | 7.87 | 7.869 | 7.85 | 7.801 | 7.388 | 5.445 | 4.072 | 2.897 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Consumer Transformation | 13.808 | 14.507 | 14.104 | 5.662 | 4.89 | 4.097 | 3.146 | 0.138 | -4.177 | -7.717 | -10.906 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Consumer Transformation | 10.928 | 10.475 | 9.836 | 9.083 | 8.462 | 7.818 | 7.049 | 3.629 | -1.68 | -5.583 | -9.101 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Consumer Transformation | 6.627 | 6.646 | 6.589 | 6.461 | 6.442 | 6.405 | 6.331 | 5.956 | 4.046 | 2.561 | 1.173 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Consumer Transformation | 11.735 | 11.303 | 10.685 | 9.969 | 9.488 | 8.995 | 8.391 | 5.85 | 1.225 | -2.211 | -5.487 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Consumer Transformation | 5.082 | 4.559 | 3.844 | 2.988 | 2.255 | 1.467 | 0.522 | -4.282 | -12.007 | -17.835 | -23.118 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Consumer Transformation | 10.367 | 10.465 | 10.556 | 10.636 | 10.711 | 10.782 | 10.849 | 11.136 | 11.03 | 10.955 | 10.891 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Consumer Transformation | 11.314 | 11.427 | 11.518 | 11.581 | 11.62 | 11.635 | 11.619 | 11.21 | 10.232 | 9.779 | 9.596 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Consumer Transformation | 2.512 | 2.599 | 2.675 | 2.739 | 2.802 | 2.859 | 2.907 | 3.087 | 2.843 | 2.692 | 2.576 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Consumer Transformation | 6.382 | 6.159 | 5.844 | 5.506 | 5.291 | 5.065 | 4.776 | 3.697 | 1.667 | 0.232 | -1.051 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Consumer Transformation | 0.596 | 0.394 | 0.134 | -0.148 | -0.4 | -0.663 | -0.978 | -2.444 | -4.537 | -6.064 | -7.388 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Consumer Transformation | 12.483 | 12.232 | 11.857 | 11.398 | 11.026 | 10.625 | 10.137 | 7.778 | 4.005 | 1.365 | -0.865 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Consumer Transformation | 12.914 | 11.021 | 11.036 | 10.993 | 10.937 | 10.852 | 10.719 | 10.134 | 8.592 | 7.483 | 6.585 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Consumer Transformation | 9.167 | 8.787 | 15.291 | 14.794 | 14.433 | 14.058 | 13.587 | 11.568 | 7.746 | 4.887 | 2.243 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Consumer Transformation | 10.089 | 9.968 | 9.789 | 9.558 | 9.422 | 9.264 | 9.075 | 7.793 | 4.363 | 1.7 | -0.722 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Consumer Transformation | 3.159 | 1.421 | 0.858 | 0.409 | 0.081 | -0.264 | -0.699 | -2.628 | -7.52 | -11.395 | -14.939 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Consumer Transformation | 12.591 | 12.569 | 12.522 | 12.455 | 12.428 | 12.398 | 12.359 | 12.124 | 11.041 | 10.091 | 9.14 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Consumer Transformation | 8.414 | 8.255 | 14.963 | 14.589 | 14.397 | 14.187 | 13.911 | 12.6 | 8.941 | 6.22 | 3.659 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Consumer Transformation | 4.912 | 3.606 | 2.883 | 2.292 | 1.813 | 1.301 | 0.672 | -2.2 | -7.209 | -10.895 | -14.163 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Consumer Transformation | 10.168 | 9.694 | 8.989 | 8.162 | 7.667 | 7.158 | 6.537 | 3.923 | -1.553 | -5.687 | -9.742 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Consumer Transformation | 10.291 | 10.128 | 7.723 | 7.329 | 6.969 | 6.508 | 5.927 | 2.155 | -2.956 | -5.91 | -7.876 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Consumer Transformation | 8.308 | 7.839 | 7.181 | 6.421 | 5.88 | 5.311 | 4.619 | 1.49 | -3.28 | -6.674 | -9.828 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Consumer Transformation | 6.814 | 4.769 | 4.08 | 3.326 | 2.843 | 2.335 | 1.704 | -0.742 | -5.74 | -9.511 | -13.031 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Consumer Transformation | 8.566 | 7.931 | 8.017 | 8.046 | 8.053 | 8.029 | 7.969 | 7.33 | 5.266 | 3.97 | 3.06 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Consumer Transformation | 18.762 | 18.74 | 18.682 | 18.583 | 18.469 | 18.314 | 18.11 | 16.594 | 14.314 | 13.095 | 12.407 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Consumer Transformation | 8.659 | 8.539 | 8.305 | 8.004 | 7.842 | 7.671 | 7.442 | 6.479 | 3.704 | 1.54 | -0.575 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Consumer Transformation | 10.724 | 10.559 | 10.305 | 9.994 | 9.671 | 9.324 | 8.894 | 6.868 | 3.526 | 1.001 | -1.101 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Consumer Transformation | 12.026 | 11.747 | 11.307 | 10.764 | 10.436 | 10.096 | 9.674 | 7.93 | 3.657 | 0.381 | -2.74 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Consumer Transformation | 12.305 | 12.288 | 12.219 | 12.111 | 12.079 | 12.033 | 11.963 | 11.521 | 9.798 | 8.571 | 7.453 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Consumer Transformation | 8.382 | 8.507 | 8.622 | 8.736 | 8.845 | 8.946 | 9.032 | 9.386 | 9.06 | 8.819 | 8.604 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Consumer Transformation | 8.061 | 6.234 | 6.039 | 5.791 | 5.726 | 5.638 | 5.504 | 4.644 | 1.465 | -0.903 | -3.115 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Consumer Transformation | 9.953 | 8.787 | 8.87 | 8.923 | 8.981 | 9.033 | 9.069 | 9.205 | 8.433 | 7.844 | 7.312 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Consumer Transformation | 1.194 | 0.979 | 0.686 | 0.346 | 0.084 | -0.189 | -0.52 | -1.976 | -4.478 | -6.445 | -8.332 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 2.858 | 2.816 | 2.747 | 2.671 | 2.657 | 2.64 | 2.614 | 2.484 | 1.573 | 0.837 | 0.066 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Consumer Transformation | 12.893 | 12.801 | 12.651 | 12.449 | 12.283 | 12.082 | 11.83 | 10.157 | 7.371 | 5.624 | 4.298 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Consumer Transformation | 24.496 | 24.549 | 24.593 | 24.617 | 24.635 | 24.65 | 24.663 | 24.677 | 24.05 | 23.473 | 22.911 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Consumer Transformation | 13.817 | 13.849 | 13.846 | 13.815 | 13.82 | 13.822 | 13.806 | 13.751 | 12.795 | 12.018 | 11.275 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Consumer Transformation | -1.724 | -1.826 | -1.979 | -2.181 | -2.344 | -2.522 | -2.734 | -3.906 | -6.333 | -8.282 | -10.065 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Consumer Transformation | 3.267 | 3.016 | 2.658 | 2.183 | 1.781 | 1.299 | 0.714 | -3.092 | -10.137 | -15.034 | -19.052 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Consumer Transformation | 10.983 | 10.799 | 10.482 | 10.087 | 9.839 | 9.582 | 9.255 | 7.891 | 4.681 | 2.256 | -0.035 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Consumer Transformation | 11.365 | 11.479 | 11.578 | 11.658 | 11.724 | 11.773 | 11.801 | 11.738 | 11.409 | 11.337 | 11.397 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Consumer Transformation | 8.092 | 7.668 | 7.041 | 6.29 | 5.753 | 5.183 | 4.488 | 1.178 | -5.269 | -10.019 | -14.284 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Consumer Transformation | 11.761 | 11.019 | 10.8 | 10.521 | 10.356 | 10.185 | 9.989 | 9.258 | 6.672 | 4.409 | 2.2 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Consumer Transformation | 4.022 | 3.672 | 3.232 | 2.804 | 2.457 | 2.105 | 1.678 | -0.078 | -3.578 | -6.307 | -8.761 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Consumer Transformation | 10.979 | 10.79 | 10.459 | 10.032 | 9.715 | 9.386 | 8.972 | 7.186 | 3.011 | -0.308 | -3.395 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Consumer Transformation | -1.253 | -1.458 | -1.751 | -2.09 | -0.32 | -0.558 | -0.848 | -2.114 | -5.224 | -7.673 | -9.99 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Consumer Transformation | 15.296 | 15.249 | 15.165 | 15.036 | 14.911 | 14.761 | 14.575 | 13.363 | 10.645 | 8.694 | 7.099 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Consumer Transformation | 14.301 | 13.6 | 12.898 | 12.439 | 12.058 | 11.656 | 11.159 | 8.807 | 4.551 | 1.433 | -1.259 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Consumer Transformation | 10.055 | 9.666 | 9.068 | 8.358 | 7.919 | 7.46 | 6.892 | 4.46 | 0.132 | -2.965 | -6.015 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Consumer Transformation | 23.77 | 23.817 | 23.86 | 23.902 | 23.945 | 23.983 | 24.016 | 24.15 | 23.949 | 23.791 | 23.645 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Consumer Transformation | 8.536 | 8.583 | 8.623 | 8.654 | 8.68 | 8.703 | 8.718 | 8.757 | 7.826 | 7.078 | 6.415 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Consumer Transformation | 11.258 | 10.951 | 10.469 | 9.884 | 9.53 | 9.166 | 8.715 | 6.849 | 3.09 | 0.268 | -2.522 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Consumer Transformation | 4.365 | 4.353 | 4.332 | 4.302 | 4.291 | 4.277 | 4.261 | 4.152 | 3.77 | 3.426 | 3.08 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Consumer Transformation | 8.841 | 8.737 | 8.586 | 8.397 | 8.27 | 8.133 | 7.974 | 7.124 | 4.906 | 3.08 | 1.323 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Consumer Transformation | 13.835 | 13.55 | 13.12 | 12.615 | 12.291 | 11.957 | 11.541 | 9.759 | 5.846 | 2.781 | -0.188 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Consumer Transformation | 10.748 | 10.43 | 9.983 | 9.454 | 9.069 | 8.669 | 8.196 | 6.205 | 2.569 | -0.167 | -2.676 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Consumer Transformation | 7.775 | 7.378 | 6.819 | 6.156 | 5.549 | 4.917 | 4.158 | 0.862 | -3.812 | -7.225 | -10.195 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Consumer Transformation | 13.085 | 12.849 | 12.556 | 12.207 | 11.892 | 11.546 | 11.152 | 8.957 | 4.919 | 1.738 | -1.082 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Consumer Transformation | 7.745 | 7.725 | 7.622 | 7.444 | 7.325 | 7.172 | 6.961 | 5.546 | 1.28 | -1.858 | -4.488 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Consumer Transformation | 13.753 | 13.488 | 13.082 | 12.6 | 12.31 | 12.009 | 11.636 | 10.071 | 6.815 | 4.367 | 1.95 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Consumer Transformation | 7.158 | 6.699 | 6.102 | 5.501 | 5.064 | 4.611 | 4.05 | 18.723 | 13.61 | 9.624 | 5.941 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Consumer Transformation | 7.478 | 7.321 | 7.1 | 6.814 | 6.61 | 6.385 | 6.122 | 4.636 | 0.715 | -2.464 | -5.481 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Falling Short | 13.258 | 13.144 | 13.066 | 13.028 | 12.974 | 12.906 | 12.839 | 12.538 | 12.315 | 12.158 | 12.017 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Falling Short | 12.218 | 10.599 | 10.566 | 10.502 | 10.4 | 10.26 | 10.089 | 9.026 | 7.732 | 6.822 | 6.5 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Falling Short | 11.455 | 11.165 | 10.83 | 10.443 | 9.996 | 9.495 | 9.001 | 6.672 | 4.678 | 3.254 | 2.136 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Falling Short | 5.901 | 4.525 | 4.545 | 4.527 | 4.474 | 4.391 | 4.293 | 3.765 | 3.166 | 2.762 | 2.609 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 15.57 | 15.372 | 15.153 | 14.917 | 14.622 | 14.271 | 13.938 | 12.619 | 11.849 | 11.451 | 11.215 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 17.119 | 17.119 | 17.114 | 17.104 | 17.084 | 17.055 | 17.027 | 16.903 | 16.812 | 16.753 | 16.711 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Falling Short | 9.108 | 8.783 | 8.404 | 7.971 | 7.459 | 6.879 | 6.314 | 3.777 | 1.642 | 0.067 | -1.171 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Falling Short | 17.141 | 17.169 | 17.187 | 17.189 | 17.176 | 17.151 | 17.126 | 17.02 | 16.915 | 16.844 | 16.791 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Falling Short | 1.013 | 0.842 | 0.634 | 0.385 | 0.087 | -0.255 | -0.592 | -2.121 | -3.345 | -4.198 | -4.838 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Falling Short | 3.204 | 2.645 | 2.724 | 2.783 | 2.826 | 2.857 | 2.882 | 2.925 | 2.861 | 2.798 | 2.747 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Falling Short | 11.991 | 11.852 | 11.673 | 11.451 | 11.178 | 10.86 | 10.55 | 10.231 | 9.202 | 8.471 | 7.933 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Falling Short | 2.721 | 2.575 | 2.407 | 2.206 | 1.935 | 1.599 | 1.254 | -0.415 | -1.981 | -2.991 | -3.454 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Falling Short | 3.284 | 3.258 | 3.227 | 3.19 | 3.148 | 3.101 | 3.051 | 2.812 | 2.566 | 2.343 | 2.154 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Falling Short | 15.767 | 15.697 | 15.597 | 15.467 | 15.296 | 15.092 | 14.897 | 14.101 | 13.568 | 13.27 | 13.081 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Falling Short | 12.952 | 12.402 | 12.341 | 12.269 | 12.187 | 12.096 | 12.004 | 11.567 | 11.141 | 10.73 | 10.321 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Falling Short | 10.545 | 10.553 | 10.544 | 10.511 | 10.453 | 10.375 | 10.291 | 9.833 | 9.319 | 8.966 | 8.79 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Falling Short | 15.618 | 15.412 | 15.158 | 14.854 | 14.484 | 14.051 | 13.621 | 11.632 | 9.967 | 8.848 | 8.168 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Falling Short | 8.301 | 8.312 | 8.312 | 8.301 | 8.276 | 8.239 | 8.196 | 7.907 | 7.545 | 7.293 | 7.193 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Falling Short | 5.673 | 5.5 | 5.306 | 5.083 | 4.834 | 4.564 | 4.293 | 2.978 | 1.751 | 0.706 | -0.266 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Falling Short | 21.394 | 21.363 | 21.31 | 21.233 | 21.13 | 21.004 | 20.881 | 20.386 | 20.086 | 19.914 | 19.804 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Falling Short | 3.597 | 3.457 | 3.308 | 3.15 | 2.98 | 2.799 | 2.617 | 1.704 | 0.799 | -0.044 | -0.84 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Falling Short | 11.547 | 11.239 | 10.871 | 10.44 | 9.923 | 9.328 | 8.733 | 5.881 | 3.304 | 1.409 | 0.065 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Falling Short | 9.566 | 9.339 | 9.069 | 8.756 | 8.358 | 7.884 | 7.423 | 5.651 | 4.53 | 3.897 | 3.569 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Falling Short | 14.743 | 14.58 | 14.396 | 14.19 | 13.938 | 13.643 | 13.36 | 12.19 | 11.473 | 11.082 | 10.811 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Falling Short | 2.902 | 2.906 | 2.874 | 2.801 | 2.68 | 2.514 | 2.329 | 1.25 | 0.003 | -0.866 | -1.245 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Falling Short | 5.333 | 5.151 | 4.935 | 4.684 | 4.389 | 4.05 | 3.709 | 2.057 | 0.508 | -0.699 | -1.561 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 15.152 | 15.124 | 15.087 | 15.033 | 14.961 | 14.874 | 14.781 | 14.392 | 14.063 | 13.841 | 13.725 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 4.16 | 1.162 | 1.126 | 1.045 | 0.913 | 0.733 | 0.521 | -0.717 | -2.146 | -3.138 | -3.551 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Falling Short | 7.332 | 7.235 | 7.104 | 6.931 | 6.711 | 6.446 | 6.155 | 4.474 | 2.561 | 1.126 | 0.325 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Falling Short | 11.753 | 11.595 | 11.387 | 11.131 | 10.812 | 10.436 | 10.072 | 8.553 | 7.556 | 6.98 | 6.602 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Falling Short | 5.834 | 5.563 | 5.219 | 4.799 | 4.277 | 3.659 | 3.044 | 0.206 | -2.167 | -3.764 | -4.705 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Falling Short | 6.867 | 6.847 | 6.825 | 6.802 | 6.776 | 6.748 | 6.721 | 6.589 | 6.461 | 6.346 | 6.237 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Falling Short | 3.66 | 3.617 | 3.567 | 3.509 | 3.441 | 3.364 | 3.286 | 2.881 | 2.473 | 2.138 | 1.88 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Falling Short | 11.669 | 11.492 | 11.262 | 10.976 | 10.62 | 10.202 | 9.794 | 8.047 | 6.705 | 5.82 | 5.224 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 13.345 | 13.153 | 12.957 | 12.754 | 12.546 | 12.336 | 12.123 | 11.04 | 9.89 | 8.718 | 7.53 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Falling Short | 4.636 | 4.564 | 4.479 | 4.381 | 4.263 | 4.128 | 3.998 | 3.438 | 3.008 | 2.706 | 2.481 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 9.495 | 9.351 | 9.156 | 8.907 | 8.582 | 8.192 | 7.816 | 6.249 | 5.168 | 4.551 | 4.183 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Falling Short | 11.609 | 11.463 | 11.27 | 11.025 | 10.706 | 10.319 | 9.94 | 8.299 | 7.093 | 6.396 | 6.079 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Falling Short | 9.218 | 9.242 | 9.249 | 9.237 | 9.204 | 9.152 | 9.092 | 8.723 | 8.282 | 7.966 | 7.799 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Falling Short | 10.149 | 10.148 | 10.124 | 10.073 | 9.989 | 9.878 | 9.769 | 9.327 | 9 | 8.809 | 8.706 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Falling Short | 17.487 | 17.383 | 17.252 | 17.094 | 16.897 | 16.664 | 16.428 | 15.319 | 14.304 | 13.595 | 13.199 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Falling Short | 7.725 | 22.316 | 22.181 | 22.015 | 21.805 | 21.555 | 21.315 | 20.307 | 19.634 | 19.256 | 19.025 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Falling Short | 10.13 | 9.798 | 9.397 | 8.926 | 8.368 | 7.733 | 7.122 | 21.691 | 19.902 | 18.652 | 17.616 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Falling Short | 3.898 | 3.842 | 3.777 | 3.705 | 3.612 | 3.5 | 3.394 | 3.001 | 2.778 | 2.663 | 2.596 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Falling Short | 6.35 | 5.831 | 5.243 | 4.598 | 3.81 | 2.889 | 1.979 | -1.49 | -3.654 | -4.948 | -5.717 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Falling Short | 3.68 | 3.306 | 2.859 | 2.33 | 1.7 | 0.98 | 0.271 | -2.992 | -5.704 | -7.645 | -9.083 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Falling Short | 5.019 | 4.579 | 4.051 | 3.433 | 2.703 | 1.871 | 1.059 | 21.609 | 18.907 | 16.944 | 15.41 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Falling Short | 4.005 | 4.033 | 4.056 | 4.071 | 4.078 | 4.08 | 4.075 | 3.992 | 3.832 | 3.699 | 3.626 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Falling Short | 8.003 | 7.752 | 7.418 | 6.998 | 6.465 | 5.823 | 5.16 | 18.822 | 15.619 | 13.44 | 12.398 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Falling Short | 12.712 | 12.754 | 12.789 | 12.81 | 12.821 | 12.824 | 12.822 | 12.724 | 12.516 | 12.364 | 12.3 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Falling Short | 9.372 | 9.445 | 9.511 | 9.569 | 9.62 | 9.666 | 9.708 | 9.842 | 9.89 | 9.905 | 9.905 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Falling Short | 10.951 | 11.006 | 11.054 | 11.088 | 11.097 | 11.088 | 11.073 | 10.925 | 10.684 | 10.512 | 10.408 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Falling Short | 8.911 | 8.95 | 8.98 | 8.997 | 8.998 | 8.987 | 8.974 | 8.891 | 8.788 | 8.716 | 8.668 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Falling Short | 10.854 | 10.731 | 10.559 | 10.338 | 10.043 | 9.676 | 9.298 | 7.435 | 5.641 | 4.46 | 3.971 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Falling Short | 5.08 | 5.022 | 4.952 | 4.869 | 4.769 | 4.653 | 4.542 | 4.068 | 3.717 | 3.451 | 3.234 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Falling Short | 7.437 | 7.326 | 7.205 | 7.075 | 6.932 | 6.779 | 6.624 | 5.828 | 5.009 | 4.183 | 3.351 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Falling Short | 13.287 | 13.039 | 12.761 | 12.455 | 12.068 | 11.608 | 11.162 | 9.307 | 8.062 | 7.372 | 7.02 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Falling Short | 0.747 | 0.719 | 0.686 | 0.647 | 0.602 | 0.551 | 0.498 | 0.212 | -0.102 | -0.396 | -0.655 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Falling Short | 2.452 | 2.307 | 2.139 | 1.945 | 1.713 | 1.448 | 1.192 | 0.081 | -0.776 | -1.378 | -1.843 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 9.601 | 9.532 | 9.417 | 9.254 | 9.036 | 8.765 | 8.488 | 7.086 | 5.617 | 4.576 | 4.012 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Falling Short | 8.423 | 8.358 | 8.29 | 8.214 | 8.102 | 7.961 | 7.824 | 7.249 | 6.826 | 6.575 | 6.423 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Falling Short | 5.166 | 4.933 | 4.668 | 4.366 | 4.013 | 3.616 | 3.22 | 1.404 | -0.175 | -1.394 | -2.349 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Falling Short | 4.163 | 4.174 | 4.183 | 4.186 | 4.185 | 4.179 | 4.17 | 4.087 | 3.965 | 3.879 | 3.844 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Falling Short | 21.976 | 21.894 | 21.796 | 21.681 | 21.53 | 21.349 | 21.176 | 20.473 | 20.023 | 19.78 | 19.627 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Falling Short | 7.346 | 7.384 | 7.417 | 7.439 | 7.444 | 7.437 | 7.428 | 7.351 | 7.228 | 7.14 | 7.078 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Falling Short | 13.152 | 12.98 | 12.797 | 12.603 | 12.354 | 12.055 | 11.768 | 10.622 | 9.921 | 9.552 | 9.343 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Falling Short | 8.381 | 8.369 | 8.331 | 8.258 | 8.145 | 7.999 | 7.854 | 7.185 | 6.639 | 6.329 | 6.187 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Falling Short | 2.459 | 2.099 | 1.67 | 1.175 | 0.547 | -0.2 | -0.927 | -3.917 | -5.921 | -7.062 | -7.674 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Falling Short | 0.942 | 0.792 | 0.629 | 0.445 | 0.24 | 0.016 | -0.213 | -0.91 | -1.309 | -1.648 | -1.922 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Falling Short | 2.67 | 2.495 | 2.301 | 2.08 | 1.829 | 1.551 | 1.258 | -0.365 | -2.172 | -3.723 | -4.914 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Falling Short | 12.931 | 12.889 | 12.813 | 12.703 | 12.551 | 12.363 | 12.181 | 12.502 | 12.088 | 11.868 | 11.768 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Falling Short | 14.51 | 14.418 | 15.282 | 15.1 | 14.865 | 14.581 | 14.309 | 13.194 | 12.479 | 12.113 | 11.914 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Falling Short | 22.062 | 22.048 | 21.993 | 21.875 | 21.687 | 21.427 | 21.105 | 18.913 | 16.05 | 14.063 | 13.438 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Falling Short | 9.728 | 9.478 | 9.187 | 8.853 | 8.464 | 8.027 | 7.594 | 12.583 | 10.861 | 9.537 | 8.472 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Falling Short | 1.99 | 1.821 | 1.614 | 1.365 | 1.063 | 0.714 | 0.369 | -1.025 | -2.067 | -2.771 | -3.234 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Falling Short | 7.999 | 7.833 | 7.595 | 7.287 | 6.895 | 6.429 | 5.983 | 4.164 | 3.052 | 2.454 | 2.057 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Falling Short | 5.189 | 2.869 | 2.849 | 2.81 | 2.751 | 2.674 | 2.588 | 2.165 | 1.744 | 1.459 | 1.324 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Falling Short | 7.612 | 7.387 | 7.095 | 6.737 | 6.282 | 5.741 | 5.219 | 3.086 | 1.668 | 0.863 | 0.397 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Falling Short | 3.421 | 3.256 | 17.74 | 17.474 | 17.133 | 16.726 | 16.325 | 14.556 | 13.227 | 12.448 | 12.055 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Falling Short | -0.481 | -0.6 | -0.739 | -0.901 | -1.09 | -1.303 | -1.51 | -2.412 | -3.117 | -3.654 | -4.112 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Falling Short | 2.519 | 2.527 | 2.528 | 2.518 | 2.499 | 2.471 | 2.439 | 2.252 | 2.026 | 1.87 | 1.799 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Falling Short | 10.381 | 10.217 | 9.996 | 9.718 | 9.368 | 8.951 | 8.552 | 6.93 | 5.924 | 5.39 | 5.067 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Falling Short | 8.324 | 8.176 | 7.974 | 7.716 | 7.384 | 6.985 | 6.591 | 4.852 | 3.453 | 2.578 | 2.098 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Falling Short | 11.148 | 11.047 | 10.918 | 10.759 | 10.563 | 10.331 | 10.098 | 8.972 | 7.927 | 7.133 | 6.562 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Falling Short | 3.457 | 2.498 | 2.503 | 2.477 | 2.414 | 2.317 | 2.201 | 1.482 | 0.617 | 0.01 | -0.232 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Falling Short | 14.789 | 14.68 | 14.557 | 14.41 | 14.241 | 14.048 | 13.84 | 12.596 | 11.097 | 9.865 | 9.037 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Falling Short | 4.439 | 4.374 | 4.296 | 4.205 | 4.098 | 3.976 | 3.857 | 3.333 | 2.921 | 2.619 | 2.372 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Falling Short | 2.063 | 2.028 | 1.979 | 1.916 | 1.833 | 1.735 | 1.64 | 1.253 | 1.003 | 0.866 | 0.779 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Falling Short | 14.974 | 14.75 | 14.475 | 14.142 | 13.734 | 13.256 | 12.775 | 10.497 | 8.489 | 7.072 | 6.172 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Falling Short | 2.716 | 2.623 | 4.479 | 4.279 | 4.01 | 3.682 | 3.359 | 1.954 | 0.914 | 0.331 | 0.015 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Falling Short | 14.783 | 14.77 | 14.741 | 14.692 | 14.622 | 14.534 | 14.443 | 13.986 | 13.539 | 13.236 | 13.059 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Falling Short | 4.42 | 4.336 | 4.237 | 4.122 | 3.985 | 3.83 | 3.678 | 3 | 2.46 | 2.078 | 1.791 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Falling Short | 4.66 | 4.358 | 3.982 | 3.531 | 2.974 | 2.323 | 1.689 | -1.091 | -3.268 | -4.742 | -5.734 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Falling Short | 11.592 | 11.377 | 11.115 | 10.804 | 10.426 | 9.991 | 9.57 | 7.783 | 6.478 | 5.59 | 4.908 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Falling Short | 12.028 | 10.436 | 10.398 | 10.306 | 10.148 | 9.92 | 9.631 | 7.823 | 5.556 | 3.95 | 3.423 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Falling Short | 1.069 | 0.885 | 0.706 | 0.539 | 0.324 | 0.066 | -0.177 | -1.14 | -1.748 | -2.089 | -2.286 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Falling Short | 7.472 | 7.038 | 6.524 | 5.935 | 5.235 | 4.434 | 3.656 | 0.283 | -2.407 | -4.353 | -5.846 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Falling Short | 9.053 | 8.993 | 8.93 | 8.862 | 8.79 | 8.713 | 8.634 | 8.217 | 7.768 | 7.299 | 6.825 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Falling Short | 1.715 | 1.574 | 1.385 | 1.137 | 0.807 | 0.387 | -0.098 | -3.167 | -6.942 | -9.589 | -10.502 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Falling Short | 10.552 | 10.347 | 10.126 | 9.889 | 9.589 | 9.233 | 8.882 | 7.335 | 6.175 | 5.475 | 5.082 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Falling Short | 8.779 | 8.566 | 8.286 | 7.939 | 7.504 | 6.988 | 6.472 | 4.096 | 2.11 | 0.793 | 0.053 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Falling Short | 1.262 | 1.16 | 1.04 | 0.898 | 0.726 | 0.525 | 0.304 | -0.984 | -2.479 | -3.643 | -4.306 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Falling Short | 7.205 | 6.984 | 6.706 | 6.369 | 5.953 | 5.47 | 5.005 | 3.063 | 1.715 | 0.836 | 0.166 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Falling Short | 0.865 | 0.857 | 0.826 | 0.765 | 0.669 | 0.543 | 0.414 | -0.162 | -0.688 | -1.05 | -1.257 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Falling Short | 1.493 | 1.49 | 1.486 | 1.483 | 1.479 | 1.475 | 1.47 | 1.448 | 1.424 | 1.399 | 1.373 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 23.957 | 23.979 | 23.983 | 23.964 | 23.924 | 23.869 | 23.812 | 23.547 | 23.299 | 23.13 | 22.995 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 33.831 | 33.813 | 33.782 | 33.735 | 33.67 | 33.59 | 33.512 | 33.206 | 32.988 | 32.858 | 32.775 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 20.483 | 20.416 | 20.334 | 20.236 | 20.117 | 19.981 | 19.85 | 19.302 | 18.914 | 18.643 | 18.428 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 14.623 | 14.468 | 14.285 | 14.075 | 13.82 | 13.521 | 13.217 | 11.718 | 10.338 | 9.34 | 8.717 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Falling Short | 13.541 | 13.27 | 12.947 | 13.572 | 13.131 | 12.632 | 12.15 | 10.01 | 8.329 | 7.186 | 6.289 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Falling Short | 10.409 | 9.476 | 9.279 | 9.024 | 8.7 | 8.317 | 7.947 | 6.538 | 5.648 | 5.108 | 4.746 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Falling Short | 1.402 | 15.187 | 14.938 | 14.648 | 14.302 | 13.9 | 13.482 | 11.342 | 9.189 | 7.575 | 6.603 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Falling Short | 11.019 | 10.698 | 10.421 | 10.195 | 9.908 | 9.566 | 9.237 | 7.892 | 7.038 | 6.568 | 6.289 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Falling Short | 15.259 | 15.18 | 15.098 | 15.01 | 14.916 | 14.819 | 14.72 | 14.202 | 13.656 | 13.111 | 12.561 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Falling Short | 3.794 | 3.091 | 2.254 | 1.279 | 0.114 | -1.221 | -2.519 | -7.258 | -10.324 | -12.44 | -14.014 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Falling Short | 6.363 | 6.048 | 5.689 | 5.293 | 4.796 | 4.207 | 3.644 | 1.402 | -0.15 | -1.116 | -1.765 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Falling Short | 4.281 | 4.322 | 4.341 | 4.334 | 4.301 | 4.247 | 4.185 | 3.832 | 3.477 | 3.237 | 3.074 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 17.08 | 14.064 | 13.836 | 13.578 | 13.29 | 12.978 | 12.67 | 11.472 | 10.535 | 9.73 | 8.987 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Falling Short | 14.624 | 14.544 | 14.453 | 14.348 | 14.227 | 14.093 | 13.948 | 13.089 | 12.08 | 11.218 | 10.58 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Falling Short | 9.018 | 8.731 | 8.419 | 8.072 | 7.684 | 7.252 | 6.784 | 4.03 | 0.772 | -1.979 | -3.884 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Falling Short | 11.638 | 11.646 | 11.637 | 11.605 | 11.552 | 11.484 | 11.416 | 11.096 | 10.821 | 10.655 | 10.533 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Falling Short | 11.198 | 11.23 | 11.248 | 11.251 | 11.239 | 11.214 | 11.187 | 11.049 | 10.905 | 10.803 | 10.739 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 3.519 | 3.239 | 2.94 | 2.614 | 2.257 | 1.864 | 1.437 | -1.107 | -4.157 | -6.795 | -8.695 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Falling Short | 14.64 | 14.564 | 14.476 | 14.373 | 14.252 | 14.116 | 13.97 | 13.159 | 12.262 | 11.509 | 10.944 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Falling Short | 10.679 | 10.574 | 10.421 | 10.216 | 9.947 | 9.624 | 9.311 | 8.035 | 7.135 | 6.606 | 6.307 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Falling Short | 9.457 | 9.429 | 9.373 | 9.285 | 9.161 | 9.006 | 8.844 | 8.032 | 7.25 | 6.726 | 6.447 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Falling Short | 7.156 | 6.987 | 6.753 | 6.452 | 6.061 | 5.585 | 5.114 | 2.981 | 1.27 | 0.24 | -0.222 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Falling Short | 4.417 | 4.109 | 3.742 | 3.313 | 2.787 | 2.171 | 1.546 | 15.836 | 13.505 | 11.791 | 10.723 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Falling Short | 10.935 | 10.926 | 10.896 | 10.84 | 10.745 | 10.607 | 10.441 | 9.421 | 8.181 | 7.32 | 7.056 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Falling Short | 15.439 | 15.313 | 15.137 | 14.91 | 14.627 | 14.292 | 13.972 | 12.682 | 11.904 | 11.487 | 11.219 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Falling Short | 8.885 | 8.606 | 8.252 | 7.816 | 7.269 | 6.616 | 5.943 | 2.57 | -0.656 | -2.869 | -3.963 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Falling Short | 3.261 | 3.17 | 3.065 | 3.443 | 3.302 | 3.142 | 2.985 | 2.284 | 1.71 | 1.273 | 0.92 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Falling Short | 7.111 | 6.968 | 6.772 | 6.522 | 6.197 | 5.806 | 5.431 | 10.923 | 10.006 | 9.527 | 9.24 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Falling Short | 4.169 | 4.072 | 3.947 | 3.796 | 3.61 | 3.391 | 3.181 | 2.321 | 1.782 | 1.472 | 1.253 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 12.175 | 12.117 | 12.048 | 11.966 | 11.871 | 11.765 | 11.655 | 11.09 | 10.488 | 9.93 | 9.423 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 25.285 | 25.252 | 25.212 | 25.161 | 25.1 | 25.032 | 24.963 | 24.61 | 24.242 | 23.942 | 23.696 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Falling Short | 14.562 | 14.392 | 14.192 | 13.961 | 13.69 | 13.383 | 13.074 | 11.662 | 10.499 | 9.676 | 9.101 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Falling Short | 12.59 | 12.62 | 12.641 | 12.647 | 12.641 | 12.626 | 12.611 | 12.51 | 12.38 | 12.295 | 12.235 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Falling Short | 19.891 | 19.806 | 19.714 | 19.609 | 19.495 | 19.376 | 19.255 | 18.823 | 18.489 | 18.166 | 17.844 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Falling Short | 6.914 | 6.755 | 6.535 | 6.252 | 5.898 | 5.48 | 5.076 | 3.568 | 2.559 | 1.925 | 1.477 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 20.962 | 20.967 | 20.947 | 20.896 | 20.811 | 20.699 | 20.583 | 19.997 | 19.421 | 19.021 | 18.768 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Falling Short | 13.981 | 13.963 | 13.936 | 13.896 | 13.839 | 13.772 | 13.704 | 13.383 | 13.115 | 12.947 | 12.811 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Falling Short | 4.276 | 4.236 | 4.18 | 4.108 | 4.015 | 3.903 | 3.793 | 3.326 | 2.997 | 2.812 | 2.721 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Falling Short | 0.862 | 0.779 | 0.691 | 0.597 | 0.496 | 0.386 | 0.271 | -0.361 | -1.068 | -1.731 | -2.3 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Falling Short | 16.102 | 16.003 | 15.886 | 15.742 | 15.571 | 15.376 | 15.169 | 14.087 | 12.914 | 11.948 | 11.247 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 22.208 | 22.097 | 21.946 | 21.755 | 21.51 | 21.217 | 20.934 | 19.773 | 19.02 | 18.611 | 18.39 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 26.341 | 26.292 | 26.226 | 26.142 | 26.036 | 25.909 | 25.787 | 25.292 | 24.987 | 24.827 | 24.727 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Falling Short | 2.353 | 2.215 | 2.059 | 1.885 | 1.684 | 1.458 | 1.238 | 0.253 | -0.527 | -1.13 | -1.645 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Falling Short | 2.214 | 2.069 | 1.9 | 1.699 | 1.463 | 1.195 | 0.914 | -0.643 | -2.359 | -3.74 | -4.722 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Falling Short | 14.262 | 14.205 | 14.131 | 14.036 | 13.914 | 13.764 | 13.594 | 12.722 | 11.783 | 11.056 | 10.663 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Falling Short | 4.616 | 4.57 | 4.511 | 4.437 | 4.344 | 4.232 | 4.126 | 3.695 | 3.426 | 3.282 | 3.196 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Falling Short | 14.476 | 14.463 | 14.446 | 14.423 | 14.384 | 14.33 | 14.27 | 13.978 | 13.698 | 13.508 | 13.419 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Falling Short | 8.973 | 9.038 | 9.092 | 9.134 | 9.163 | 9.182 | 9.192 | 10.131 | 9.932 | 9.773 | 9.713 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Falling Short | 1.227 | 1.009 | 0.737 | 0.412 | 0.016 | -0.445 | -0.898 | -2.932 | -4.571 | -5.678 | -6.377 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 16.79 | 16.759 | 16.719 | 16.669 | 16.606 | 16.532 | 16.456 | 16.062 | 15.658 | 15.336 | 15.098 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 16.716 | 16.678 | 16.628 | 16.566 | 16.488 | 16.394 | 16.291 | 15.686 | 14.982 | 14.432 | 14.107 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Falling Short | 4.435 | 4.156 | 3.823 | 3.431 | 2.959 | 2.416 | 1.878 | 14.289 | 12.477 | 11.191 | 10.318 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Falling Short | 14.285 | 14.197 | 14.094 | 13.974 | 13.834 | 13.678 | 13.519 | 12.759 | 12.032 | 11.438 | 10.96 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Falling Short | 8.09 | 7.77 | 7.409 | 7.007 | 6.502 | 5.906 | 5.333 | 20.03 | 18.637 | 17.899 | 17.463 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Falling Short | 4.872 | 4.83 | 4.768 | 4.68 | 4.553 | 4.39 | 4.213 | 3.306 | 2.388 | 1.765 | 1.463 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Falling Short | 10.37 | 10.189 | 9.95 | 9.651 | 9.281 | 8.847 | 8.431 | 6.692 | 5.532 | 4.825 | 4.308 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Falling Short | 0.087 | -0.003 | -0.104 | -0.217 | -0.346 | -0.487 | -0.632 | -1.364 | -2.136 | -2.803 | -3.347 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Falling Short | 13.365 | 13.219 | 13.027 | 12.789 | 12.481 | 12.11 | 11.749 | 10.216 | 9.129 | 8.506 | 8.194 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Falling Short | 17.468 | 17.463 | 17.45 | 17.426 | 17.391 | 17.348 | 17.302 | 17.05 | 16.778 | 16.592 | 16.491 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Falling Short | 12.564 | 12.426 | 12.268 | 12.09 | 11.889 | 11.669 | 11.447 | 10.35 | 9.281 | 8.378 | 7.581 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Falling Short | 6.878 | 6.746 | 6.593 | 6.417 | 6.213 | 5.984 | 5.749 | 4.569 | 3.466 | 2.624 | 1.992 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Falling Short | 9.286 | 9.158 | 9.004 | 8.818 | 8.594 | 8.33 | 8.041 | 6.343 | 4.396 | 2.873 | 1.955 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Falling Short | 15.17 | 15.089 | 15.005 | 14.919 | 14.83 | 14.739 | 14.645 | 15.145 | 14.599 | 14.021 | 13.43 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Falling Short | 16.376 | 16.321 | 16.242 | 16.134 | 15.991 | 15.82 | 15.653 | 14.938 | 14.42 | 14.124 | 13.964 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Falling Short | 12.793 | 12.675 | 12.532 | 12.359 | 12.151 | 11.912 | 11.682 | 10.845 | 10.294 | 9.889 | 9.541 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Falling Short | 10.647 | 10.444 | 10.245 | 10.052 | 9.801 | 9.501 | 9.211 | 8.04 | 7.264 | 6.826 | 6.559 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Falling Short | 9.634 | 9.413 | 9.147 | 8.837 | 8.437 | 7.957 | 7.497 | 5.674 | 4.527 | 3.913 | 3.573 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Falling Short | 2.136 | 2.159 | 2.177 | 2.189 | 2.195 | 2.195 | 2.192 | 2.139 | 2.041 | 1.967 | 1.939 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Falling Short | 10.087 | 9.752 | 9.42 | 9.094 | 8.685 | 8.202 | 7.74 | 22.883 | 21.735 | 21.117 | 20.737 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Falling Short | 4.44 | 4.286 | 4.095 | 3.855 | 3.559 | 3.212 | 2.837 | 0.761 | -1.551 | -3.323 | -4.399 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Falling Short | 3.355 | 3.086 | 2.762 | 2.383 | 1.932 | 1.42 | 0.928 | -1.11 | -2.554 | -3.535 | -4.315 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Falling Short | 23.044 | 23.052 | 23.038 | 22.993 | 22.921 | 22.828 | 22.734 | 22.291 | 21.886 | 21.63 | 21.457 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Falling Short | 6.135 | 5.919 | 5.678 | 5.408 | 5.103 | 4.765 | 4.423 | 2.684 | 0.913 | -0.637 | -1.957 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Falling Short | 6.75 | 6.747 | 6.741 | 6.734 | 6.723 | 6.71 | 6.698 | 6.644 | 6.606 | 6.585 | 6.574 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Falling Short | 11.639 | 11.31 | 10.882 | 10.358 | 9.715 | 8.968 | 8.239 | 5.294 | 3.226 | 1.863 | 0.898 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Falling Short | 21.097 | 21.107 | 21.093 | 21.049 | 20.965 | 20.835 | 20.656 | 19.367 | 17.617 | 16.372 | 16.021 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Falling Short | 11.264 | 11.161 | 11.021 | 10.842 | 10.607 | 10.324 | 10.047 | 8.851 | 7.957 | 7.423 | 7.124 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Falling Short | 12.574 | 12.423 | 12.23 | 11.982 | 11.663 | 11.266 | 10.8 | 8.041 | 4.776 | 2.401 | 1.406 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Falling Short | 0.081 | -0.017 | -0.131 | -0.266 | -0.426 | -0.611 | -0.801 | -1.768 | -2.74 | -3.509 | -4.052 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Falling Short | 6.879 | 1.119 | 0.895 | 0.633 | 0.322 | -0.034 | -0.382 | 6.753 | 5.552 | 4.733 | 4.119 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Falling Short | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Falling Short | 3.528 | 3.31 | 3.056 | 2.762 | 2.419 | 2.032 | 1.654 | -0.066 | -1.492 | -2.605 | -3.542 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Falling Short | 12.435 | 12.328 | 12.183 | 11.986 | 11.712 | 11.355 | 10.939 | 8.269 | 4.958 | 2.677 | 1.946 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Falling Short | 5.51 | 5.396 | 5.246 | 5.062 | 4.817 | 4.517 | 4.217 | 2.997 | 2.069 | 1.465 | 1.136 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Falling Short | 1.094 | 0.996 | 0.891 | 0.784 | 0.646 | 0.478 | 0.318 | -0.32 | -0.724 | -0.941 | -1.071 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Falling Short | 12.674 | 12.62 | 12.536 | 12.42 | 12.263 | 12.072 | 11.885 | 11.084 | 10.506 | 10.173 | 9.986 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Falling Short | 7.079 | 7.11 | 7.134 | 7.145 | 7.138 | 7.119 | 7.099 | 6.978 | 6.818 | 6.709 | 6.631 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Falling Short | 13.453 | 13.439 | 13.409 | 13.36 | 13.291 | 13.205 | 13.117 | 12.648 | 12.152 | 11.797 | 11.559 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Falling Short | 6.841 | 6.499 | 6.101 | 5.648 | 5.119 | 4.521 | 3.935 | 1.276 | -0.935 | -2.652 | -4.045 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Falling Short | 9.667 | 9.657 | 9.613 | 9.528 | 9.39 | 9.195 | 8.948 | 7.321 | 5.238 | 3.769 | 3.299 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Falling Short | 14.69 | 14.705 | 14.718 | 14.727 | 14.734 | 14.738 | 14.741 | 14.738 | 14.71 | 14.68 | 14.65 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Falling Short | 5.549 | 5.543 | 5.532 | 5.516 | 5.493 | 5.464 | 5.435 | 5.31 | 5.222 | 5.174 | 5.147 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Falling Short | 13.925 | 13.944 | 13.955 | 13.95 | 13.933 | 13.908 | 13.883 | 13.745 | 13.585 | 13.48 | 13.404 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Falling Short | 4.056 | 3.92 | 3.73 | 3.486 | 3.179 | 2.814 | 2.458 | 1.018 | 0.007 | -0.61 | -0.984 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Falling Short | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Falling Short | 8.799 | 7.881 | 7.526 | 7.103 | 6.588 | 5.991 | 5.416 | 3.07 | 1.509 | 0.532 | -0.194 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Falling Short | 8.881 | 8.632 | 8.323 | 7.957 | 24.593 | 24.041 | 23.512 | 21.363 | 19.965 | 19.184 | 18.716 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Falling Short | 3.11 | 3.143 | 3.159 | 3.153 | 3.127 | 3.085 | 3.039 | 2.757 | 2.44 | 2.231 | 2.115 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Falling Short | 1.845 | 1.566 | 1.222 | 0.813 | 0.323 | -0.24 | -0.78 | -3.025 | -4.535 | -5.493 | -6.227 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Falling Short | 14.428 | 14.327 | 14.197 | 14.037 | 13.831 | 13.585 | 13.349 | 12.379 | 11.747 | 11.399 | 11.194 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Falling Short | 5.632 | 5.385 | 5.055 | 4.641 | 4.126 | 3.518 | 2.921 | 0.23 | -1.976 | -3.492 | -4.503 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Falling Short | 4.963 | 4.095 | 3.93 | 3.735 | 3.476 | 3.157 | 2.833 | 1.37 | 0.195 | -0.541 | -0.91 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Falling Short | 14.971 | 14.883 | 14.768 | 14.625 | 14.443 | 14.224 | 14.014 | 13.248 | 12.816 | 12.577 | 12.423 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Falling Short | 3.567 | 3.443 | 3.27 | 3.046 | 2.751 | 2.392 | 2.037 | 15.165 | 13.895 | 13.118 | 12.744 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Falling Short | 6.669 | 6.46 | 6.216 | 5.933 | 5.603 | 5.229 | 4.841 | 2.768 | 0.499 | -1.344 | -2.674 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Falling Short | 8.384 | 8.202 | 7.956 | 7.649 | 7.256 | 6.785 | 6.331 | 4.362 | 2.675 | 1.543 | 0.825 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Falling Short | 5.931 | 5.645 | 5.303 | 4.905 | 4.433 | 3.892 | 3.37 | 1.138 | -0.384 | -1.322 | -2.018 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Falling Short | 1.492 | 1.07 | 0.627 | 0.167 | -0.412 | -1.099 | -1.758 | -4.394 | -5.964 | -6.788 | -7.28 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Falling Short | 9.914 | 9.699 | 9.452 | 9.18 | 8.829 | 8.411 | 8.01 | 6.411 | 5.409 | 4.862 | 4.522 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Falling Short | 10.843 | 10.603 | 10.328 | 10.018 | 9.617 | 9.13 | 8.64 | 6.357 | 4.437 | 3.258 | 2.767 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Falling Short | 12.286 | 12.293 | 12.281 | 12.239 | 12.166 | 12.062 | 11.933 | 11.001 | 9.732 | 8.846 | 8.547 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Falling Short | 8.612 | 8.552 | 8.472 | 8.369 | 8.232 | 8.068 | 7.91 | 7.235 | 6.752 | 6.477 | 6.315 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Falling Short | 2.853 | 2.841 | 2.806 | 2.745 | 2.653 | 2.529 | 2.387 | 1.482 | 0.347 | -0.458 | -0.776 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Falling Short | 12.887 | 12.785 | 12.645 | 12.468 | 12.239 | 11.964 | 11.701 | 10.639 | 9.971 | 9.609 | 9.387 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Falling Short | 18.291 | 18.237 | 18.156 | 18.049 | 17.908 | 17.739 | 17.575 | 16.911 | 16.506 | 16.301 | 16.197 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Falling Short | 15.393 | 15.321 | 15.233 | 15.126 | 15.002 | 14.864 | 14.726 | 14.026 | 13.258 | 12.606 | 12.021 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Falling Short | 2.688 | 2.422 | 2.092 | 1.678 | 1.161 | 0.532 | -0.192 | -3.668 | -7.149 | -9.726 | -10.932 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Falling Short | 9.707 | 9.736 | 9.751 | 9.745 | 9.719 | 9.677 | 9.627 | 9.3 | 8.872 | 8.568 | 8.415 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Falling Short | 6.051 | 5.924 | 5.777 | 5.605 | 5.403 | 5.17 | 4.921 | 3.694 | 2.429 | 1.4 | 0.704 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Falling Short | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Falling Short | 7.006 | 6.763 | 6.475 | 6.142 | 5.717 | 5.207 | 4.702 | 2.571 | 0.963 | -0.026 | -0.539 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Falling Short | 14.447 | 14.318 | 14.141 | 13.916 | 13.634 | 13.302 | 12.977 | 11.596 | 10.683 | 10.174 | 9.877 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Falling Short | 3.114 | 3.003 | 2.873 | 2.723 | 2.544 | 2.342 | 2.146 | 1.327 | 0.707 | 0.25 | -0.124 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Falling Short | 8.728 | 8.495 | 8.207 | 7.843 | 7.387 | 6.831 | 6.182 | 1.945 | -3.446 | -7.455 | -9.277 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Falling Short | 13.319 | 13.089 | 12.846 | 12.587 | 12.26 | 11.874 | 11.503 | 9.974 | 8.98 | 8.453 | 8.161 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Falling Short | 4.98 | 4.908 | 4.823 | 4.728 | 4.615 | 4.489 | 4.366 | 3.846 | 3.473 | 3.205 | 2.979 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Falling Short | 6.076 | 5.784 | 5.429 | 5.007 | 4.495 | 3.906 | 3.339 | 0.99 | -0.771 | -2.01 | -2.98 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Falling Short | 10.001 | 9.844 | 9.631 | 9.359 | 9.009 | 8.591 | 8.19 | 6.654 | 5.722 | 5.211 | 4.917 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Falling Short | 15.679 | 15.514 | 15.328 | 15.122 | 14.866 | 14.565 | 14.277 | 13.159 | 12.531 | 12.206 | 11.998 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Falling Short | 6.062 | 5.985 | 5.856 | 5.672 | 5.424 | 5.119 | 4.819 | 3.563 | 2.603 | 2.016 | 1.696 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Falling Short | 12.855 | 12.452 | 11.988 | 11.455 | 10.831 | 10.122 | 9.416 | 6.266 | 3.654 | 1.752 | 0.388 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Falling Short | 12.727 | 12.682 | 12.623 | 12.547 | 12.455 | 12.349 | 12.243 | 11.777 | 11.341 | 10.981 | 10.674 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Falling Short | 9.33 | 9.14 | 8.899 | 8.607 | 8.243 | 7.811 | 7.375 | 5.421 | 3.748 | 2.595 | 1.932 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Falling Short | 11.283 | 11.293 | 11.281 | 11.24 | 11.168 | 11.064 | 10.936 | 10.105 | 9.051 | 8.313 | 8.053 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Falling Short | 5.502 | 5.496 | 5.454 | 5.37 | 5.236 | 5.054 | 4.844 | 3.56 | 1.965 | 0.822 | 0.342 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Falling Short | 28.493 | 28.406 | 28.3 | 28.17 | 28.013 | 27.829 | 27.631 | 26.524 | 25.278 | 24.283 | 23.651 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Falling Short | 2.899 | 2.578 | 2.241 | 1.887 | 1.51 | 1.115 | 0.711 | -1.373 | -3.507 | -5.506 | -7.357 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Falling Short | 1.832 | 1.775 | 1.709 | 1.634 | 1.548 | 1.452 | 1.358 | 0.918 | 0.527 | 0.171 | -0.165 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Falling Short | 11.647 | 11.439 | 11.198 | 10.918 | 10.584 | 10.202 | 9.829 | 8.168 | 6.845 | 5.91 | 5.187 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Falling Short | 9.842 | 9.854 | 9.853 | 9.834 | 9.797 | 9.744 | 9.685 | 9.353 | 8.984 | 8.735 | 8.617 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Falling Short | 10.663 | 10.616 | 10.542 | 10.433 | 10.289 | 10.119 | 9.947 | 9.134 | 8.467 | 8.059 | 7.782 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Falling Short | 1.737 | 1.657 | 1.566 | 1.457 | 1.332 | 1.189 | 1.037 | 0.277 | -0.518 | -1.173 | -1.63 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Falling Short | 11.795 | 11.79 | 11.758 | 11.684 | 11.561 | 11.383 | 11.152 | 9.386 | 6.9 | 5.146 | 4.623 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Falling Short | 15.657 | 15.637 | 15.609 | 15.573 | 15.518 | 15.445 | 15.37 | 14.976 | 14.585 | 14.328 | 14.209 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Falling Short | 7.747 | 6.666 | 6.257 | 5.778 | 5.211 | 4.567 | 3.938 | 1.338 | -0.607 | -1.992 | -3.069 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Falling Short | 11.947 | 11.886 | 11.796 | 11.678 | 11.52 | 11.328 | 11.142 | 10.397 | 9.946 | 9.698 | 9.538 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Falling Short | 15.757 | 15.77 | 15.735 | 15.635 | 15.452 | 15.177 | 14.814 | 12.061 | 8.208 | 5.483 | 4.69 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Falling Short | 8.798 | 8.651 | 8.442 | 8.17 | 7.812 | 7.376 | 6.95 | 5.082 | 3.656 | 2.81 | 2.384 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Falling Short | 4.223 | 4.176 | 4.119 | 4.053 | 3.974 | 3.884 | 3.796 | 3.397 | 3.068 | 2.807 | 2.592 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Falling Short | 8.942 | 8.774 | 8.582 | 8.363 | 8.083 | 7.748 | 7.422 | 6.122 | 5.241 | 4.727 | 4.419 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 14.235 | 14.026 | 13.783 | 13.501 | 13.176 | 12.814 | 12.443 | 10.568 | 8.668 | 7.035 | 5.655 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 13.164 | 12.968 | 12.742 | 12.474 | 12.166 | 11.827 | 11.475 | 9.575 | 7.512 | 5.722 | 4.226 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Falling Short | 12.234 | 12.245 | 12.244 | 12.225 | 12.186 | 12.132 | 12.07 | 11.682 | 11.185 | 10.841 | 10.685 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Falling Short | 8.031 | 8.055 | 8.067 | 8.065 | 8.049 | 8.022 | 7.993 | 7.845 | 7.707 | 7.608 | 7.518 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Falling Short | 17.528 | 17.474 | 17.396 | 17.294 | 17.165 | 17.01 | 16.858 | 16.196 | 15.672 | 15.343 | 15.158 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Falling Short | 4.671 | 4.533 | 4.385 | 4.224 | 4.051 | 3.864 | 3.666 | 2.523 | 1.184 | -0.115 | -1.276 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Falling Short | 2.398 | 2.179 | 1.935 | 1.668 | 1.329 | 0.926 | 0.539 | -1.039 | -2.053 | -2.609 | -2.948 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Falling Short | 11.641 | 11.447 | 11.223 | 10.972 | 10.655 | 10.281 | 9.922 | 8.471 | 7.455 | 6.838 | 6.431 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Falling Short | 10.179 | 9.953 | 9.68 | 9.358 | 8.946 | 8.448 | 7.946 | 5.555 | 3.468 | 2.141 | 1.523 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 12.926 | 12.929 | 12.914 | 12.877 | 12.812 | 12.719 | 12.604 | 11.794 | 10.72 | 9.969 | 9.723 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Falling Short | 16.097 | 16.007 | 15.882 | 15.722 | 15.516 | 15.27 | 15.034 | 14.089 | 13.513 | 13.212 | 13.038 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Falling Short | 12.839 | 12.78 | 12.688 | 12.558 | 12.383 | 12.169 | 11.962 | 11.111 | 10.528 | 10.213 | 10.059 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Falling Short | 9.426 | 9.327 | 9.18 | 8.983 | 8.716 | 8.385 | 8.049 | 6.44 | 4.996 | 4.08 | 3.691 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Falling Short | 11.53 | 9.884 | 9.793 | 9.664 | 9.488 | 9.274 | 9.067 | 8.304 | 7.867 | 7.636 | 7.491 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Falling Short | 4.142 | 4.066 | 3.975 | 3.868 | 3.737 | 3.584 | 3.436 | 2.806 | 2.348 | 2.051 | 1.851 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Falling Short | 14.06 | 13.844 | 13.57 | 13.237 | 12.82 | 12.328 | 11.854 | 9.894 | 8.62 | 7.921 | 7.522 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Falling Short | 2.199 | 2.006 | 1.737 | 1.391 | 0.942 | 0.404 | -0.116 | -2.217 | -3.567 | -4.317 | -4.76 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Falling Short | 14.67 | 14.549 | 14.389 | 14.194 | 13.94 | 13.632 | 13.334 | 12.082 | 11.2 | 10.688 | 10.418 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Falling Short | 7.735 | 7.548 | 7.305 | 7.007 | 6.624 | 6.168 | 5.731 | 3.918 | 2.701 | 2.007 | 1.569 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Falling Short | 18.458 | 18.482 | 18.478 | 18.437 | 18.357 | 18.246 | 18.125 | 17.448 | 16.729 | 16.26 | 16.04 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Falling Short | 12.549 | 12.447 | 12.323 | 12.175 | 11.99 | 11.772 | 11.556 | 10.581 | 9.813 | 9.338 | 9.072 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Falling Short | 3.274 | 3.04 | 2.756 | 2.418 | 2.009 | 1.536 | 1.068 | -1.102 | -2.984 | -4.387 | -5.409 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Falling Short | 3.422 | 2.567 | 1.577 | 0.449 | -0.869 | -2.364 | -3.827 | -10.222 | -14.972 | -18.194 | -20.601 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Falling Short | 4.047 | 3.778 | 3.466 | 3.107 | 2.656 | 2.124 | 1.605 | 16.663 | 15.503 | 14.847 | 14.441 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Falling Short | 12.615 | 12.341 | 12.01 | 11.624 | 11.162 | 10.634 | 10.125 | 7.993 | 6.508 | 5.523 | 4.752 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Falling Short | 21.663 | 18.663 | 18.71 | 18.745 | 18.772 | 18.796 | 18.818 | 18.86 | 18.85 | 18.841 | 18.832 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Falling Short | 3.287 | 2.987 | 2.641 | 2.231 | 1.743 | 1.173 | 0.532 | -2.833 | -6.549 | -9.486 | -11.184 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Falling Short | 12.598 | 12.572 | 12.53 | 12.471 | 12.389 | 12.289 | 12.188 | 11.709 | 11.288 | 11.005 | 10.787 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Falling Short | 13.952 | 13.992 | 14.026 | 14.051 | 14.069 | 14.08 | 14.088 | 14.096 | 14.069 | 14.039 | 14.011 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Falling Short | 14.929 | 14.958 | 14.978 | 14.986 | 14.984 | 14.973 | 14.962 | 14.891 | 14.793 | 14.724 | 14.678 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Falling Short | 9.768 | 9.475 | 9.099 | 8.643 | 8.082 | 7.426 | 6.791 | 4.13 | 2.23 | 1.006 | 0.172 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Falling Short | 15.713 | 15.631 | 15.54 | 15.434 | 15.314 | 15.182 | 15.046 | 14.317 | 13.541 | 12.875 | 12.319 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Falling Short | 5.452 | 5.429 | 5.382 | 5.308 | 5.203 | 5.078 | 4.95 | 4.325 | 3.737 | 3.355 | 3.095 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Falling Short | 14.033 | 13.95 | 13.832 | 13.68 | 13.48 | 13.238 | 13.002 | 11.972 | 11.169 | 10.681 | 10.415 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Falling Short | 18.278 | 14.828 | 14.797 | 14.754 | 14.688 | 14.602 | 14.517 | 14.239 | 14.088 | 14.002 | 13.967 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Falling Short | 11.593 | 11.465 | 11.312 | 11.134 | 10.918 | 10.667 | 10.419 | 9.288 | 8.357 | 7.705 | 7.25 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Falling Short | 2.548 | 2.434 | 2.289 | 2.111 | 1.888 | 1.623 | 1.343 | -0.154 | -1.66 | -2.691 | -3.177 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Falling Short | 11.006 | 10.867 | 10.685 | 10.466 | 10.185 | 9.848 | 9.524 | 8.213 | 7.282 | 6.696 | 6.305 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Falling Short | 10.103 | 9.979 | 9.804 | 9.576 | 9.276 | 8.913 | 8.559 | 8.175 | 7.247 | 6.714 | 6.443 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Falling Short | 5.519 | 5.208 | 4.852 | 4.439 | 3.958 | 3.408 | 2.806 | -0.254 | -3.472 | -6.054 | -7.71 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Falling Short | 16.347 | 16.22 | 16.074 | 15.905 | 15.71 | 15.489 | 15.271 | 14.266 | 13.418 | 12.764 | 12.254 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Falling Short | 8.798 | 7.037 | 6.704 | 6.318 | 5.869 | 5.356 | 4.798 | 8.854 | 5.726 | 3.319 | 1.838 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Falling Short | 3.81 | 3.701 | 3.573 | 3.426 | 3.252 | 3.056 | 2.866 | 2.048 | 1.442 | 1.016 | 0.676 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Falling Short | 14.44 | 14.302 | 14.112 | 13.87 | 13.56 | 13.188 | 12.829 | 11.37 | 10.406 | 9.884 | 9.635 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Falling Short | -0.309 | -0.475 | -0.672 | 0.095 | -0.188 | -0.515 | -0.839 | -2.201 | -3.294 | -4.069 | -4.583 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Falling Short | 9.162 | 8.937 | 8.661 | 8.332 | 7.934 | 7.475 | 7.025 | 5.007 | 3.346 | 2.138 | 1.244 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Falling Short | 7.782 | 7.656 | 7.477 | 7.241 | 6.927 | 6.546 | 6.173 | 4.554 | 3.328 | 2.607 | 2.243 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Falling Short | 4.997 | 4.696 | 4.33 | 3.89 | 3.357 | 2.743 | 2.144 | -0.463 | -2.567 | -4.073 | -5.195 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Falling Short | 16.162 | 16.027 | 15.839 | 15.594 | 15.271 | 14.88 | 14.495 | 12.859 | 11.568 | 10.77 | 10.365 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Falling Short | 7.771 | 7.804 | 7.817 | 7.804 | 7.766 | 7.705 | 7.634 | 7.179 | 6.602 | 6.193 | 6.014 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Falling Short | 13.875 | 14.648 | 14.379 | 6.075 | 5.397 | 4.617 | 3.864 | 1.564 | 0.455 | -0.234 | -0.754 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Falling Short | 10.981 | 10.663 | 10.276 | 9.817 | 9.27 | 8.642 | 8.026 | 5.269 | 3.141 | 1.732 | 0.735 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Falling Short | 6.53 | 6.557 | 6.562 | 6.535 | 6.48 | 6.403 | 6.319 | 5.951 | 5.61 | 5.381 | 5.262 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Falling Short | 11.857 | 11.646 | 11.375 | 11.044 | 10.637 | 10.16 | 9.701 | 7.812 | 6.635 | 5.998 | 5.579 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Falling Short | 4.956 | 4.513 | 4 | 3.405 | 2.71 | 1.922 | 1.12 | -2.932 | -6.921 | -10.041 | -12.259 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Falling Short | 10.257 | 10.304 | 10.346 | 10.382 | 10.412 | 10.438 | 10.462 | 10.537 | 10.551 | 10.55 | 10.543 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Falling Short | 11.17 | 11.221 | 11.258 | 11.275 | 11.273 | 11.249 | 11.206 | 10.753 | 10.014 | 9.483 | 9.325 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Falling Short | 2.406 | 2.448 | 2.483 | 2.511 | 2.53 | 2.543 | 2.553 | 2.548 | 2.477 | 2.417 | 2.389 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Falling Short | 6.432 | 6.332 | 6.208 | 6.061 | 5.867 | 5.632 | 5.402 | 4.572 | 4.058 | 3.757 | 3.589 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Falling Short | 0.607 | 0.441 | 0.256 | 0.051 | -0.189 | -0.461 | -0.73 | -1.975 | -3.013 | -3.773 | -4.335 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Falling Short | 12.534 | 12.399 | 12.215 | 11.979 | 11.679 | 11.323 | 10.961 | 9.231 | 7.837 | 7.013 | 6.615 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Falling Short | 12.823 | 10.889 | 10.884 | 10.839 | 10.755 | 10.638 | 10.504 | 9.961 | 9.503 | 9.193 | 9.072 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Falling Short | 9.343 | 9.163 | 15.956 | 15.723 | 15.425 | 15.069 | 14.724 | 13.317 | 12.421 | 11.931 | 11.646 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Falling Short | 9.946 | 9.8 | 9.638 | 9.454 | 9.246 | 9.015 | 8.766 | 7.322 | 5.669 | 4.284 | 3.269 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Falling Short | 3.364 | 1.833 | 1.559 | 1.292 | 0.957 | 0.561 | 0.173 | -1.467 | -2.644 | -3.421 | -3.99 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Falling Short | 12.453 | 12.384 | 12.308 | 12.222 | 12.128 | 12.027 | 11.925 | 11.379 | 10.797 | 10.225 | 9.655 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Falling Short | 8.395 | 8.345 | 15.259 | 15.133 | 14.959 | 14.742 | 14.527 | 13.552 | 12.756 | 12.273 | 12.013 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Falling Short | 5.218 | 4.2 | 3.845 | 3.495 | 3.06 | 2.548 | 2.033 | -0.238 | -2.177 | -3.545 | -4.388 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Falling Short | 10.335 | 10.157 | 9.916 | 9.614 | 9.228 | 8.769 | 8.329 | 6.561 | 5.402 | 4.743 | 4.326 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Falling Short | 10.152 | 9.989 | 7.636 | 7.342 | 6.971 | 6.512 | 5.972 | 2.783 | -1.035 | -3.932 | -5.281 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Falling Short | 8.38 | 8.115 | 7.785 | 7.392 | 6.913 | 6.353 | 5.801 | 3.323 | 1.364 | 0.047 | -0.817 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Falling Short | 6.934 | 5.139 | 4.873 | 4.555 | 4.144 | 3.651 | 3.166 | 1.38 | 0.241 | -0.431 | -0.792 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Falling Short | 8.407 | 7.709 | 7.739 | 7.736 | 7.703 | 7.643 | 7.558 | 6.901 | 5.959 | 5.295 | 5.073 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Falling Short | 18.732 | 18.714 | 18.678 | 18.615 | 18.52 | 18.389 | 18.224 | 17.077 | 15.549 | 14.475 | 14.147 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Falling Short | 8.64 | 8.599 | 8.524 | 8.414 | 8.259 | 8.066 | 7.879 | 7.12 | 6.637 | 6.374 | 6.211 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Falling Short | 10.728 | 10.602 | 10.432 | 10.216 | 9.942 | 9.616 | 9.288 | 7.765 | 6.593 | 5.901 | 5.522 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Falling Short | 12.095 | 11.991 | 11.842 | 11.644 | 11.387 | 11.082 | 10.789 | 9.64 | 8.909 | 8.519 | 8.287 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Falling Short | 12.244 | 12.255 | 12.25 | 12.224 | 12.176 | 12.109 | 12.035 | 11.6 | 11.051 | 10.655 | 10.456 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Falling Short | 8.23 | 8.291 | 8.349 | 8.399 | 8.437 | 8.466 | 8.491 | 8.553 | 8.53 | 8.499 | 8.474 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Falling Short | 8.026 | 6.267 | 6.222 | 6.154 | 6.051 | 5.916 | 5.767 | 4.97 | 4.127 | 3.538 | 3.246 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Falling Short | 9.814 | 8.595 | 8.631 | 8.649 | 8.653 | 8.647 | 8.638 | 8.563 | 8.441 | 8.355 | 8.29 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Falling Short | 1.209 | 1.062 | 0.891 | 0.695 | 0.463 | 0.198 | -0.061 | -1.184 | -2.072 | -2.721 | -3.226 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 2.841 | 2.833 | 2.819 | 2.801 | 2.775 | 2.742 | 2.71 | 2.542 | 2.371 | 2.239 | 2.128 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Falling Short | 12.803 | 12.712 | 12.598 | 12.453 | 12.272 | 12.054 | 11.809 | 10.306 | 8.482 | 7.091 | 6.352 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Falling Short | 24.326 | 24.281 | 24.228 | 24.164 | 24.093 | 24.017 | 23.939 | 23.578 | 23.201 | 22.814 | 22.417 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Falling Short | 13.74 | 13.757 | 13.761 | 13.752 | 13.726 | 13.688 | 13.65 | 13.495 | 13.378 | 13.299 | 13.235 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Falling Short | -2.04 | -2.272 | -2.525 | -2.803 | -3.108 | -3.438 | -3.777 | -5.58 | -7.524 | -9.333 | -10.955 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Falling Short | 3.081 | 2.811 | 2.5 | 2.124 | 1.677 | 1.154 | 0.57 | -2.889 | -7.011 | -10.228 | -12.071 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Falling Short | 11 | 10.931 | 10.819 | 10.666 | 10.46 | 10.209 | 9.967 | 8.995 | 8.388 | 8.078 | 7.911 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Falling Short | 11.231 | 11.285 | 11.328 | 11.359 | 11.376 | 11.379 | 11.369 | 11.173 | 10.796 | 10.516 | 10.437 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Falling Short | 8.106 | 7.844 | 7.518 | 7.123 | 6.636 | 6.065 | 5.495 | 2.853 | 0.579 | -0.999 | -1.971 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Falling Short | 11.699 | 10.965 | 10.804 | 10.615 | 10.398 | 10.16 | 9.923 | 9.064 | 8.467 | 7.994 | 7.55 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Falling Short | 4.199 | 4.008 | 3.794 | 3.56 | 3.268 | 2.925 | 2.597 | 1.315 | 0.602 | 0.241 | 0.018 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Falling Short | 11.002 | 10.895 | 10.74 | 10.536 | 10.27 | 9.954 | 9.647 | 8.402 | 7.651 | 7.268 | 7.041 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Falling Short | -1.195 | -1.295 | -1.421 | -1.574 | 0.235 | 0.011 | -0.205 | -1.114 | -1.748 | -2.128 | -2.385 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Falling Short | 15.221 | 15.152 | 15.068 | 14.958 | 14.822 | 14.661 | 14.48 | 13.398 | 12.099 | 11.112 | 10.575 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Falling Short | 14.824 | 14.502 | 14.221 | 13.987 | 13.69 | 13.334 | 12.983 | 11.432 | 10.249 | 9.558 | 9.249 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Falling Short | 10.136 | 10.006 | 9.811 | 9.555 | 9.221 | 8.819 | 8.429 | 6.767 | 5.549 | 4.805 | 4.359 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Falling Short | 23.71 | 23.734 | 23.756 | 23.775 | 23.79 | 23.8 | 23.809 | 23.83 | 23.818 | 23.804 | 23.793 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Falling Short | 8.471 | 8.493 | 8.513 | 8.522 | 8.519 | 8.51 | 8.501 | 8.442 | 8.35 | 8.292 | 8.252 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Falling Short | 11.336 | 11.225 | 11.06 | 10.844 | 10.564 | 10.228 | 9.906 | 8.621 | 7.827 | 7.401 | 7.145 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Falling Short | 4.285 | 4.239 | 4.19 | 4.138 | 4.083 | 4.024 | 3.964 | 3.644 | 3.301 | 2.951 | 2.598 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Falling Short | 8.715 | 8.587 | 8.445 | 8.284 | 8.103 | 7.905 | 7.704 | 6.659 | 5.577 | 4.625 | 3.803 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Falling Short | 13.907 | 13.779 | 13.609 | 13.397 | 13.128 | 12.809 | 12.501 | 11.245 | 10.461 | 10.029 | 9.76 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Falling Short | 10.765 | 10.535 | 10.268 | 9.96 | 9.596 | 9.182 | 8.773 | 7.049 | 5.661 | 4.64 | 3.873 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Falling Short | 7.778 | 7.439 | 7.035 | 6.56 | 5.998 | 5.355 | 4.723 | 1.969 | -0.074 | -1.404 | -2.345 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Falling Short | 12.856 | 12.529 | 12.18 | 11.798 | 11.379 | 10.925 | 10.448 | 7.959 | 5.29 | 2.956 | 1.114 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Falling Short | 7.656 | 7.638 | 7.587 | 7.496 | 7.36 | 7.183 | 6.984 | 5.807 | 4.463 | 3.558 | 3.203 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Falling Short | 13.817 | 13.725 | 13.591 | 13.418 | 13.192 | 12.921 | 12.661 | 11.597 | 10.872 | 10.452 | 10.2 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Falling Short | 7.36 | 7.133 | 6.874 | 6.583 | 6.214 | 5.778 | 5.355 | 20.692 | 19.649 | 19.065 | 18.705 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Falling Short | 7.294 | 7.111 | 6.906 | 6.669 | 6.4 | 6.106 | 5.8 | 4.136 | 2.303 | 0.737 | -0.517 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Leading the Way | 13.095 | 12.842 | 12.59 | 12.496 | 12.477 | 12.453 | 12.341 | 10.626 | 9.188 | 8.133 | 8.455 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Leading the Way | 12.273 | 10.634 | 10.518 | 10.33 | 10.197 | 10.009 | 9.661 | 6.175 | 3.673 | 2.162 | 2.42 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Leading the Way | 11.529 | 11.234 | 10.841 | 10.387 | 9.931 | 9.451 | 8.801 | 3.433 | -0.851 | -4.105 | -4.434 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Leading the Way | 6.037 | 4.683 | 4.689 | 4.641 | 4.605 | 4.536 | 4.369 | 1.373 | -0.552 | -1.884 | -1.419 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 15.39 | 15.001 | 14.492 | 14.007 | 13.661 | 13.302 | 12.735 | 8.368 | 5.101 | 2.8 | 2.997 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 17.148 | 17.141 | 17.11 | 17.075 | 17.071 | 17.064 | 17.014 | 16.268 | 15.676 | 15.242 | 15.388 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Leading the Way | 9.029 | 8.476 | 7.73 | 6.903 | 6.331 | 5.737 | 4.893 | -1.945 | -7.156 | -10.85 | -10.975 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Leading the Way | 17.217 | 17.249 | 17.248 | 17.23 | 17.254 | 17.273 | 17.234 | 15.618 | 14.434 | 13.502 | 13.854 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Leading the Way | 1.046 | 0.845 | 0.55 | 0.197 | -0.107 | -0.43 | -0.92 | -5.496 | -9.189 | -12.046 | -12.105 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Leading the Way | 3.406 | 2.921 | 3.059 | 3.169 | 3.306 | 3.432 | 3.518 | 2.754 | 2.216 | 1.836 | 2.34 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Leading the Way | 12.006 | 11.757 | 11.378 | 10.926 | 10.628 | 10.313 | 9.843 | 6.902 | 3.975 | 1.855 | 1.84 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Leading the Way | 2.652 | 2.332 | 1.899 | 1.48 | 1.158 | 0.787 | 0.26 | -4.728 | -8.148 | -10.332 | -10 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Leading the Way | 3.331 | 3.325 | 3.307 | 3.282 | 3.262 | 3.238 | 3.2 | 2.811 | 2.518 | 2.3 | 2.284 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Leading the Way | 15.738 | 15.547 | 15.244 | 14.885 | 14.689 | 14.484 | 14.129 | 10.494 | 7.716 | 5.731 | 6.052 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Leading the Way | 13.072 | 12.558 | 12.516 | 12.455 | 12.44 | 12.42 | 12.358 | 11.362 | 10.564 | 9.934 | 9.995 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Leading the Way | 10.64 | 10.636 | 10.578 | 10.484 | 10.439 | 10.377 | 10.243 | 7.862 | 6.14 | 4.984 | 5.452 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Leading the Way | 15.586 | 15.247 | 14.753 | 14.178 | 13.747 | 13.283 | 12.627 | 7.863 | 4.389 | 2.157 | 2.135 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Leading the Way | 8.361 | 8.384 | 8.379 | 8.35 | 8.336 | 8.307 | 8.217 | 6.762 | 5.612 | 4.836 | 5.106 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Leading the Way | 5.848 | 5.708 | 5.497 | 5.234 | 5.067 | 4.89 | 4.589 | 0.605 | -2.774 | -5.547 | -5.648 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Leading the Way | 21.438 | 21.4 | 21.299 | 21.155 | 21.061 | 20.959 | 20.771 | 19.213 | 18.054 | 17.253 | 17.428 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Leading the Way | 3.691 | 3.559 | 3.389 | 3.196 | 3.078 | 2.954 | 2.761 | 0.737 | -1.031 | -2.497 | -2.763 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Leading the Way | 11.549 | 11.065 | 10.38 | 9.592 | 9.034 | 8.433 | 7.56 | 0.36 | -5.064 | -8.771 | -8.855 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Leading the Way | 9.399 | 8.956 | 8.332 | 7.669 | 7.195 | 6.692 | 5.904 | -0.131 | -4.337 | -7.25 | -6.976 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Leading the Way | 14.705 | 14.455 | 14.105 | 13.753 | 13.494 | 13.221 | 12.82 | 10.004 | 7.988 | 6.655 | 6.779 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Leading the Way | 3.007 | 2.944 | 2.762 | 2.495 | 2.373 | 2.205 | 1.86 | -2.358 | -5.519 | -7.548 | -7.036 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Leading the Way | 5.395 | 5.172 | 4.85 | 4.469 | 4.168 | 3.839 | 3.39 | 0.121 | -2.287 | -3.874 | -4.035 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 15.168 | 15.121 | 15.039 | 14.939 | 14.871 | 14.789 | 14.629 | 12.638 | 11.34 | 10.379 | 10.55 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 4.298 | 1.3 | 1.203 | 1.043 | 0.926 | 0.748 | 0.377 | -4.694 | -8.362 | -10.833 | -10.22 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Leading the Way | 7.451 | 7.331 | 7.108 | 6.805 | 6.581 | 6.303 | 5.867 | 1.345 | -2.169 | -4.502 | -4.4 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Leading the Way | 11.699 | 11.408 | 10.949 | 10.392 | 10.041 | 9.671 | 9.034 | 3.311 | -1.086 | -4.269 | -3.973 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Leading the Way | 5.81 | 5.369 | 4.692 | 3.877 | 3.275 | 2.621 | 1.613 | -6.773 | -13.111 | -17.492 | -17.371 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Leading the Way | 6.881 | 6.864 | 6.842 | 6.816 | 6.796 | 6.774 | 6.747 | 6.4 | 6.094 | 5.829 | 5.8 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Leading the Way | 3.704 | 3.668 | 3.614 | 3.549 | 3.492 | 3.427 | 3.338 | 2.489 | 1.838 | 1.357 | 1.313 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Leading the Way | 11.589 | 11.188 | 10.599 | 9.91 | 9.495 | 9.055 | 8.368 | 2.462 | -1.883 | -4.911 | -4.752 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 13.548 | 13.454 | 13.356 | 13.252 | 13.146 | 13.039 | 12.931 | 11.699 | 10.46 | 9.239 | 8.716 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Leading the Way | 4.62 | 4.504 | 4.342 | 4.158 | 4.022 | 3.881 | 3.684 | 2.247 | 1.237 | 0.563 | 0.569 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 9.432 | 9.103 | 8.588 | 7.986 | 7.605 | 7.202 | 6.542 | 0.417 | -4.064 | -7.192 | -6.744 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Leading the Way | 11.554 | 11.283 | 10.852 | 10.342 | 9.954 | 9.533 | 8.873 | 3.508 | -0.398 | -3.052 | -2.805 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Leading the Way | 9.324 | 9.347 | 9.314 | 9.244 | 9.252 | 9.242 | 9.14 | 7.076 | 5.522 | 4.441 | 4.828 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Leading the Way | 10.227 | 10.216 | 10.139 | 10.026 | 9.956 | 9.872 | 9.711 | 7.944 | 6.867 | 6.17 | 6.46 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Leading the Way | 17.46 | 17.28 | 17.022 | 16.719 | 16.478 | 16.213 | 15.852 | 13.456 | 11.837 | 10.904 | 10.909 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Leading the Way | 7.685 | 22.197 | 21.914 | 21.59 | 21.351 | 21.099 | 20.676 | 16.625 | 13.507 | 11.225 | 11.498 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Leading the Way | 10.144 | 9.715 | 9.077 | 8.308 | 7.723 | 7.121 | 6.213 | 16.099 | 10.294 | 5.854 | 5.626 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Leading the Way | 3.861 | 3.732 | 3.558 | 3.391 | 3.285 | 3.174 | 3.009 | 1.862 | 1.086 | 0.579 | 0.651 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Leading the Way | 5.887 | 4.93 | 3.719 | 2.527 | 1.571 | 0.561 | -0.874 | -9.911 | -15.898 | -19.87 | -19.685 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Leading the Way | 3.756 | 3.349 | 2.778 | 2.103 | 1.43 | 0.713 | -0.294 | -9.056 | -15.864 | -21.192 | -21.706 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Leading the Way | 5.039 | 4.453 | 3.6 | 2.582 | 1.806 | 0.994 | -0.207 | 14.284 | 6.807 | 1.215 | 0.887 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Leading the Way | 4.091 | 4.156 | 4.211 | 4.256 | 4.297 | 4.329 | 4.348 | 4.102 | 3.93 | 3.851 | 4.015 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Leading the Way | 7.943 | 7.472 | 6.746 | 5.852 | 5.167 | 4.393 | 3.256 | 11.495 | 5.088 | 1.06 | 1.044 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Leading the Way | 12.825 | 12.907 | 12.975 | 13.026 | 13.072 | 13.107 | 13.126 | 12.244 | 11.549 | 11.07 | 11.414 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Leading the Way | 9.528 | 9.676 | 9.816 | 9.946 | 10.07 | 10.188 | 10.299 | 10.471 | 10.594 | 10.705 | 11.032 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Leading the Way | 11.125 | 11.218 | 11.277 | 11.348 | 11.446 | 11.529 | 11.544 | 9.588 | 8.06 | 6.93 | 7.639 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Leading the Way | 9.029 | 9.097 | 9.135 | 9.161 | 9.213 | 9.257 | 9.262 | 8.35 | 7.671 | 7.191 | 7.576 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Leading the Way | 10.773 | 10.468 | 9.995 | 9.439 | 9.037 | 8.58 | 7.899 | 2.774 | -0.806 | -2.89 | -2.689 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Leading the Way | 5.106 | 5.048 | 4.96 | 4.86 | 4.76 | 4.656 | 4.529 | 3.988 | 3.696 | 3.547 | 3.483 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Leading the Way | 7.663 | 7.65 | 7.616 | 7.569 | 7.532 | 7.49 | 7.426 | 6.876 | 6.387 | 5.965 | 5.795 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Leading the Way | 13.062 | 12.572 | 11.924 | 11.286 | 10.811 | 10.31 | 9.527 | 3.173 | -1.491 | -4.68 | -4.326 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Leading the Way | 0.818 | 0.817 | 0.806 | 0.786 | 0.771 | 0.751 | 0.718 | 0.339 | 0.03 | -0.205 | -0.227 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Leading the Way | 2.421 | 2.193 | 1.89 | 1.558 | 1.302 | 1.036 | 0.687 | -1.888 | -3.695 | -4.946 | -4.997 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 9.585 | 9.348 | 8.975 | 8.522 | 8.233 | 7.907 | 7.415 | 3.114 | 0.023 | -1.888 | -1.659 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Leading the Way | 8.408 | 8.26 | 8.056 | 7.891 | 7.792 | 7.679 | 7.448 | 4.479 | 2.329 | 0.785 | 1.234 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Leading the Way | 5.205 | 4.889 | 4.454 | 3.963 | 3.616 | 3.247 | 2.711 | -2.1 | -5.859 | -8.689 | -8.894 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Leading the Way | 4.2 | 4.226 | 4.244 | 4.254 | 4.264 | 4.269 | 4.258 | 3.94 | 3.702 | 3.554 | 3.648 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Leading the Way | 21.926 | 21.743 | 21.478 | 21.199 | 21.038 | 20.869 | 20.564 | 17.456 | 15.081 | 13.392 | 13.733 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Leading the Way | 7.451 | 7.501 | 7.52 | 7.539 | 7.599 | 7.652 | 7.652 | 6.266 | 5.228 | 4.452 | 4.9 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Leading the Way | 12.99 | 12.644 | 12.201 | 11.804 | 11.517 | 11.214 | 10.721 | 6.691 | 3.755 | 1.747 | 2.089 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Leading the Way | 8.455 | 8.422 | 8.307 | 8.139 | 8.028 | 7.899 | 7.642 | 4.401 | 2.008 | 0.285 | 0.695 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Leading the Way | 2.177 | 1.4 | 0.309 | -0.845 | -1.592 | -2.383 | -3.626 | -13.551 | -20.774 | -25.622 | -25.07 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Leading the Way | 0.989 | 0.847 | 0.669 | 0.463 | 0.267 | 0.054 | -0.209 | -1.876 | -2.662 | -3.312 | -3.441 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Leading the Way | 2.862 | 2.739 | 2.56 | 2.336 | 2.137 | 1.906 | 1.587 | -1.579 | -4.176 | -6.098 | -6.394 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Leading the Way | 12.961 | 12.893 | 12.741 | 12.531 | 12.367 | 12.19 | 11.89 | 10.483 | 8.852 | 7.738 | 8.007 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Leading the Way | 14.476 | 14.265 | 14.912 | 14.474 | 14.194 | 13.899 | 13.399 | 8.82 | 5.39 | 2.94 | 3.238 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Leading the Way | 22.157 | 22.112 | 21.951 | 21.669 | 21.359 | 20.934 | 20.299 | 13.788 | 9.138 | 6.473 | 6.884 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Leading the Way | 9.798 | 9.501 | 9.084 | 8.598 | 8.217 | 7.815 | 7.24 | 9.322 | 5.413 | 2.455 | 2.174 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Leading the Way | 1.897 | 1.556 | 1.099 | 0.578 | 0.236 | -0.129 | -0.649 | -4.608 | -7.295 | -9.225 | -9.33 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Leading the Way | 7.982 | 7.598 | 6.957 | 6.167 | 5.75 | 5.313 | 4.509 | -3.194 | -9.223 | -13.602 | -13.091 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Leading the Way | 5.242 | 2.93 | 2.896 | 2.831 | 2.782 | 2.715 | 2.569 | 0.729 | -0.549 | -1.458 | -1.273 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Leading the Way | 7.479 | 7.012 | 6.318 | 5.527 | 4.979 | 4.401 | 3.516 | -3.414 | -8.342 | -11.653 | -11.277 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Leading the Way | 3.365 | 3.089 | 17.358 | 16.848 | 16.446 | 16.012 | 15.31 | 9.148 | 4.509 | 1.294 | 1.677 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Leading the Way | -0.459 | -0.603 | -0.811 | -1.056 | -1.252 | -1.455 | -1.75 | -4.312 | -6.37 | -7.99 | -8.122 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Leading the Way | 2.558 | 2.562 | 2.543 | 2.506 | 2.493 | 2.471 | 2.418 | 1.437 | 0.732 | 0.27 | 0.465 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Leading the Way | 10.365 | 10.077 | 9.61 | 9.049 | 8.665 | 8.26 | 7.623 | 2.596 | -1.152 | -3.747 | -3.425 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Leading the Way | 8.243 | 7.862 | 7.279 | 6.599 | 6.194 | 5.755 | 5.049 | -1.261 | -5.83 | -8.885 | -8.522 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Leading the Way | 11.231 | 11.105 | 10.896 | 10.641 | 10.457 | 10.252 | 9.952 | 7.584 | 5.903 | 4.848 | 4.9 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Leading the Way | 3.616 | 2.692 | 2.683 | 2.614 | 2.589 | 2.526 | 2.329 | -0.517 | -2.703 | -4.149 | -3.694 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Leading the Way | 14.894 | 14.796 | 14.657 | 14.482 | 14.315 | 14.116 | 13.859 | 11.12 | 8.904 | 7.32 | 7.136 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Leading the Way | 4.445 | 4.353 | 4.22 | 4.067 | 3.957 | 3.842 | 3.672 | 2.197 | 1.021 | 0.139 | 0.111 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Leading the Way | 2.056 | 1.985 | 1.869 | 1.731 | 1.641 | 1.546 | 1.383 | -0.173 | -1.353 | -2.193 | -2.051 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Leading the Way | 14.965 | 14.604 | 14.063 | 13.418 | 12.96 | 12.458 | 11.703 | 5.166 | 0.224 | -3.255 | -3.315 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Leading the Way | 2.746 | 2.579 | 4.274 | 3.885 | 3.59 | 3.267 | 2.698 | -3.275 | -7.734 | -11.021 | -10.594 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Leading the Way | 14.811 | 14.732 | 14.58 | 14.385 | 14.324 | 14.252 | 14.07 | 11.488 | 9.458 | 8.049 | 8.423 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Leading the Way | 4.419 | 4.308 | 4.155 | 3.981 | 3.834 | 3.681 | 3.471 | 1.773 | 0.449 | -0.547 | -0.627 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Leading the Way | 4.622 | 4.109 | 3.364 | 2.508 | 1.864 | 1.179 | 0.247 | -6.823 | -11.945 | -15.48 | -15.569 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Leading the Way | 11.569 | 11.192 | 10.653 | 10.043 | 9.625 | 9.189 | 8.566 | 3.651 | -0.016 | -2.639 | -2.691 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Leading the Way | 12.116 | 10.474 | 10.297 | 10.007 | 9.76 | 9.403 | 8.844 | 4.004 | 0.86 | -0.71 | -0.331 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Leading the Way | 0.86 | 0.487 | 0.059 | -0.261 | -0.522 | -0.793 | -1.148 | -3.187 | -4.493 | -5.231 | -5.11 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Leading the Way | 7.293 | 6.502 | 5.443 | 4.276 | 3.471 | 2.635 | 1.464 | -6.745 | -12.709 | -16.715 | -16.905 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Leading the Way | 9.177 | 9.175 | 9.166 | 9.152 | 9.14 | 9.125 | 9.102 | 8.927 | 8.758 | 8.594 | 8.471 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Leading the Way | 1.656 | 1.419 | 1.049 | 0.557 | 0.015 | -0.656 | -1.558 | -8.024 | -12.52 | -14.763 | -14.973 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Leading the Way | 10.373 | 9.948 | 9.392 | 8.857 | 8.516 | 8.15 | 7.532 | 1.62 | -2.988 | -6.296 | -5.974 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Leading the Way | 8.73 | 8.317 | 7.68 | 6.907 | 6.398 | 5.842 | 4.991 | -1.807 | -6.798 | -10.073 | -9.925 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Leading the Way | 1.32 | 1.212 | 1.054 | 0.854 | 0.658 | 0.423 | 0.118 | -2.054 | -3.608 | -4.472 | -4.671 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Leading the Way | 7.196 | 6.844 | 6.308 | 5.675 | 5.23 | 4.767 | 4.039 | -2.409 | -7.441 | -11.199 | -11.053 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Leading the Way | 0.951 | 0.9 | 0.76 | 0.572 | 0.505 | 0.418 | 0.203 | -2.806 | -4.896 | -6.337 | -5.846 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Leading the Way | 1.499 | 1.499 | 1.498 | 1.497 | 1.496 | 1.495 | 1.494 | 1.477 | 1.461 | 1.446 | 1.44 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 24.097 | 24.128 | 24.109 | 24.057 | 24.075 | 24.084 | 24.028 | 22.143 | 20.71 | 19.637 | 20.107 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 33.854 | 33.8 | 33.702 | 33.583 | 33.519 | 33.449 | 33.324 | 31.901 | 30.955 | 30.283 | 30.434 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 20.499 | 20.417 | 20.295 | 20.15 | 20.024 | 19.893 | 19.72 | 18.609 | 17.819 | 17.274 | 17.241 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 14.621 | 14.381 | 14.039 | 13.655 | 13.38 | 13.073 | 12.617 | 9.067 | 6.393 | 4.633 | 4.552 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Leading the Way | 13.548 | 13.203 | 12.733 | 13.197 | 12.717 | 12.222 | 11.559 | 6.887 | 3.345 | 0.845 | 0.701 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Leading the Way | 10.376 | 9.283 | 8.788 | 8.188 | 7.827 | 7.446 | 6.826 | 1.676 | -1.956 | -4.571 | -4.374 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Leading the Way | 1.424 | 15.166 | 14.811 | 14.392 | 13.985 | 13.525 | 12.906 | 8.251 | 4.792 | 2.424 | 2.025 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Leading the Way | 10.584 | 9.891 | 9.125 | 8.611 | 8.296 | 7.964 | 7.404 | 2.332 | -1.589 | -4.371 | -4.01 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Leading the Way | 15.372 | 15.337 | 15.288 | 15.229 | 15.195 | 15.158 | 15.096 | 14.181 | 13.331 | 12.582 | 12.452 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Leading the Way | 3.682 | 2.637 | 1.15 | -0.559 | -1.835 | -3.169 | -5.093 | -17.845 | -26.368 | -32.498 | -32.752 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Leading the Way | 6.057 | 5.346 | 4.409 | 3.488 | 2.883 | 2.255 | 1.336 | -5.085 | -9.565 | -12.339 | -11.853 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Leading the Way | 4.406 | 4.411 | 4.315 | 4.15 | 4.194 | 4.221 | 4.069 | 0.652 | -2.199 | -4.376 | -3.829 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 17.143 | 14.113 | 13.815 | 13.478 | 13.219 | 12.953 | 12.604 | 9.608 | 7.425 | 5.605 | 5.339 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Leading the Way | 14.753 | 14.715 | 14.652 | 14.567 | 14.482 | 14.378 | 14.241 | 12.757 | 11.541 | 10.67 | 10.543 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Leading the Way | 9.232 | 9.009 | 8.721 | 8.368 | 7.997 | 7.561 | 7.02 | 2.675 | -0.799 | -3.177 | -3.956 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Leading the Way | 11.726 | 11.702 | 11.617 | 11.494 | 11.472 | 11.444 | 11.332 | 8.82 | 6.771 | 5.206 | 5.624 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Leading the Way | 11.293 | 11.336 | 11.34 | 11.318 | 11.342 | 11.359 | 11.327 | 10.404 | 9.704 | 9.246 | 9.574 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 3.761 | 3.573 | 3.342 | 3.06 | 2.746 | 2.373 | 1.928 | -1.504 | -4.258 | -6.132 | -6.931 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Leading the Way | 14.723 | 14.635 | 14.492 | 14.311 | 14.224 | 14.12 | 13.923 | 11.574 | 9.66 | 8.294 | 8.347 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Leading the Way | 10.625 | 10.306 | 9.804 | 9.207 | 8.886 | 8.545 | 7.969 | 2.592 | -1.367 | -4.096 | -3.668 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Leading the Way | 9.493 | 9.362 | 9.113 | 8.79 | 8.667 | 8.521 | 8.197 | 4.023 | 0.803 | -1.412 | -0.892 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Leading the Way | 7.107 | 6.753 | 6.185 | 5.492 | 5.023 | 4.505 | 3.706 | -2.755 | -7.34 | -10.249 | -9.814 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Leading the Way | 4.394 | 3.906 | 3.208 | 2.415 | 1.811 | 1.144 | 0.201 | 10.329 | 5.583 | 2.446 | 2.446 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Leading the Way | 10.982 | 10.965 | 10.889 | 10.774 | 10.633 | 10.435 | 10.145 | 8.103 | 6.875 | 6.419 | 6.559 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Leading the Way | 15.371 | 15.052 | 14.55 | 13.941 | 13.616 | 13.277 | 12.702 | 7.594 | 3.739 | 1.028 | 1.336 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Leading the Way | 8.816 | 8.328 | 7.602 | 6.72 | 6.024 | 5.24 | 4.122 | -4.462 | -10.655 | -14.588 | -14.722 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Leading the Way | 3.275 | 3.158 | 2.994 | 3.306 | 3.159 | 3.005 | 2.79 | 1.127 | -0.132 | -1.056 | -1.153 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Leading the Way | 7.103 | 6.872 | 6.485 | 6.026 | 5.675 | 5.307 | 4.674 | 5.857 | 1.348 | -1.962 | -1.461 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Leading the Way | 4.143 | 3.943 | 3.642 | 3.296 | 3.093 | 2.882 | 2.542 | -0.187 | -2.221 | -3.634 | -3.528 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 12.31 | 12.293 | 12.247 | 12.181 | 12.149 | 12.109 | 12.029 | 10.809 | 9.801 | 8.997 | 8.999 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 25.325 | 25.282 | 25.216 | 25.133 | 25.083 | 25.028 | 24.941 | 23.564 | 22.399 | 21.466 | 21.501 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Leading the Way | 14.643 | 14.485 | 14.255 | 13.976 | 13.719 | 13.438 | 13.067 | 10.827 | 9.335 | 8.443 | 8.354 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Leading the Way | 12.69 | 12.743 | 12.772 | 12.783 | 12.812 | 12.836 | 12.829 | 11.675 | 10.773 | 10.089 | 10.428 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Leading the Way | 19.977 | 19.932 | 19.868 | 19.788 | 19.737 | 19.684 | 19.608 | 18.515 | 17.81 | 17.186 | 17.132 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Leading the Way | 6.898 | 6.556 | 6.018 | 5.376 | 4.993 | 4.588 | 3.956 | -0.739 | -3.785 | -5.768 | -5.414 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 21.099 | 21.089 | 20.997 | 20.85 | 20.809 | 20.75 | 20.572 | 17.583 | 15.261 | 13.602 | 14.124 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Leading the Way | 14.006 | 13.926 | 13.784 | 13.615 | 13.586 | 13.552 | 13.408 | 10.574 | 8.271 | 6.563 | 7.037 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Leading the Way | 4.252 | 4.153 | 3.998 | 3.813 | 3.704 | 3.586 | 3.391 | 1.72 | 0.502 | -0.317 | -0.214 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Leading the Way | 0.965 | 0.925 | 0.872 | 0.807 | 0.748 | 0.68 | 0.592 | -0.024 | -0.524 | -0.879 | -1.062 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Leading the Way | 16.228 | 16.138 | 15.987 | 15.791 | 15.654 | 15.492 | 15.241 | 12.258 | 9.909 | 8.163 | 8.164 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 22.162 | 21.96 | 21.641 | 21.257 | 20.964 | 20.654 | 20.161 | 16.226 | 13.371 | 11.44 | 11.727 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 26.324 | 26.224 | 26.063 | 25.87 | 25.751 | 25.626 | 25.403 | 23.272 | 21.648 | 20.494 | 20.69 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Leading the Way | 2.373 | 2.227 | 2.034 | 1.82 | 1.623 | 1.419 | 1.134 | -0.941 | -2.574 | -3.854 | -4.08 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Leading the Way | 2.282 | 2.048 | 1.719 | 1.326 | 1.098 | 0.837 | 0.417 | -4.828 | -9.117 | -12.369 | -12.438 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Leading the Way | 14.335 | 14.278 | 14.167 | 14.016 | 13.891 | 13.727 | 13.481 | 11.627 | 10.431 | 9.734 | 9.73 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Leading the Way | 4.592 | 4.502 | 4.365 | 4.207 | 4.099 | 3.986 | 3.791 | 2.051 | 0.724 | -0.238 | -0.124 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Leading the Way | 14.496 | 14.473 | 14.421 | 14.368 | 14.343 | 14.304 | 14.188 | 12.665 | 11.62 | 10.872 | 11.049 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Leading the Way | 9.126 | 9.249 | 9.349 | 9.428 | 9.517 | 9.592 | 9.634 | 10.172 | 9.82 | 9.647 | 10.02 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Leading the Way | 1.179 | 0.83 | 0.327 | -0.263 | -0.737 | -1.241 | -1.921 | -6.319 | -9.376 | -11.276 | -11.391 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 16.836 | 16.798 | 16.728 | 16.637 | 16.588 | 16.531 | 16.427 | 15.072 | 13.98 | 13.169 | 13.244 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 16.764 | 16.719 | 16.639 | 16.533 | 16.457 | 16.363 | 16.215 | 14.804 | 13.723 | 13.037 | 13.043 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Leading the Way | 4.394 | 3.972 | 3.367 | 2.662 | 2.121 | 1.544 | 0.707 | 9.172 | 4.656 | 1.454 | 1.293 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Leading the Way | 14.347 | 14.24 | 14.079 | 13.881 | 13.769 | 13.646 | 13.44 | 10.942 | 8.982 | 7.508 | 7.584 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Leading the Way | 7.842 | 7.269 | 6.511 | 5.771 | 5.179 | 4.561 | 3.624 | 13.507 | 8.317 | 4.658 | 4.891 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Leading the Way | 4.915 | 4.82 | 4.649 | 4.455 | 4.341 | 4.195 | 3.888 | -0.172 | -3.236 | -5.427 | -4.985 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Leading the Way | 10.372 | 10.062 | 9.555 | 8.927 | 8.536 | 8.127 | 7.415 | 0.546 | -4.954 | -9.094 | -8.811 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Leading the Way | 0.143 | 0.044 | -0.09 | -0.247 | -0.352 | -0.468 | -0.648 | -2.59 | -4.106 | -5.262 | -5.319 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Leading the Way | 13.28 | 12.971 | 12.502 | 11.967 | 11.589 | 11.185 | 10.555 | 5.508 | 1.786 | -0.749 | -0.534 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Leading the Way | 17.504 | 17.494 | 17.464 | 17.42 | 17.392 | 17.356 | 17.288 | 16.037 | 15.061 | 14.348 | 14.533 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Leading the Way | 12.598 | 12.37 | 12.062 | 11.713 | 11.544 | 11.364 | 11.065 | 7.811 | 5.103 | 2.999 | 2.816 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Leading the Way | 6.93 | 6.806 | 6.621 | 6.389 | 6.205 | 6.003 | 5.673 | 2.381 | -0.356 | -2.445 | -2.545 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Leading the Way | 9.393 | 9.257 | 9.024 | 8.711 | 8.492 | 8.222 | 7.759 | 2.962 | -0.921 | -3.655 | -3.728 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Leading the Way | 15.303 | 15.287 | 15.27 | 15.25 | 15.227 | 15.203 | 15.177 | 15.997 | 15.791 | 15.569 | 15.365 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Leading the Way | 16.384 | 16.286 | 16.119 | 15.914 | 15.749 | 15.572 | 15.296 | 12.734 | 10.859 | 9.524 | 9.699 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Leading the Way | 12.83 | 12.666 | 12.414 | 12.11 | 11.904 | 11.691 | 11.325 | 7.777 | 5.219 | 3.203 | 3.308 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Leading the Way | 10.391 | 9.896 | 9.294 | 8.792 | 8.506 | 8.204 | 7.712 | 3.208 | -0.175 | -2.53 | -2.184 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Leading the Way | 9.445 | 8.942 | 8.236 | 7.495 | 7.007 | 6.493 | 5.68 | -0.864 | -5.467 | -8.591 | -8.207 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Leading the Way | 2.197 | 2.243 | 2.279 | 2.306 | 2.334 | 2.355 | 2.361 | 2.161 | 2.023 | 1.968 | 2.115 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Leading the Way | 9.704 | 9.013 | 8.179 | 7.478 | 7.001 | 6.505 | 5.699 | 15.684 | 10.309 | 6.425 | 6.796 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Leading the Way | 4.558 | 4.342 | 4.002 | 3.563 | 3.255 | 2.886 | 2.306 | -4.292 | -9.395 | -13.051 | -12.991 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Leading the Way | 3.317 | 2.901 | 2.313 | 1.633 | 1.133 | 0.618 | -0.112 | -5.986 | -10.447 | -13.783 | -13.914 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Leading the Way | 23.141 | 23.105 | 22.982 | 22.799 | 22.765 | 22.719 | 22.54 | 18.865 | 16.048 | 13.956 | 14.577 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Leading the Way | 6.326 | 6.13 | 5.858 | 5.546 | 5.312 | 5.057 | 4.709 | 1.703 | -0.696 | -2.462 | -2.75 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Leading the Way | 6.75 | 6.741 | 6.725 | 6.703 | 6.692 | 6.679 | 6.656 | 6.42 | 6.257 | 6.153 | 6.185 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Leading the Way | 11.54 | 10.856 | 9.833 | 8.625 | 7.894 | 7.124 | 5.929 | -3.522 | -10.408 | -15.299 | -15.247 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Leading the Way | 21.154 | 21.167 | 21.124 | 21.016 | 20.849 | 20.599 | 20.249 | 17.822 | 16.337 | 15.86 | 15.939 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Leading the Way | 11.218 | 10.967 | 10.575 | 10.119 | 9.846 | 9.553 | 9.065 | 4.393 | 0.875 | -1.561 | -1.184 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Leading the Way | 12.609 | 12.43 | 12.145 | 11.747 | 11.292 | 10.713 | 9.904 | 3.714 | -0.645 | -3.154 | -3.348 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Leading the Way | 0.144 | 0.045 | -0.103 | -0.283 | -0.443 | -0.623 | -0.874 | -3.087 | -4.781 | -6.003 | -6.127 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Leading the Way | 6.903 | 1.037 | 0.68 | 0.265 | -0.049 | -0.38 | -0.846 | 4.457 | 1.943 | 0.239 | 0.173 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Leading the Way | 3.587 | 3.291 | 2.874 | 2.395 | 2.063 | 1.716 | 1.221 | -2.881 | -6.049 | -8.404 | -8.642 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Leading the Way | 12.37 | 12.138 | 11.778 | 11.326 | 10.881 | 10.319 | 9.53 | 3.135 | -1.341 | -3.641 | -3.514 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Leading the Way | 5.489 | 5.231 | 4.831 | 4.394 | 4.132 | 3.837 | 3.355 | -0.443 | -2.924 | -4.468 | -4.115 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Leading the Way | 1.002 | 0.772 | 0.479 | 0.226 | 0.073 | -0.088 | -0.335 | -2.205 | -3.554 | -4.423 | -4.261 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Leading the Way | 12.67 | 12.513 | 12.238 | 11.897 | 11.73 | 11.548 | 11.199 | 7.633 | 5.044 | 3.309 | 3.723 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Leading the Way | 7.197 | 7.25 | 7.281 | 7.314 | 7.36 | 7.398 | 7.404 | 5.85 | 4.716 | 3.863 | 4.351 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Leading the Way | 13.483 | 13.399 | 13.246 | 13.05 | 12.992 | 12.923 | 12.743 | 9.933 | 7.717 | 6.141 | 6.526 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Leading the Way | 6.932 | 6.538 | 5.986 | 5.35 | 4.818 | 4.257 | 3.496 | -1.972 | -5.993 | -8.89 | -9.321 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Leading the Way | 9.714 | 9.642 | 9.459 | 9.178 | 8.958 | 8.646 | 8.143 | 3.762 | 0.781 | -0.747 | -0.512 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Leading the Way | 14.74 | 14.775 | 14.806 | 14.832 | 14.86 | 14.885 | 14.906 | 14.78 | 14.678 | 14.604 | 14.717 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Leading the Way | 5.554 | 5.534 | 5.496 | 5.453 | 5.431 | 5.407 | 5.361 | 4.957 | 4.689 | 4.518 | 4.557 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Leading the Way | 14.011 | 14.04 | 14.044 | 14.03 | 14.036 | 14.039 | 14.015 | 12.67 | 11.641 | 10.882 | 11.244 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Leading the Way | 4.001 | 3.684 | 3.183 | 2.571 | 2.214 | 1.835 | 1.217 | -3.833 | -7.427 | -9.803 | -9.445 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Leading the Way | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Leading the Way | 8.712 | 7.598 | 6.886 | 6.057 | 5.493 | 4.907 | 3.993 | -3.602 | -9.347 | -13.543 | -13.362 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Leading the Way | 8.674 | 8.06 | 7.183 | 6.237 | 22.772 | 22.18 | 21.241 | 13.639 | 8.148 | 4.455 | 4.852 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Leading the Way | 3.249 | 3.331 | 3.381 | 3.402 | 3.425 | 3.437 | 3.374 | 1.352 | -0.327 | -1.64 | -1.217 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Leading the Way | 1.839 | 1.51 | 1.04 | 0.484 | -0.053 | -0.608 | -1.408 | -7.713 | -12.65 | -16.516 | -16.71 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Leading the Way | 14.388 | 14.197 | 13.904 | 13.572 | 13.337 | 13.09 | 12.679 | 8.839 | 5.857 | 3.665 | 3.898 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Leading the Way | 5.601 | 5.074 | 4.274 | 3.325 | 2.722 | 2.076 | 1.112 | -6.778 | -12.619 | -16.608 | -16.57 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Leading the Way | 4.917 | 3.928 | 3.535 | 3.12 | 2.853 | 2.549 | 2.013 | -2.769 | -6.31 | -8.7 | -8.329 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Leading the Way | 14.926 | 14.714 | 14.388 | 14.018 | 13.817 | 13.605 | 13.235 | 10.114 | 7.932 | 6.373 | 6.554 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Leading the Way | 3.493 | 3.163 | 2.65 | 2.046 | 1.671 | 1.26 | 0.599 | 9.524 | 5.361 | 2.592 | 2.909 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Leading the Way | 6.743 | 6.452 | 6.052 | 5.579 | 5.249 | 4.88 | 4.352 | -0.745 | -4.79 | -7.676 | -7.885 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Leading the Way | 8.228 | 7.735 | 7.03 | 6.231 | 5.72 | 5.184 | 4.386 | -1.762 | -6.105 | -8.87 | -8.528 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Leading the Way | 5.937 | 5.58 | 5.064 | 4.465 | 3.964 | 3.441 | 2.735 | -1.725 | -4.898 | -6.961 | -7.037 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Leading the Way | 1.106 | 0.326 | -0.652 | -1.518 | -2.182 | -2.876 | -4.005 | -13.217 | -19.997 | -24.696 | -23.969 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Leading the Way | 9.687 | 9.148 | 8.416 | 7.681 | 7.272 | 6.843 | 6.122 | -0.159 | -4.8 | -7.984 | -7.526 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Leading the Way | 10.623 | 10.112 | 9.422 | 8.731 | 8.211 | 7.637 | 6.774 | 0.134 | -4.618 | -7.597 | -7.357 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Leading the Way | 12.36 | 12.348 | 12.275 | 12.147 | 12.041 | 11.89 | 11.643 | 8.598 | 6.38 | 5.127 | 5.506 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Leading the Way | 8.59 | 8.463 | 8.263 | 8.027 | 7.865 | 7.692 | 7.4 | 4.508 | 2.375 | 0.862 | 1.087 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Leading the Way | 2.883 | 2.806 | 2.655 | 2.452 | 2.324 | 2.158 | 1.885 | -0.771 | -2.699 | -3.77 | -3.551 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Leading the Way | 12.841 | 12.616 | 12.257 | 11.83 | 11.566 | 11.289 | 10.83 | 6.723 | 3.658 | 1.504 | 1.795 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Leading the Way | 18.286 | 18.196 | 18.032 | 17.82 | 17.658 | 17.486 | 17.208 | 15.002 | 13.373 | 12.223 | 12.332 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Leading the Way | 15.454 | 15.34 | 15.165 | 14.952 | 14.858 | 14.758 | 14.568 | 12.085 | 9.992 | 8.398 | 8.48 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Leading the Way | 2.74 | 2.38 | 1.835 | 1.112 | 0.431 | -0.426 | -1.619 | -9.836 | -14.866 | -17.878 | -18.119 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Leading the Way | 9.819 | 9.86 | 9.863 | 9.838 | 9.844 | 9.833 | 9.768 | 7.844 | 6.418 | 5.431 | 5.863 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Leading the Way | 6.129 | 5.973 | 5.738 | 5.448 | 5.261 | 5.038 | 4.685 | 1.406 | -0.926 | -2.523 | -2.52 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Leading the Way | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Leading the Way | 6.776 | 6.194 | 5.411 | 4.602 | 4.09 | 3.533 | 2.689 | -3.808 | -8.252 | -11.163 | -10.967 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Leading the Way | 14.34 | 14.015 | 13.529 | 12.943 | 12.621 | 12.282 | 11.709 | 6.66 | 2.853 | 0.147 | 0.355 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Leading the Way | 3.108 | 2.937 | 2.699 | 2.429 | 2.237 | 2.039 | 1.753 | -0.604 | -2.362 | -3.693 | -3.773 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Leading the Way | 8.762 | 8.407 | 7.89 | 7.213 | 6.564 | 5.75 | 4.663 | -4.578 | -11.468 | -15.478 | -15.979 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Leading the Way | 13.065 | 12.57 | 11.946 | 11.364 | 10.968 | 10.553 | 9.925 | 4.534 | 0.627 | -2.092 | -1.85 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Leading the Way | 4.983 | 4.891 | 4.758 | 4.607 | 4.492 | 4.374 | 4.193 | 2.725 | 1.566 | 0.693 | 0.661 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Leading the Way | 6.033 | 5.538 | 4.829 | 4.009 | 3.448 | 2.865 | 2 | -5.648 | -11.485 | -15.922 | -15.958 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Leading the Way | 9.941 | 9.617 | 9.095 | 8.464 | 8.067 | 7.648 | 6.933 | 0.738 | -3.776 | -6.962 | -6.468 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Leading the Way | 15.547 | 15.241 | 14.835 | 14.436 | 14.143 | 13.841 | 13.378 | 9.832 | 7.144 | 5.227 | 5.395 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Leading the Way | 6.061 | 5.823 | 5.409 | 4.89 | 4.611 | 4.304 | 3.766 | -1.531 | -5.321 | -7.912 | -7.412 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Leading the Way | 12.895 | 12.434 | 11.814 | 11.111 | 10.448 | 9.738 | 8.79 | 1.982 | -3.017 | -6.656 | -7.173 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Leading the Way | 12.783 | 12.713 | 12.596 | 12.448 | 12.388 | 12.322 | 12.185 | 10.282 | 8.892 | 7.842 | 7.999 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Leading the Way | 9.278 | 8.889 | 8.329 | 7.698 | 7.266 | 6.79 | 6.109 | 1.189 | -2.253 | -4.441 | -4.465 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Leading the Way | 11.371 | 11.379 | 11.327 | 11.22 | 11.132 | 11.001 | 10.781 | 8.422 | 6.776 | 5.878 | 6.149 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Leading the Way | 5.568 | 5.472 | 5.262 | 4.968 | 4.794 | 4.561 | 4.156 | -0.173 | -3.242 | -5.066 | -4.644 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Leading the Way | 28.572 | 28.484 | 28.34 | 28.153 | 27.996 | 27.809 | 27.547 | 25.357 | 23.718 | 22.689 | 22.602 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Leading the Way | 3.153 | 2.93 | 2.645 | 2.313 | 2.07 | 1.811 | 1.408 | -2.8 | -6.543 | -9.684 | -10.365 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Leading the Way | 1.901 | 1.863 | 1.802 | 1.73 | 1.672 | 1.61 | 1.527 | 0.969 | 0.553 | 0.245 | 0.173 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Leading the Way | 11.63 | 11.296 | 10.836 | 10.327 | 9.98 | 9.614 | 9.079 | 4.239 | 0.552 | -2.165 | -2.195 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Leading the Way | 9.904 | 9.903 | 9.854 | 9.771 | 9.752 | 9.717 | 9.606 | 7.652 | 6.235 | 5.245 | 5.55 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Leading the Way | 10.723 | 10.637 | 10.456 | 10.205 | 10.084 | 9.951 | 9.607 | 4.286 | -0.199 | -3.717 | -3.213 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Leading the Way | 1.805 | 1.728 | 1.615 | 1.475 | 1.361 | 1.227 | 1.043 | -0.656 | -1.909 | -2.812 | -2.904 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Leading the Way | 11.862 | 11.847 | 11.764 | 11.604 | 11.379 | 11.059 | 10.608 | 6.373 | 3.367 | 1.889 | 2.113 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Leading the Way | 15.675 | 15.626 | 15.542 | 15.457 | 15.406 | 15.343 | 15.225 | 13.753 | 12.668 | 11.951 | 12.152 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Leading the Way | 7.731 | 6.506 | 5.803 | 4.986 | 4.376 | 3.737 | 2.805 | -4.96 | -10.753 | -15.123 | -15.311 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Leading the Way | 11.965 | 11.861 | 11.667 | 11.427 | 11.273 | 11.107 | 10.803 | 8.135 | 6.15 | 4.778 | 5.084 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Leading the Way | 15.91 | 15.941 | 15.852 | 15.635 | 15.317 | 14.845 | 14.165 | 8.789 | 5.246 | 3.963 | 4.259 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Leading the Way | 8.721 | 8.318 | 7.672 | 6.901 | 6.485 | 6.033 | 5.237 | -2.148 | -7.624 | -11.302 | -10.672 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Leading the Way | 4.247 | 4.189 | 4.1 | 3.994 | 3.922 | 3.845 | 3.729 | 2.803 | 2.103 | 1.595 | 1.564 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Leading the Way | 8.799 | 8.395 | 7.831 | 7.249 | 6.942 | 6.614 | 6.029 | 0.531 | -3.304 | -5.856 | -5.24 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 14.483 | 14.309 | 14.033 | 13.686 | 13.458 | 13.201 | 12.806 | 8.44 | 4.931 | 2.265 | 2.154 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 13.457 | 13.316 | 13.085 | 12.783 | 12.577 | 12.343 | 11.98 | 6.9 | 2.569 | -0.865 | -0.97 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Leading the Way | 12.317 | 12.319 | 12.282 | 12.222 | 12.192 | 12.145 | 12.046 | 10.174 | 8.799 | 7.923 | 8.34 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Leading the Way | 8.13 | 8.162 | 8.15 | 8.104 | 8.139 | 8.167 | 8.121 | 6.655 | 5.459 | 4.562 | 4.922 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Leading the Way | 17.514 | 17.383 | 17.175 | 16.925 | 16.77 | 16.603 | 16.351 | 14.361 | 12.924 | 12.009 | 12.13 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Leading the Way | 4.956 | 4.953 | 4.932 | 4.894 | 4.844 | 4.777 | 4.683 | 3.747 | 2.913 | 2.258 | 1.976 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Leading the Way | 2.194 | 1.708 | 1.055 | 0.412 | 0.029 | -0.373 | -1.043 | -6.969 | -11.357 | -14.36 | -13.865 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Leading the Way | 11.473 | 11.068 | 10.522 | 9.969 | 9.592 | 9.2 | 8.575 | 3.31 | -0.625 | -3.355 | -2.982 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Leading the Way | 10.023 | 9.506 | 8.771 | 7.98 | 7.478 | 6.921 | 6.042 | -1.237 | -6.461 | -9.637 | -9.094 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 13.004 | 13.014 | 12.978 | 12.899 | 12.813 | 12.685 | 12.493 | 10.505 | 9.129 | 8.463 | 8.698 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Leading the Way | 16.045 | 15.832 | 15.492 | 15.084 | 14.844 | 14.591 | 14.175 | 10.78 | 8.339 | 6.722 | 6.983 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Leading the Way | 12.848 | 12.736 | 12.529 | 12.261 | 12.053 | 11.829 | 11.44 | 7.539 | 4.699 | 2.695 | 3.132 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Leading the Way | 9.39 | 9.129 | 8.705 | 8.193 | 7.858 | 7.478 | 6.883 | 1.711 | -2.01 | -4.349 | -3.993 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Leading the Way | 11.547 | 9.837 | 9.588 | 9.267 | 9.09 | 8.902 | 8.539 | 5.152 | 2.658 | 0.822 | 1.102 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Leading the Way | 4.124 | 4.001 | 3.83 | 3.643 | 3.49 | 3.33 | 3.105 | 1.394 | 0.14 | -0.753 | -0.763 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Leading the Way | 13.927 | 13.474 | 12.811 | 12.059 | 11.544 | 11.002 | 10.182 | 3.807 | -0.79 | -3.965 | -3.879 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Leading the Way | 2.165 | 1.804 | 1.211 | 0.498 | -0.005 | -0.536 | -1.43 | -9.263 | -15.15 | -19.33 | -18.717 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Leading the Way | 14.589 | 14.306 | 13.883 | 13.411 | 13.1 | 12.767 | 12.249 | 8.19 | 5.234 | 3.248 | 3.414 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Leading the Way | 7.622 | 7.171 | 6.507 | 5.768 | 5.321 | 4.851 | 4.104 | -2.764 | -7.937 | -11.624 | -11.28 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Leading the Way | 18.617 | 18.657 | 18.608 | 18.489 | 18.448 | 18.382 | 18.155 | 13.967 | 10.56 | 8.028 | 8.668 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Leading the Way | 12.575 | 12.433 | 12.218 | 11.977 | 11.781 | 11.567 | 11.263 | 8.87 | 7.176 | 6.129 | 6.342 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Leading the Way | 3.323 | 2.976 | 2.461 | 1.85 | 1.421 | 0.959 | 0.275 | -5.627 | -10.042 | -13.175 | -13.218 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Leading the Way | 3.388 | 2.441 | 1.179 | -0.24 | -1.617 | -3.06 | -4.99 | -17.273 | -26.349 | -32.866 | -33.934 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Leading the Way | 3.907 | 3.457 | 2.818 | 2.149 | 1.664 | 1.151 | 0.288 | 10.081 | 4.893 | 1.056 | 1.382 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Leading the Way | 12.492 | 11.98 | 11.27 | 10.468 | 9.95 | 9.415 | 8.63 | 2.68 | -1.813 | -5.033 | -5.179 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Leading the Way | 21.734 | 18.772 | 18.871 | 18.957 | 19.037 | 19.114 | 19.189 | 18.768 | 18.582 | 18.435 | 18.561 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Leading the Way | 3.44 | 3.1 | 2.617 | 2.017 | 1.464 | 0.781 | -0.117 | -6.691 | -11.17 | -13.909 | -14.408 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Leading the Way | 12.606 | 12.468 | 12.235 | 11.958 | 11.893 | 11.819 | 11.582 | 7.855 | 4.828 | 2.552 | 2.95 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Leading the Way | 14.047 | 14.114 | 14.161 | 14.196 | 14.26 | 14.319 | 14.352 | 14.026 | 13.781 | 13.62 | 13.857 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Leading the Way | 15.002 | 15.042 | 15.057 | 15.053 | 15.078 | 15.099 | 15.085 | 14.109 | 13.382 | 12.841 | 13.112 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Leading the Way | 9.65 | 9.081 | 8.244 | 7.266 | 6.611 | 5.923 | 4.909 | -2.486 | -7.892 | -11.58 | -11.567 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Leading the Way | 15.789 | 15.692 | 15.544 | 15.362 | 15.276 | 15.18 | 14.995 | 12.344 | 10.105 | 8.358 | 8.393 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Leading the Way | 5.507 | 5.416 | 5.237 | 5.003 | 4.92 | 4.825 | 4.587 | 0.552 | -2.679 | -5.069 | -4.514 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Leading the Way | 14.008 | 13.826 | 13.537 | 13.193 | 12.951 | 12.69 | 12.297 | 8.868 | 6.409 | 4.779 | 5.031 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Leading the Way | 18.295 | 14.835 | 14.759 | 14.672 | 14.612 | 14.544 | 14.428 | 13.797 | 13.483 | 13.328 | 13.438 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Leading the Way | 11.563 | 11.326 | 10.993 | 10.626 | 10.385 | 10.129 | 9.75 | 6.71 | 4.429 | 2.859 | 2.813 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Leading the Way | 2.504 | 2.289 | 1.974 | 1.594 | 1.302 | 0.967 | 0.498 | -3.082 | -5.697 | -7.27 | -7.336 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Leading the Way | 10.901 | 10.526 | 9.989 | 9.414 | 9.08 | 8.729 | 8.182 | 4.033 | 1.026 | -0.979 | -0.801 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Leading the Way | 10.039 | 9.717 | 9.207 | 8.601 | 8.249 | 7.87 | 7.237 | 3.015 | -0.57 | -2.976 | -2.592 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Leading the Way | 5.736 | 5.486 | 5.111 | 4.615 | 4.15 | 3.59 | 2.774 | -4.128 | -9.108 | -12.545 | -12.886 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Leading the Way | 16.369 | 16.22 | 16.009 | 15.759 | 15.558 | 15.346 | 15.041 | 12.626 | 10.728 | 9.308 | 9.149 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Leading the Way | 8.836 | 6.995 | 6.462 | 5.798 | 5.305 | 4.728 | 3.813 | 2.502 | -3.777 | -8.109 | -8.287 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Leading the Way | 3.8 | 3.649 | 3.438 | 3.197 | 3.009 | 2.815 | 2.549 | 0.614 | -0.803 | -1.826 | -1.931 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Leading the Way | 14.363 | 14.052 | 13.573 | 13.005 | 12.618 | 12.21 | 11.609 | 7.188 | 4.115 | 2.157 | 2.417 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Leading the Way | -0.322 | -0.562 | -0.901 | -0.292 | -0.617 | -0.967 | -1.47 | -5.511 | -8.371 | -10.43 | -10.447 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Leading the Way | 9.189 | 8.839 | 8.327 | 7.733 | 7.303 | 6.846 | 6.177 | 0.319 | -4.261 | -7.655 | -7.733 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Leading the Way | 7.728 | 7.412 | 6.905 | 6.297 | 5.916 | 5.503 | 4.837 | -1.246 | -5.666 | -8.653 | -8.212 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Leading the Way | 4.997 | 4.495 | 3.772 | 2.933 | 2.344 | 1.723 | 0.824 | -7.529 | -13.93 | -18.787 | -18.903 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Leading the Way | 16.081 | 15.749 | 15.24 | 14.642 | 14.23 | 13.783 | 13.117 | 7.791 | 4.19 | 1.876 | 2.169 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Leading the Way | 7.888 | 7.923 | 7.899 | 7.829 | 7.816 | 7.778 | 7.657 | 5.375 | 3.705 | 2.623 | 3.099 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Leading the Way | 13.822 | 14.519 | 14.103 | 5.651 | 4.92 | 4.16 | 3.017 | -4.198 | -8.476 | -11.832 | -11.967 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Leading the Way | 10.958 | 10.506 | 9.859 | 9.103 | 8.503 | 7.869 | 6.976 | 0.446 | -4.418 | -7.784 | -7.96 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Leading the Way | 6.628 | 6.631 | 6.554 | 6.42 | 6.4 | 6.36 | 6.199 | 3.372 | 1.597 | 0.3 | 0.695 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Leading the Way | 11.781 | 11.366 | 10.752 | 10.04 | 9.594 | 9.127 | 8.397 | 2.534 | -1.672 | -4.533 | -4.216 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Leading the Way | 5.082 | 4.54 | 3.788 | 2.899 | 2.15 | 1.33 | 0.233 | -8.871 | -15.934 | -21.085 | -21.955 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Leading the Way | 10.367 | 10.461 | 10.549 | 10.629 | 10.705 | 10.777 | 10.844 | 10.759 | 10.682 | 10.63 | 10.9 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Leading the Way | 11.306 | 11.406 | 11.478 | 11.521 | 11.533 | 11.512 | 11.454 | 10.365 | 9.653 | 9.398 | 9.714 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Leading the Way | 2.513 | 2.596 | 2.667 | 2.73 | 2.791 | 2.846 | 2.889 | 2.636 | 2.45 | 2.351 | 2.628 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Leading the Way | 6.401 | 6.183 | 5.862 | 5.525 | 5.323 | 5.104 | 4.743 | 1.857 | 0.085 | -1.023 | -0.65 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Leading the Way | 0.606 | 0.407 | 0.142 | -0.147 | -0.395 | -0.66 | -1.022 | -3.573 | -5.461 | -6.755 | -6.913 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Leading the Way | 12.457 | 12.186 | 11.784 | 11.302 | 10.928 | 10.521 | 9.945 | 5.241 | 1.843 | -0.311 | -0.029 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Leading the Way | 12.912 | 10.99 | 10.963 | 10.895 | 10.815 | 10.695 | 10.481 | 7.598 | 6.183 | 5.203 | 5.516 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Leading the Way | 9.202 | 8.836 | 15.333 | 14.832 | 14.495 | 14.138 | 13.568 | 8.826 | 5.351 | 2.949 | 3.24 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Leading the Way | 10.084 | 9.949 | 9.748 | 9.493 | 9.332 | 9.139 | 8.819 | 5.131 | 2.064 | -0.185 | -0.317 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Leading the Way | 3.213 | 1.494 | 0.912 | 0.449 | 0.133 | -0.206 | -0.805 | -6.605 | -11.105 | -14.426 | -14.066 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Leading the Way | 12.593 | 12.566 | 12.515 | 12.448 | 12.424 | 12.396 | 12.331 | 11.183 | 10.171 | 9.331 | 9.304 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Leading the Way | 8.423 | 8.26 | 14.959 | 14.582 | 14.401 | 14.197 | 13.807 | 9.455 | 6.212 | 4.036 | 4.597 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Leading the Way | 4.967 | 3.676 | 2.921 | 2.301 | 1.813 | 1.275 | 0.501 | -5.8 | -10.36 | -13.571 | -13.584 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Leading the Way | 10.191 | 9.726 | 9.021 | 8.198 | 7.736 | 7.254 | 6.456 | -0.27 | -5.28 | -8.734 | -8.344 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Leading the Way | 10.258 | 10.055 | 7.583 | 7.082 | 6.581 | 5.935 | 5.06 | -1.145 | -5.317 | -7.496 | -7.832 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Leading the Way | 8.341 | 7.884 | 7.222 | 6.454 | 5.926 | 5.357 | 4.532 | -1.493 | -5.802 | -8.655 | -8.723 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Leading the Way | 6.837 | 4.796 | 4.089 | 3.322 | 2.85 | 2.343 | 1.49 | -5.399 | -10.064 | -13.328 | -12.93 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Leading the Way | 8.556 | 7.894 | 7.943 | 7.943 | 7.912 | 7.836 | 7.708 | 5.224 | 3.507 | 2.485 | 2.95 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Leading the Way | 18.747 | 18.702 | 18.608 | 18.463 | 18.288 | 18.052 | 17.734 | 15.087 | 13.295 | 12.457 | 12.542 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Leading the Way | 8.668 | 8.55 | 8.312 | 8.011 | 7.863 | 7.703 | 7.374 | 4.043 | 1.466 | -0.388 | -0.036 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Leading the Way | 10.697 | 10.506 | 10.22 | 9.88 | 9.562 | 9.217 | 8.71 | 4.613 | 1.552 | -0.599 | -0.508 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Leading the Way | 12.041 | 11.759 | 11.313 | 10.774 | 10.471 | 10.153 | 9.617 | 4.243 | 0.333 | -2.428 | -1.944 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Leading the Way | 12.303 | 12.274 | 12.19 | 12.071 | 12.029 | 11.969 | 11.833 | 9.817 | 8.295 | 7.294 | 7.612 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Leading the Way | 8.387 | 8.508 | 8.617 | 8.73 | 8.842 | 8.946 | 9.03 | 8.678 | 8.408 | 8.227 | 8.669 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Leading the Way | 8.067 | 6.232 | 6.019 | 5.754 | 5.676 | 5.565 | 5.27 | 1.525 | -1.286 | -3.175 | -2.698 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Leading the Way | 9.965 | 8.795 | 8.871 | 8.928 | 8.992 | 9.049 | 9.083 | 8.127 | 7.437 | 6.929 | 7.339 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Leading the Way | 1.203 | 0.99 | 0.694 | 0.355 | 0.106 | -0.156 | -0.532 | -3.68 | -6.035 | -7.809 | -7.95 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 2.861 | 2.817 | 2.744 | 2.668 | 2.657 | 2.643 | 2.59 | 1.556 | 0.696 | 0.049 | 0.176 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Leading the Way | 12.891 | 12.785 | 12.609 | 12.374 | 12.166 | 11.906 | 11.549 | 8.443 | 6.125 | 4.767 | 4.702 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Leading the Way | 24.496 | 24.539 | 24.575 | 24.6 | 24.618 | 24.634 | 24.646 | 23.9 | 23.292 | 22.73 | 22.76 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Leading the Way | 13.819 | 13.848 | 13.839 | 13.806 | 13.815 | 13.819 | 13.768 | 12.658 | 11.777 | 11.111 | 11.383 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Leading the Way | -1.725 | -1.841 | -2.011 | -2.221 | -2.391 | -2.581 | -2.847 | -5.459 | -7.653 | -9.35 | -9.69 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Leading the Way | 3.242 | 2.941 | 2.508 | 1.95 | 1.443 | 0.821 | -0.028 | -8.062 | -14.208 | -18.331 | -18.779 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Leading the Way | 10.995 | 10.813 | 10.493 | 10.099 | 9.869 | 9.625 | 9.203 | 5.31 | 2.398 | 0.385 | 0.781 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Leading the Way | 11.361 | 11.469 | 11.558 | 11.628 | 11.679 | 11.709 | 11.715 | 11.354 | 11.167 | 11.2 | 11.47 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Leading the Way | 8.099 | 7.665 | 7.011 | 6.233 | 5.691 | 5.099 | 4.191 | -3.536 | -9.311 | -13.263 | -13.076 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Leading the Way | 11.761 | 10.999 | 10.757 | 10.467 | 10.309 | 10.144 | 9.825 | 6.125 | 3.544 | 1.384 | 1.384 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Leading the Way | 4.051 | 3.713 | 3.264 | 2.825 | 2.494 | 2.152 | 1.611 | -2.585 | -5.807 | -8.136 | -7.952 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Leading the Way | 10.988 | 10.798 | 10.458 | 10.021 | 9.726 | 9.415 | 8.871 | 3.87 | -0.023 | -2.904 | -2.652 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Leading the Way | -1.241 | -1.447 | -1.749 | -2.094 | -0.311 | -0.538 | -0.913 | -4.623 | -7.504 | -9.624 | -9.43 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Leading the Way | 15.288 | 15.22 | 15.109 | 14.952 | 14.795 | 14.6 | 14.327 | 11.274 | 8.889 | 7.236 | 7.238 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Leading the Way | 14.374 | 13.705 | 12.981 | 12.503 | 12.122 | 11.712 | 11.095 | 5.956 | 2.133 | -0.475 | -0.278 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Leading the Way | 10.068 | 9.678 | 9.072 | 8.361 | 7.947 | 7.507 | 6.823 | 1.31 | -2.663 | -5.267 | -5.003 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Leading the Way | 23.772 | 23.818 | 23.858 | 23.9 | 23.943 | 23.983 | 24.013 | 23.796 | 23.621 | 23.492 | 23.674 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Leading the Way | 8.541 | 8.575 | 8.6 | 8.631 | 8.66 | 8.686 | 8.697 | 7.409 | 6.536 | 5.846 | 6.152 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Leading the Way | 11.273 | 10.971 | 10.491 | 9.91 | 9.582 | 9.239 | 8.678 | 3.995 | 0.537 | -1.852 | -1.596 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Leading the Way | 4.364 | 4.352 | 4.329 | 4.299 | 4.288 | 4.274 | 4.245 | 3.857 | 3.501 | 3.2 | 3.14 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Leading the Way | 8.842 | 8.73 | 8.568 | 8.373 | 8.241 | 8.097 | 7.883 | 5.456 | 3.379 | 1.722 | 1.53 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Leading the Way | 13.847 | 13.564 | 13.126 | 12.612 | 12.309 | 11.99 | 11.447 | 6.68 | 3.028 | 0.379 | 0.557 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Leading the Way | 10.76 | 10.424 | 9.955 | 9.418 | 9.04 | 8.639 | 8.043 | 3.412 | 0.093 | -2.226 | -2.201 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Leading the Way | 7.836 | 7.459 | 6.903 | 6.24 | 5.658 | 5.037 | 4.182 | -1.729 | -6.016 | -8.998 | -9.223 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Leading the Way | 13.078 | 12.822 | 12.498 | 12.118 | 11.767 | 11.373 | 10.856 | 6.329 | 2.656 | -0.161 | -0.849 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Leading the Way | 7.737 | 7.695 | 7.56 | 7.35 | 7.198 | 6.999 | 6.607 | 1.852 | -1.875 | -4.421 | -3.962 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Leading the Way | 13.762 | 13.499 | 13.088 | 12.604 | 12.333 | 12.047 | 11.578 | 7.545 | 4.538 | 2.461 | 2.678 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Leading the Way | 7.195 | 6.745 | 6.133 | 5.521 | 5.109 | 4.674 | 3.953 | 14.56 | 9.826 | 6.393 | 6.766 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Leading the Way | 7.474 | 7.294 | 7.045 | 6.744 | 6.526 | 6.283 | 5.941 | 1.596 | -2.051 | -4.937 | -5.194 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - System Transformation | 12.952 | 12.66 | 12.454 | 12.393 | 12.336 | 12.271 | 12.199 | 11.762 | 10.882 | 9.519 | 7.432 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - System Transformation | 12.224 | 10.584 | 10.505 | 10.385 | 10.253 | 10.08 | 9.859 | 8.357 | 6.144 | 4.177 | 1.764 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - System Transformation | 11.416 | 11.146 | 10.811 | 10.413 | 9.928 | 9.417 | 8.884 | 6.205 | 3.104 | -0.373 | -4.769 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - System Transformation | 5.954 | 4.576 | 4.577 | 4.535 | 4.471 | 4.376 | 4.233 | 3.458 | 1.463 | -0.166 | -1.928 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 15.301 | 14.897 | 14.461 | 14.063 | 13.672 | 13.273 | 12.863 | 10.983 | 8.863 | 6.285 | 2.468 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 17.117 | 17.105 | 17.085 | 17.064 | 17.04 | 17.011 | 16.978 | 16.788 | 16.473 | 16.077 | 15.504 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - System Transformation | 8.928 | 8.424 | 7.821 | 7.166 | 6.513 | 5.838 | 5.133 | 1.724 | -1.816 | -6.125 | -12.046 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - System Transformation | 17.161 | 17.175 | 17.171 | 17.155 | 17.14 | 17.117 | 17.076 | 16.877 | 15.794 | 14.673 | 13.234 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - System Transformation | 0.974 | 0.765 | 0.498 | 0.187 | -0.15 | -0.504 | -0.876 | -2.743 | -5.63 | -8.767 | -12.888 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - System Transformation | 3.294 | 2.763 | 2.859 | 2.929 | 2.989 | 3.033 | 3.054 | 3.031 | 2.257 | 1.478 | 0.528 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - System Transformation | 11.964 | 11.735 | 11.425 | 11.066 | 10.709 | 10.338 | 9.943 | 9.126 | 6.934 | 4.497 | 1.187 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - System Transformation | 2.516 | 2.184 | 1.832 | 1.503 | 1.14 | 0.736 | 0.275 | -2.088 | -5.288 | -8.047 | -11.184 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - System Transformation | 3.306 | 3.287 | 3.261 | 3.228 | 3.191 | 3.149 | 3.1 | 2.85 | 2.494 | 2.17 | 1.833 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - System Transformation | 15.697 | 15.523 | 15.287 | 15.022 | 14.779 | 14.53 | 14.263 | 13.007 | 11.106 | 8.829 | 5.524 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - System Transformation | 12.996 | 12.453 | 12.392 | 12.318 | 12.249 | 12.173 | 12.086 | 11.625 | 10.776 | 9.781 | 8.512 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - System Transformation | 10.563 | 10.556 | 10.518 | 10.454 | 10.38 | 10.289 | 10.169 | 9.499 | 7.853 | 6.351 | 4.618 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - System Transformation | 15.525 | 15.22 | 14.826 | 14.379 | 13.909 | 13.415 | 12.895 | 10.293 | 7.815 | 5.127 | 1.558 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - System Transformation | 8.324 | 8.336 | 8.33 | 8.308 | 8.281 | 8.242 | 8.188 | 7.766 | 6.704 | 5.673 | 4.368 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - System Transformation | 5.727 | 5.572 | 5.377 | 5.147 | 4.91 | 4.658 | 4.382 | 2.919 | 0.13 | -3.08 | -7.269 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - System Transformation | 21.389 | 21.331 | 21.23 | 21.097 | 20.968 | 20.832 | 20.687 | 19.995 | 19.141 | 18.101 | 16.565 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - System Transformation | 3.624 | 3.474 | 3.306 | 3.128 | 2.961 | 2.788 | 2.604 | 1.601 | 0.036 | -1.805 | -4.227 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - System Transformation | 11.425 | 10.977 | 10.42 | 9.795 | 9.155 | 8.479 | 7.754 | 4.008 | -0.013 | -4.525 | -10.515 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - System Transformation | 9.295 | 8.838 | 8.307 | 7.77 | 7.247 | 6.702 | 6.127 | 3.6 | 0.656 | -2.585 | -7.15 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - System Transformation | 14.593 | 14.35 | 14.062 | 13.777 | 13.467 | 13.148 | 12.822 | 11.325 | 10.052 | 8.45 | 6.142 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - System Transformation | 2.925 | 2.879 | 2.765 | 2.598 | 2.421 | 2.208 | 1.945 | 0.292 | -2.281 | -4.953 | -8.494 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - System Transformation | 5.323 | 5.09 | 4.795 | 4.457 | 4.111 | 3.743 | 3.35 | 1.326 | -0.855 | -2.99 | -5.552 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 15.131 | 15.089 | 15.036 | 14.972 | 14.896 | 14.807 | 14.699 | 14.203 | 13.176 | 12.129 | 10.808 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 4.192 | 1.186 | 1.128 | 1.03 | 0.886 | 0.69 | 0.429 | -1.24 | -4.589 | -7.655 | -11.297 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - System Transformation | 7.357 | 7.24 | 7.065 | 6.838 | 6.585 | 6.292 | 5.947 | 3.807 | 0.63 | -2.339 | -5.889 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - System Transformation | 11.614 | 11.328 | 10.949 | 10.514 | 10.101 | 9.672 | 9.225 | 7.019 | 4.18 | 0.584 | -4.796 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - System Transformation | 5.695 | 5.24 | 4.646 | 3.968 | 3.304 | 2.601 | 1.85 | -2.016 | -6.967 | -12.095 | -18.984 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - System Transformation | 6.871 | 6.852 | 6.829 | 6.804 | 6.778 | 6.752 | 6.723 | 6.583 | 6.285 | 5.981 | 5.626 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - System Transformation | 3.671 | 3.625 | 3.567 | 3.501 | 3.429 | 3.35 | 3.262 | 2.782 | 2.073 | 1.444 | 0.755 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - System Transformation | 11.531 | 11.173 | 10.716 | 10.203 | 9.711 | 9.201 | 8.66 | 6.075 | 3.132 | -0.389 | -5.441 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 13.449 | 13.305 | 13.156 | 12.998 | 12.833 | 12.663 | 12.483 | 11.548 | 9.891 | 8.221 | 6.476 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - System Transformation | 4.597 | 4.483 | 4.341 | 4.183 | 4.028 | 3.87 | 3.705 | 2.928 | 2.141 | 1.307 | 0.205 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 9.331 | 9.007 | 8.583 | 8.109 | 7.655 | 7.181 | 6.675 | 4.244 | 1.062 | -2.507 | -7.54 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - System Transformation | 11.479 | 11.187 | 10.802 | 10.37 | 9.945 | 9.494 | 9.014 | 6.643 | 3.626 | 0.61 | -3.479 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - System Transformation | 9.247 | 9.26 | 9.245 | 9.207 | 9.166 | 9.107 | 9.023 | 8.443 | 7.137 | 5.685 | 3.722 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - System Transformation | 10.156 | 10.116 | 10.03 | 9.915 | 9.793 | 9.656 | 9.494 | 8.75 | 7.606 | 6.649 | 5.526 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - System Transformation | 17.416 | 17.243 | 17.026 | 16.78 | 16.524 | 16.25 | 15.957 | 14.479 | 13.149 | 11.886 | 10.356 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - System Transformation | 7.626 | 22.129 | 21.882 | 21.611 | 21.342 | 21.062 | 20.767 | 19.323 | 17.011 | 14.483 | 10.975 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - System Transformation | 10.039 | 9.579 | 8.981 | 8.3 | 7.641 | 6.967 | 6.279 | 20.192 | 15.979 | 11.081 | 4.203 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - System Transformation | 3.84 | 3.716 | 3.577 | 3.448 | 3.319 | 3.187 | 3.048 | 2.482 | 1.976 | 1.35 | 0.437 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - System Transformation | 5.732 | 4.801 | 3.807 | 2.864 | 1.87 | 0.829 | -0.248 | -4.819 | -8.567 | -12.941 | -19.01 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - System Transformation | 3.632 | 3.193 | 2.638 | 1.991 | 1.264 | 0.495 | -0.319 | -4.411 | -10.342 | -16.043 | -22.978 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - System Transformation | 4.909 | 4.296 | 3.513 | 2.624 | 1.751 | 0.851 | -0.082 | 19.518 | 13.824 | 7.498 | -1.086 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - System Transformation | 4.048 | 4.092 | 4.127 | 4.152 | 4.169 | 4.177 | 4.174 | 4.066 | 3.712 | 3.432 | 3.161 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - System Transformation | 7.899 | 7.475 | 6.895 | 6.209 | 5.502 | 4.734 | 3.894 | 16.311 | 11.21 | 6.363 | 0.155 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - System Transformation | 12.769 | 12.831 | 12.881 | 12.916 | 12.938 | 12.95 | 12.944 | 12.813 | 11.908 | 11.19 | 10.494 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - System Transformation | 9.452 | 9.559 | 9.656 | 9.74 | 9.815 | 9.88 | 9.935 | 10.101 | 9.913 | 9.738 | 9.567 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - System Transformation | 10.983 | 11.019 | 11.051 | 11.091 | 11.116 | 11.122 | 11.098 | 10.837 | 9.137 | 7.505 | 5.558 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - System Transformation | 8.953 | 8.994 | 9.019 | 9.034 | 9.039 | 9.034 | 9.013 | 8.857 | 8.128 | 7.471 | 6.728 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - System Transformation | 10.723 | 10.446 | 10.078 | 9.662 | 9.236 | 8.771 | 8.262 | 5.528 | 2.801 | 0.158 | -3.302 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - System Transformation | 5.075 | 4.998 | 4.897 | 4.784 | 4.664 | 4.54 | 4.413 | 3.841 | 3.419 | 3.133 | 2.902 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - System Transformation | 7.542 | 7.476 | 7.392 | 7.295 | 7.185 | 7.066 | 6.937 | 6.224 | 5.341 | 4.423 | 3.458 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - System Transformation | 12.956 | 12.448 | 11.892 | 11.367 | 10.851 | 10.315 | 9.754 | 7.063 | 3.727 | 0.114 | -4.941 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - System Transformation | 0.781 | 0.764 | 0.738 | 0.705 | 0.667 | 0.623 | 0.573 | 0.28 | -0.156 | -0.555 | -0.961 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - System Transformation | 2.356 | 2.128 | 1.863 | 1.577 | 1.285 | 0.984 | 0.667 | -0.8 | -2.331 | -3.895 | -5.815 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 9.553 | 9.392 | 9.152 | 8.854 | 8.515 | 8.146 | 7.74 | 5.578 | 3.508 | 1.134 | -2.075 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - System Transformation | 8.297 | 8.112 | 7.926 | 7.779 | 7.629 | 7.464 | 7.275 | 6.347 | 4.432 | 2.546 | 0.121 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - System Transformation | 5.105 | 4.78 | 4.396 | 3.983 | 3.575 | 3.148 | 2.691 | 0.441 | -2.642 | -5.928 | -10.16 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - System Transformation | 4.179 | 4.197 | 4.209 | 4.215 | 4.216 | 4.211 | 4.2 | 4.08 | 3.79 | 3.543 | 3.259 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - System Transformation | 21.856 | 21.666 | 21.445 | 21.228 | 21.027 | 20.819 | 20.598 | 19.537 | 17.862 | 15.85 | 12.945 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - System Transformation | 7.364 | 7.382 | 7.389 | 7.397 | 7.404 | 7.399 | 7.373 | 7.174 | 6.08 | 4.99 | 3.627 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - System Transformation | 12.888 | 12.514 | 12.128 | 11.794 | 11.46 | 11.114 | 10.754 | 9.064 | 6.951 | 4.572 | 1.191 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - System Transformation | 8.38 | 8.323 | 8.211 | 8.061 | 7.907 | 7.733 | 7.531 | 6.457 | 4.306 | 2.299 | -0.261 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - System Transformation | 2.009 | 1.23 | 0.321 | -0.587 | -1.437 | -2.317 | -3.245 | -7.596 | -12.501 | -18.187 | -26.426 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - System Transformation | 0.948 | 0.792 | 0.612 | 0.411 | 0.198 | -0.03 | -0.28 | -1.053 | -1.823 | -2.53 | -3.3 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - System Transformation | 2.758 | 2.605 | 2.419 | 2.202 | 1.961 | 1.693 | 1.392 | -0.374 | -3.014 | -5.333 | -7.741 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - System Transformation | 12.911 | 12.824 | 12.677 | 12.487 | 12.289 | 12.081 | 11.858 | 11.901 | 10.61 | 9.261 | 7.441 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - System Transformation | 14.438 | 14.242 | 14.959 | 14.621 | 14.292 | 13.951 | 13.59 | 11.853 | 9.507 | 6.791 | 2.833 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - System Transformation | 22.1 | 22.066 | 21.961 | 21.776 | 21.532 | 21.203 | 20.776 | 17.788 | 12.993 | 9.629 | 6.379 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - System Transformation | 9.711 | 9.405 | 9.027 | 8.602 | 8.162 | 7.703 | 7.219 | 11.791 | 8.599 | 5.156 | 0.724 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - System Transformation | 1.82 | 1.511 | 1.16 | 0.774 | 0.384 | -0.024 | -0.458 | -2.371 | -4.22 | -6.341 | -9.238 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - System Transformation | 7.912 | 7.572 | 7.078 | 6.5 | 5.969 | 5.423 | 4.851 | 2.106 | -1.539 | -6.463 | -14.092 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - System Transformation | 5.204 | 2.885 | 2.858 | 2.809 | 2.743 | 2.661 | 2.557 | 1.971 | 0.829 | -0.247 | -1.577 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - System Transformation | 7.372 | 6.908 | 6.322 | 5.68 | 5.053 | 4.405 | 3.725 | 0.549 | -2.956 | -6.843 | -12.359 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - System Transformation | 3.285 | 2.996 | 17.317 | 16.89 | 16.456 | 15.997 | 15.509 | 13.029 | 9.531 | 5.867 | 0.888 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - System Transformation | -0.501 | -0.662 | -0.864 | -1.093 | -1.316 | -1.544 | -1.783 | -2.924 | -4.638 | -6.436 | -8.783 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - System Transformation | 2.528 | 2.528 | 2.516 | 2.492 | 2.466 | 2.431 | 2.384 | 2.096 | 1.414 | 0.787 | 0.055 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - System Transformation | 10.289 | 10.012 | 9.625 | 9.176 | 8.722 | 8.254 | 7.771 | 5.532 | 2.992 | -0.174 | -4.811 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - System Transformation | 8.188 | 7.858 | 7.423 | 6.934 | 6.459 | 5.957 | 5.415 | 2.743 | -0.334 | -3.906 | -9.014 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - System Transformation | 11.155 | 11.015 | 10.821 | 10.594 | 10.354 | 10.096 | 9.816 | 8.357 | 6.792 | 5.229 | 3.308 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - System Transformation | 3.514 | 2.554 | 2.537 | 2.481 | 2.413 | 2.312 | 2.173 | 1.162 | -0.891 | -2.857 | -5.351 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - System Transformation | 14.831 | 14.726 | 14.597 | 14.44 | 14.263 | 14.06 | 13.825 | 12.374 | 10.017 | 8.008 | 5.944 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - System Transformation | 4.425 | 4.335 | 4.221 | 4.094 | 3.966 | 3.833 | 3.695 | 3.031 | 2.162 | 1.157 | -0.205 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - System Transformation | 2.028 | 1.953 | 1.853 | 1.74 | 1.632 | 1.519 | 1.399 | 0.832 | -0.025 | -1.001 | -2.381 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - System Transformation | 14.858 | 14.49 | 14.024 | 13.498 | 12.986 | 12.439 | 11.847 | 8.768 | 4.834 | 0.8 | -4.496 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - System Transformation | 2.656 | 2.481 | 4.22 | 3.898 | 3.547 | 3.17 | 2.756 | 0.663 | -2.776 | -6.365 | -11.207 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - System Transformation | 14.768 | 14.707 | 14.611 | 14.494 | 14.392 | 14.279 | 14.149 | 13.393 | 12.007 | 10.227 | 7.62 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - System Transformation | 4.397 | 4.288 | 4.154 | 4.003 | 3.842 | 3.676 | 3.502 | 2.67 | 1.602 | 0.489 | -0.915 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - System Transformation | 4.518 | 4.014 | 3.37 | 2.653 | 1.926 | 1.169 | 0.367 | -3.407 | -7.626 | -11.866 | -17.246 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - System Transformation | 11.491 | 11.141 | 10.698 | 10.212 | 9.722 | 9.22 | 8.692 | 6.269 | 3.62 | 0.61 | -3.501 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - System Transformation | 12.055 | 10.43 | 10.327 | 10.155 | 9.932 | 9.63 | 9.239 | 6.732 | 3.56 | 1.231 | -1.124 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - System Transformation | 0.747 | 0.339 | -0.042 | -0.328 | -0.62 | -0.92 | -1.229 | -2.562 | -3.604 | -4.645 | -5.954 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - System Transformation | 7.175 | 6.478 | 5.651 | 4.754 | 3.839 | 2.896 | 1.92 | -2.655 | -6.171 | -10.957 | -17.818 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - System Transformation | 9.114 | 9.079 | 9.036 | 8.987 | 8.933 | 8.874 | 8.81 | 8.435 | 7.982 | 7.515 | 7.033 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - System Transformation | 1.656 | 1.442 | 1.148 | 0.776 | 0.34 | -0.183 | -0.799 | -4.874 | -9.555 | -12.498 | -15.061 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - System Transformation | 10.257 | 9.828 | 9.379 | 8.976 | 8.589 | 8.183 | 7.749 | 5.553 | 2.369 | -1.343 | -6.663 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - System Transformation | 8.648 | 8.255 | 7.732 | 7.131 | 6.556 | 5.949 | 5.299 | 1.978 | -1.7 | -5.711 | -11.271 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - System Transformation | 1.284 | 1.171 | 1.027 | 0.853 | 0.657 | 0.432 | 0.176 | -1.395 | -3.136 | -4.421 | -5.62 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - System Transformation | 7.093 | 6.728 | 6.254 | 5.719 | 5.199 | 4.663 | 4.103 | 1.472 | -2.199 | -6.408 | -12.296 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - System Transformation | 0.86 | 0.797 | 0.688 | 0.553 | 0.427 | 0.282 | 0.107 | -0.758 | -2.542 | -4.42 | -6.871 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - System Transformation | 1.496 | 1.494 | 1.492 | 1.489 | 1.486 | 1.483 | 1.479 | 1.458 | 1.429 | 1.4 | 1.371 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 23.988 | 24.01 | 24.005 | 23.973 | 23.929 | 23.874 | 23.799 | 23.396 | 22.129 | 20.719 | 18.875 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 33.829 | 33.781 | 33.707 | 33.62 | 33.528 | 33.43 | 33.317 | 32.833 | 32.068 | 31.285 | 30.262 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 20.471 | 20.381 | 20.264 | 20.128 | 19.986 | 19.84 | 19.69 | 19.024 | 18.388 | 17.823 | 17.192 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 14.567 | 14.331 | 14.046 | 13.741 | 13.431 | 13.098 | 12.738 | 10.809 | 8.71 | 6.511 | 3.608 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - System Transformation | 13.459 | 13.163 | 12.781 | 13.331 | 12.811 | 12.274 | 11.725 | 9.138 | 6.917 | 4.136 | 0.424 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - System Transformation | 10.323 | 9.254 | 8.861 | 8.404 | 7.965 | 7.511 | 7.029 | 4.955 | 2.522 | -0.387 | -4.617 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - System Transformation | 1.368 | 15.098 | 14.768 | 14.395 | 13.99 | 13.547 | 13.06 | 10.389 | 7.062 | 4.281 | 1.212 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - System Transformation | 10.355 | 9.604 | 8.962 | 8.566 | 8.196 | 7.813 | 7.411 | 5.493 | 2.921 | -0.259 | -4.94 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - System Transformation | 15.31 | 15.25 | 15.182 | 15.107 | 15.033 | 14.953 | 14.867 | 14.371 | 13.454 | 12.406 | 11.118 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - System Transformation | 3.499 | 2.445 | 1.135 | -0.311 | -1.738 | -3.211 | -4.74 | -10.87 | -17.072 | -23.915 | -33.175 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - System Transformation | 5.905 | 5.23 | 4.489 | 3.791 | 3.087 | 2.365 | 1.626 | -1.672 | -4.188 | -7.81 | -13.239 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - System Transformation | 4.293 | 4.29 | 4.24 | 4.157 | 4.106 | 4.037 | 3.941 | 3.189 | 1.365 | -1.299 | -5.538 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 17.086 | 14.043 | 13.758 | 13.444 | 13.134 | 12.815 | 12.476 | 11.115 | 9.114 | 7.047 | 4.572 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - System Transformation | 14.686 | 14.632 | 14.56 | 14.471 | 14.361 | 14.235 | 14.088 | 13.17 | 11.74 | 10.498 | 9.25 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - System Transformation | 9.125 | 8.87 | 8.574 | 8.233 | 7.849 | 7.416 | 6.926 | 3.902 | -0.087 | -3.197 | -6.051 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - System Transformation | 11.674 | 11.659 | 11.609 | 11.535 | 11.465 | 11.386 | 11.287 | 10.755 | 9.139 | 7.288 | 4.755 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - System Transformation | 11.239 | 11.271 | 11.28 | 11.271 | 11.257 | 11.233 | 11.198 | 10.976 | 10.434 | 9.853 | 9.107 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 3.644 | 3.409 | 3.145 | 2.844 | 2.505 | 2.121 | 1.687 | -1.04 | -4.586 | -7.362 | -9.867 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - System Transformation | 14.658 | 14.564 | 14.444 | 14.306 | 14.179 | 14.038 | 13.876 | 12.866 | 11.261 | 9.429 | 6.985 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - System Transformation | 10.588 | 10.318 | 9.947 | 9.523 | 9.13 | 8.723 | 8.287 | 6.271 | 3.68 | 0.496 | -4.187 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - System Transformation | 9.428 | 9.323 | 9.158 | 8.956 | 8.78 | 8.585 | 8.359 | 7.063 | 4.8 | 2.046 | -1.922 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - System Transformation | 6.984 | 6.632 | 6.159 | 5.611 | 5.077 | 4.511 | 3.901 | 0.8 | -2.756 | -6.516 | -11.671 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - System Transformation | 4.269 | 3.774 | 3.173 | 2.524 | 1.867 | 1.163 | 0.406 | 13.859 | 9.951 | 6.055 | 1.21 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - System Transformation | 10.933 | 10.9 | 10.835 | 10.744 | 10.614 | 10.443 | 10.227 | 8.84 | 7.365 | 6.591 | 6.114 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - System Transformation | 15.333 | 15.055 | 14.675 | 14.236 | 13.839 | 13.433 | 13.008 | 11.021 | 8.761 | 5.649 | 0.804 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - System Transformation | 8.744 | 8.277 | 7.67 | 6.968 | 6.254 | 5.478 | 4.63 | 0.026 | -5.228 | -9.948 | -15.75 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - System Transformation | 3.243 | 3.118 | 2.963 | 3.292 | 3.122 | 2.946 | 2.762 | 1.866 | 0.785 | -0.312 | -1.709 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - System Transformation | 6.995 | 6.731 | 6.374 | 5.969 | 5.559 | 5.133 | 4.689 | 9.59 | 6.271 | 2.509 | -2.795 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - System Transformation | 4.102 | 3.931 | 3.704 | 3.452 | 3.201 | 2.945 | 2.68 | 1.448 | 0.287 | -1.334 | -3.836 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 12.232 | 12.186 | 12.122 | 12.043 | 11.959 | 11.864 | 11.755 | 11.141 | 10.045 | 8.869 | 7.442 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 25.296 | 25.255 | 25.201 | 25.135 | 25.069 | 24.998 | 24.917 | 24.482 | 23.458 | 22.388 | 21.065 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - System Transformation | 14.534 | 14.385 | 14.192 | 13.958 | 13.67 | 13.363 | 13.039 | 11.466 | 10.261 | 9.053 | 7.659 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - System Transformation | 12.633 | 12.668 | 12.688 | 12.691 | 12.688 | 12.676 | 12.65 | 12.474 | 11.516 | 10.622 | 9.578 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - System Transformation | 19.931 | 19.865 | 19.785 | 19.691 | 19.595 | 19.492 | 19.376 | 18.959 | 18.208 | 17.426 | 16.524 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - System Transformation | 6.806 | 6.531 | 6.146 | 5.689 | 5.201 | 4.695 | 4.168 | 1.977 | 0.228 | -2.251 | -5.933 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 20.989 | 20.959 | 20.881 | 20.767 | 20.659 | 20.532 | 20.376 | 19.466 | 17.426 | 15.24 | 12.325 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - System Transformation | 13.946 | 13.873 | 13.779 | 13.679 | 13.608 | 13.53 | 13.435 | 12.874 | 11.271 | 9.231 | 6.256 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - System Transformation | 4.226 | 4.129 | 4.003 | 3.862 | 3.731 | 3.594 | 3.449 | 2.731 | 1.906 | 0.937 | -0.493 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - System Transformation | 0.913 | 0.849 | 0.775 | 0.693 | 0.605 | 0.507 | 0.401 | -0.23 | -0.95 | -1.595 | -2.219 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - System Transformation | 16.15 | 16.048 | 15.911 | 15.743 | 15.565 | 15.366 | 15.134 | 13.852 | 11.595 | 9.399 | 6.812 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 22.118 | 21.909 | 21.626 | 21.298 | 20.973 | 20.635 | 20.281 | 18.602 | 16.495 | 14.22 | 11.058 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 26.301 | 26.204 | 26.073 | 25.922 | 25.78 | 25.634 | 25.48 | 24.737 | 23.641 | 22.305 | 20.341 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - System Transformation | 2.328 | 2.165 | 1.973 | 1.764 | 1.542 | 1.312 | 1.075 | -0.078 | -1.448 | -2.907 | -4.777 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - System Transformation | 2.195 | 1.986 | 1.737 | 1.456 | 1.181 | 0.878 | 0.531 | -1.512 | -5.084 | -8.883 | -13.746 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - System Transformation | 14.29 | 14.224 | 14.128 | 14.007 | 13.868 | 13.699 | 13.498 | 12.403 | 11.166 | 10.144 | 9.037 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - System Transformation | 4.57 | 4.479 | 4.362 | 4.233 | 4.108 | 3.98 | 3.846 | 3.202 | 2.285 | 1.199 | -0.389 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - System Transformation | 14.451 | 14.41 | 14.365 | 14.326 | 14.282 | 14.225 | 14.15 | 13.721 | 12.843 | 11.949 | 10.766 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - System Transformation | 9.049 | 9.139 | 9.212 | 9.267 | 9.312 | 9.341 | 9.354 | 10.236 | 9.661 | 9.114 | 8.464 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - System Transformation | 1.126 | 0.788 | 0.352 | -0.145 | -0.656 | -1.188 | -1.745 | -4.439 | -6.805 | -9.158 | -12.149 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 16.799 | 16.759 | 16.702 | 16.632 | 16.562 | 16.484 | 16.394 | 15.89 | 14.986 | 13.973 | 12.647 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 16.729 | 16.681 | 16.613 | 16.53 | 16.44 | 16.336 | 16.214 | 15.446 | 14.433 | 13.474 | 12.323 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - System Transformation | 4.328 | 3.909 | 3.381 | 2.79 | 2.2 | 1.584 | 0.933 | 12.593 | 9.074 | 5.428 | 0.636 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - System Transformation | 14.287 | 14.174 | 14.035 | 13.878 | 13.732 | 13.575 | 13.4 | 12.491 | 10.823 | 8.995 | 6.653 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - System Transformation | 7.703 | 7.094 | 6.424 | 5.786 | 5.135 | 4.462 | 3.765 | 17.551 | 13.835 | 9.8 | 4.165 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - System Transformation | 4.816 | 4.717 | 4.595 | 4.466 | 4.317 | 4.138 | 3.922 | 2.663 | 0.16 | -2.454 | -5.862 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - System Transformation | 10.287 | 9.979 | 9.552 | 9.055 | 8.587 | 8.105 | 7.603 | 5.158 | 1.469 | -3.081 | -9.785 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - System Transformation | 0.092 | -0.008 | -0.125 | -0.259 | -0.397 | -0.547 | -0.714 | -1.61 | -2.939 | -4.393 | -6.211 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - System Transformation | 13.236 | 12.938 | 12.553 | 12.13 | 11.708 | 11.267 | 10.803 | 8.564 | 5.94 | 3.065 | -0.994 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - System Transformation | 17.469 | 17.458 | 17.438 | 17.406 | 17.366 | 17.32 | 17.26 | 16.914 | 15.994 | 15.149 | 14.168 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - System Transformation | 12.548 | 12.364 | 12.15 | 11.916 | 11.679 | 11.43 | 11.164 | 9.745 | 8.047 | 5.588 | 2.003 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - System Transformation | 6.874 | 6.743 | 6.578 | 6.382 | 6.174 | 5.948 | 5.706 | 4.32 | 2.226 | -0.163 | -3.374 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - System Transformation | 9.313 | 9.17 | 8.976 | 8.737 | 8.492 | 8.209 | 7.881 | 5.719 | 2.392 | -0.963 | -5.287 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - System Transformation | 15.237 | 15.186 | 15.131 | 15.071 | 15.006 | 14.937 | 14.864 | 15.438 | 14.91 | 14.364 | 13.817 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - System Transformation | 16.346 | 16.244 | 16.096 | 15.918 | 15.728 | 15.527 | 15.311 | 14.263 | 12.724 | 11.222 | 9.28 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - System Transformation | 12.777 | 12.615 | 12.406 | 12.168 | 11.931 | 11.685 | 11.425 | 10.404 | 8.782 | 7.075 | 4.9 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - System Transformation | 10.259 | 9.759 | 9.281 | 8.913 | 8.566 | 8.208 | 7.829 | 6.08 | 3.888 | 1.146 | -2.867 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - System Transformation | 9.345 | 8.844 | 8.259 | 7.673 | 7.109 | 6.525 | 5.91 | 3.088 | -0.104 | -3.681 | -8.81 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - System Transformation | 2.165 | 2.197 | 2.221 | 2.238 | 2.249 | 2.253 | 2.25 | 2.173 | 1.949 | 1.772 | 1.595 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - System Transformation | 9.526 | 8.803 | 8.105 | 7.552 | 7.016 | 6.464 | 5.892 | 20.213 | 16.62 | 12.349 | 6.142 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - System Transformation | 4.448 | 4.24 | 3.969 | 3.639 | 3.298 | 2.908 | 2.451 | -0.246 | -4.841 | -9.192 | -14.427 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - System Transformation | 3.246 | 2.839 | 2.33 | 1.762 | 1.202 | 0.631 | 0.039 | -2.634 | -5.931 | -9.588 | -14.501 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - System Transformation | 23.066 | 23.034 | 22.955 | 22.842 | 22.747 | 22.639 | 22.501 | 21.755 | 19.529 | 17.044 | 13.673 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - System Transformation | 6.194 | 5.966 | 5.694 | 5.389 | 5.07 | 4.73 | 4.362 | 2.399 | -0.011 | -2.542 | -5.534 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - System Transformation | 6.746 | 6.736 | 6.722 | 6.705 | 6.69 | 6.673 | 6.655 | 6.564 | 6.432 | 6.298 | 6.112 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - System Transformation | 11.489 | 10.901 | 10.116 | 9.223 | 8.362 | 7.473 | 6.539 | 2.362 | -2.005 | -7.468 | -15.472 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - System Transformation | 21.13 | 21.143 | 21.122 | 21.056 | 20.941 | 20.768 | 20.533 | 18.818 | 16.918 | 15.97 | 15.451 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - System Transformation | 11.136 | 10.893 | 10.577 | 10.228 | 9.901 | 9.558 | 9.19 | 7.372 | 4.913 | 2.079 | -1.959 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - System Transformation | 12.576 | 12.42 | 12.203 | 11.913 | 11.542 | 11.084 | 10.534 | 7.06 | 2.752 | -0.413 | -3.546 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - System Transformation | 0.091 | -0.028 | -0.179 | -0.354 | -0.538 | -0.738 | -0.958 | -2.167 | -3.898 | -5.411 | -7.113 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - System Transformation | 6.82 | 1.018 | 0.72 | 0.381 | 0.017 | -0.362 | -0.754 | 6.036 | 4.279 | 2.221 | -0.539 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - System Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - System Transformation | 3.515 | 3.222 | 2.857 | 2.453 | 2.047 | 1.626 | 1.182 | -0.975 | -3.518 | -6.359 | -10.1 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - System Transformation | 12.321 | 12.112 | 11.843 | 11.525 | 11.156 | 10.705 | 10.162 | 6.53 | 2.095 | -0.957 | -3.911 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - System Transformation | 5.4 | 5.15 | 4.837 | 4.51 | 4.179 | 3.822 | 3.431 | 1.674 | -0.11 | -2.158 | -5 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - System Transformation | 0.951 | 0.724 | 0.491 | 0.3 | 0.106 | -0.094 | -0.302 | -1.228 | -2.077 | -3.226 | -4.947 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - System Transformation | 12.611 | 12.457 | 12.24 | 11.989 | 11.766 | 11.531 | 11.274 | 9.971 | 8.159 | 5.995 | 2.819 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - System Transformation | 7.101 | 7.119 | 7.13 | 7.141 | 7.142 | 7.132 | 7.098 | 6.9 | 5.572 | 4.425 | 3.198 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - System Transformation | 13.43 | 13.373 | 13.284 | 13.171 | 13.069 | 12.955 | 12.821 | 12.015 | 10.551 | 8.634 | 5.838 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - System Transformation | 6.798 | 6.353 | 5.805 | 5.195 | 4.574 | 3.93 | 3.254 | -0.054 | -3.781 | -7.369 | -11.719 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - System Transformation | 9.671 | 9.62 | 9.508 | 9.341 | 9.145 | 8.885 | 8.55 | 6.252 | 3.412 | 1.238 | -1.144 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - System Transformation | 14.714 | 14.738 | 14.757 | 14.772 | 14.784 | 14.793 | 14.798 | 14.793 | 14.599 | 14.419 | 14.224 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - System Transformation | 5.541 | 5.519 | 5.489 | 5.455 | 5.42 | 5.382 | 5.34 | 5.13 | 4.931 | 4.7 | 4.359 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - System Transformation | 13.956 | 13.977 | 13.982 | 13.971 | 13.953 | 13.927 | 13.887 | 13.668 | 12.617 | 11.66 | 10.591 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - System Transformation | 3.944 | 3.66 | 3.271 | 2.818 | 2.393 | 1.952 | 1.487 | -0.662 | -2.905 | -5.79 | -10.094 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - System Transformation | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - System Transformation | 8.603 | 7.497 | 6.895 | 6.224 | 5.579 | 4.916 | 4.229 | 1.07 | -2.837 | -7.563 | -14.329 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - System Transformation | 8.603 | 8.047 | 7.369 | 6.668 | 23.096 | 22.407 | 21.684 | 18.328 | 14.93 | 10.664 | 4.23 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - System Transformation | 3.172 | 3.23 | 3.266 | 3.276 | 3.263 | 3.236 | 3.189 | 2.816 | 1.271 | -0.326 | -2.35 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - System Transformation | 1.767 | 1.425 | 0.981 | 0.461 | -0.112 | -0.703 | -1.305 | -4.08 | -7.8 | -11.854 | -17.229 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - System Transformation | 14.335 | 14.14 | 13.891 | 13.621 | 13.353 | 13.075 | 12.784 | 11.393 | 9.263 | 6.851 | 3.437 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - System Transformation | 5.557 | 5.113 | 4.503 | 3.793 | 3.083 | 2.34 | 1.547 | -2.328 | -6.35 | -11.039 | -17.617 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - System Transformation | 4.78 | 3.763 | 3.431 | 3.101 | 2.773 | 2.414 | 2.022 | -0.039 | -2.612 | -5.555 | -9.735 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - System Transformation | 14.881 | 14.679 | 14.421 | 14.144 | 13.89 | 13.628 | 13.349 | 12.168 | 10.782 | 9.026 | 6.37 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - System Transformation | 3.451 | 3.154 | 2.756 | 2.308 | 1.876 | 1.418 | 0.923 | 13.156 | 10.181 | 6.97 | 2.451 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - System Transformation | 6.642 | 6.38 | 6.066 | 5.703 | 5.319 | 4.9 | 4.438 | 1.844 | -1.472 | -5.071 | -9.567 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - System Transformation | 8.154 | 7.751 | 7.237 | 6.654 | 6.057 | 5.436 | 4.785 | 1.682 | -0.803 | -4.188 | -9.2 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - System Transformation | 5.82 | 5.492 | 5.061 | 4.565 | 4.011 | 3.441 | 2.862 | 0.198 | -1.857 | -4.272 | -7.504 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - System Transformation | 0.871 | 0.015 | -0.856 | -1.603 | -2.346 | -3.115 | -3.91 | -7.648 | -12.477 | -17.939 | -25.673 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - System Transformation | 9.575 | 9.055 | 8.477 | 7.936 | 7.44 | 6.93 | 6.395 | 3.905 | 1.054 | -2.659 | -8.299 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - System Transformation | 10.531 | 10.025 | 9.459 | 8.919 | 8.371 | 7.784 | 7.15 | 3.878 | 0.309 | -3.2 | -7.873 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - System Transformation | 12.312 | 12.304 | 12.261 | 12.182 | 12.084 | 11.95 | 11.772 | 10.467 | 8.173 | 6.435 | 4.665 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - System Transformation | 8.554 | 8.424 | 8.252 | 8.059 | 7.869 | 7.67 | 7.455 | 6.387 | 4.724 | 3.008 | 0.681 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - System Transformation | 2.857 | 2.81 | 2.723 | 2.602 | 2.464 | 2.296 | 2.094 | 0.769 | -0.826 | -2.323 | -4.17 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - System Transformation | 12.779 | 12.553 | 12.252 | 11.913 | 11.6 | 11.276 | 10.935 | 9.333 | 7.213 | 4.733 | 1.133 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - System Transformation | 18.255 | 18.155 | 18.005 | 17.82 | 17.635 | 17.442 | 17.24 | 16.28 | 15.111 | 13.83 | 11.989 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - System Transformation | 15.389 | 15.317 | 15.216 | 15.089 | 14.938 | 14.776 | 14.606 | 13.664 | 12.493 | 10.564 | 7.705 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - System Transformation | 2.652 | 2.353 | 1.961 | 1.459 | 0.856 | 0.129 | -0.738 | -5.112 | -9.77 | -13.429 | -17.225 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - System Transformation | 9.742 | 9.77 | 9.778 | 9.762 | 9.735 | 9.689 | 9.617 | 9.136 | 7.698 | 6.382 | 4.882 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - System Transformation | 6.06 | 5.899 | 5.697 | 5.465 | 5.24 | 4.987 | 4.697 | 3.16 | 1.033 | -1.075 | -3.661 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - System Transformation | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - System Transformation | 6.66 | 6.119 | 5.521 | 4.934 | 4.344 | 3.721 | 3.052 | -0.084 | -3.013 | -6.405 | -11.235 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - System Transformation | 14.27 | 13.972 | 13.596 | 13.166 | 12.779 | 12.38 | 11.958 | 9.881 | 7.599 | 4.553 | -0.181 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - System Transformation | 3.067 | 2.891 | 2.679 | 2.446 | 2.223 | 1.993 | 1.752 | 0.648 | -0.753 | -2.253 | -4.237 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - System Transformation | 8.714 | 8.42 | 8.047 | 7.578 | 7.026 | 6.359 | 5.56 | 0.167 | -6.731 | -11.853 | -16.857 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - System Transformation | 12.943 | 12.433 | 11.911 | 11.45 | 11.009 | 10.553 | 10.071 | 7.807 | 5.004 | 1.978 | -2.226 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - System Transformation | 4.956 | 4.855 | 4.73 | 4.593 | 4.462 | 4.327 | 4.188 | 3.527 | 2.662 | 1.67 | 0.286 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - System Transformation | 5.904 | 5.406 | 4.791 | 4.11 | 3.458 | 2.787 | 2.081 | -1.13 | -5.534 | -10.435 | -17.077 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - System Transformation | 9.853 | 9.526 | 9.084 | 8.582 | 8.117 | 7.636 | 7.132 | 4.869 | 1.777 | -1.878 | -7.192 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - System Transformation | 15.475 | 15.158 | 14.809 | 14.479 | 14.153 | 13.821 | 13.482 | 11.978 | 10.226 | 8.081 | 4.953 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - System Transformation | 5.986 | 5.774 | 5.463 | 5.089 | 4.735 | 4.358 | 3.945 | 1.993 | -0.683 | -3.763 | -8.119 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - System Transformation | 12.778 | 12.298 | 11.721 | 11.078 | 10.368 | 9.618 | 8.827 | 5.037 | 0.71 | -3.431 | -8.354 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - System Transformation | 12.72 | 12.655 | 12.569 | 12.464 | 12.361 | 12.248 | 12.12 | 11.514 | 10.44 | 9.126 | 7.364 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - System Transformation | 9.239 | 8.901 | 8.475 | 8.006 | 7.52 | 7.003 | 6.446 | 3.775 | 1.261 | -1.424 | -4.996 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - System Transformation | 11.317 | 11.319 | 11.284 | 11.21 | 11.115 | 10.986 | 10.817 | 9.667 | 7.939 | 6.618 | 5.239 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - System Transformation | 5.505 | 5.448 | 5.331 | 5.157 | 4.954 | 4.705 | 4.397 | 2.465 | -0.098 | -2.545 | -5.571 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - System Transformation | 28.522 | 28.431 | 28.306 | 28.152 | 27.979 | 27.782 | 27.558 | 26.238 | 24.642 | 23.362 | 22.094 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - System Transformation | 3.003 | 2.718 | 2.4 | 2.057 | 1.722 | 1.368 | 0.991 | -1.173 | -4.653 | -8.579 | -13.607 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - System Transformation | 1.859 | 1.802 | 1.729 | 1.646 | 1.558 | 1.466 | 1.369 | 0.898 | 0.402 | -0.075 | -0.583 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - System Transformation | 11.531 | 11.212 | 10.836 | 10.435 | 10.029 | 9.607 | 9.157 | 6.998 | 4.236 | 1.154 | -2.945 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - System Transformation | 9.854 | 9.846 | 9.812 | 9.759 | 9.708 | 9.643 | 9.555 | 9.01 | 7.768 | 6.532 | 4.933 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - System Transformation | 10.655 | 10.582 | 10.46 | 10.297 | 10.136 | 9.959 | 9.759 | 8.58 | 5.464 | 1.657 | -3.817 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - System Transformation | 1.764 | 1.683 | 1.581 | 1.459 | 1.328 | 1.18 | 1.01 | 0.129 | -1.142 | -2.305 | -3.591 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - System Transformation | 11.826 | 11.819 | 11.77 | 11.668 | 11.509 | 11.282 | 10.979 | 8.637 | 5.181 | 3.074 | 1.41 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - System Transformation | 15.621 | 15.558 | 15.485 | 15.416 | 15.344 | 15.259 | 15.159 | 14.579 | 13.573 | 12.642 | 11.498 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - System Transformation | 7.632 | 6.406 | 5.79 | 5.102 | 4.419 | 3.71 | 2.965 | -0.405 | -4.877 | -9.665 | -15.969 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - System Transformation | 11.896 | 11.771 | 11.592 | 11.384 | 11.182 | 10.97 | 10.747 | 9.672 | 8.254 | 6.517 | 3.964 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - System Transformation | 15.828 | 15.841 | 15.774 | 15.619 | 15.373 | 15.017 | 14.546 | 10.851 | 6.343 | 3.921 | 2.336 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - System Transformation | 8.616 | 8.238 | 7.735 | 7.169 | 6.653 | 6.112 | 5.531 | 2.581 | -1.07 | -5.508 | -12.106 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - System Transformation | 4.223 | 4.158 | 4.073 | 3.978 | 3.885 | 3.787 | 3.684 | 3.175 | 2.577 | 1.922 | 1.048 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - System Transformation | 8.67 | 8.262 | 7.81 | 7.38 | 6.995 | 6.592 | 6.16 | 4.139 | 1.546 | -1.624 | -6.251 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 14.301 | 14.108 | 13.857 | 13.555 | 13.226 | 12.867 | 12.47 | 10.321 | 7.184 | 3.706 | -0.613 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 13.282 | 13.105 | 12.874 | 12.593 | 12.297 | 11.972 | 11.601 | 9.473 | 5.294 | 1.012 | -4.096 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - System Transformation | 12.248 | 12.247 | 12.223 | 12.181 | 12.128 | 12.059 | 11.966 | 11.37 | 9.971 | 8.758 | 7.414 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - System Transformation | 8.061 | 8.078 | 8.07 | 8.042 | 8.026 | 8.002 | 7.964 | 7.688 | 6.782 | 5.569 | 3.764 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - System Transformation | 17.496 | 17.388 | 17.234 | 17.054 | 16.87 | 16.677 | 16.474 | 15.504 | 14.594 | 13.437 | 11.752 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - System Transformation | 4.814 | 4.738 | 4.645 | 4.533 | 4.405 | 4.257 | 4.09 | 3.012 | 1.499 | 0.103 | -1.274 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - System Transformation | 2.058 | 1.564 | 1.03 | 0.536 | 0.078 | -0.395 | -0.891 | -3.246 | -6.116 | -9.679 | -14.948 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - System Transformation | 11.372 | 10.97 | 10.521 | 10.087 | 9.655 | 9.209 | 8.75 | 6.602 | 4.056 | 0.873 | -3.768 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - System Transformation | 9.912 | 9.428 | 8.859 | 8.28 | 7.716 | 7.113 | 6.461 | 3.018 | -0.69 | -4.766 | -10.414 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 12.957 | 12.962 | 12.938 | 12.884 | 12.804 | 12.693 | 12.546 | 11.473 | 9.863 | 8.75 | 7.742 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - System Transformation | 16.002 | 15.796 | 15.517 | 15.2 | 14.911 | 14.614 | 14.303 | 12.844 | 11.28 | 9.326 | 6.366 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - System Transformation | 12.796 | 12.666 | 12.472 | 12.233 | 11.994 | 11.742 | 11.467 | 10.141 | 7.778 | 5.458 | 2.413 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - System Transformation | 9.32 | 9.07 | 8.731 | 8.342 | 7.963 | 7.553 | 7.1 | 4.71 | 1.754 | -1.179 | -5.068 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - System Transformation | 11.491 | 9.776 | 9.571 | 9.322 | 9.088 | 8.844 | 8.584 | 7.439 | 5.823 | 3.762 | 0.656 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - System Transformation | 4.095 | 3.968 | 3.814 | 3.65 | 3.482 | 3.307 | 3.124 | 2.271 | 1.256 | 0.253 | -1.031 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - System Transformation | 13.885 | 13.468 | 12.934 | 12.349 | 11.771 | 11.174 | 10.548 | 7.616 | 4.564 | 1.148 | -3.802 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - System Transformation | 2.064 | 1.693 | 1.18 | 0.589 | 0.002 | -0.608 | -1.25 | -4.258 | -8.485 | -13.317 | -20.185 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - System Transformation | 14.546 | 14.28 | 13.941 | 13.577 | 13.216 | 12.839 | 12.442 | 10.552 | 8.595 | 6.318 | 3.004 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - System Transformation | 7.541 | 7.125 | 6.607 | 6.054 | 5.52 | 4.969 | 4.385 | 1.653 | -1.798 | -5.891 | -11.794 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - System Transformation | 18.511 | 18.526 | 18.486 | 18.398 | 18.307 | 18.19 | 18.035 | 17 | 14.092 | 11.098 | 7.137 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - System Transformation | 12.486 | 12.344 | 12.165 | 11.967 | 11.748 | 11.515 | 11.264 | 10.046 | 8.673 | 7.271 | 5.507 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - System Transformation | 3.206 | 2.841 | 2.377 | 1.854 | 1.345 | 0.81 | 0.235 | -2.677 | -6.427 | -10.253 | -15.188 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - System Transformation | 3.168 | 2.184 | 1.008 | -0.298 | -1.77 | -3.3 | -4.863 | -12.279 | -19.142 | -26.464 | -35.758 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - System Transformation | 3.765 | 3.286 | 2.738 | 2.193 | 1.647 | 1.074 | 0.474 | 14.857 | 11.309 | 7.183 | 1.297 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - System Transformation | 12.421 | 11.955 | 11.389 | 10.773 | 10.174 | 9.562 | 8.932 | 6.013 | 3.334 | -0.264 | -5.62 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - System Transformation | 21.698 | 18.719 | 18.792 | 18.851 | 18.899 | 18.941 | 18.968 | 19.035 | 18.779 | 18.561 | 18.349 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - System Transformation | 3.381 | 3.079 | 2.696 | 2.238 | 1.692 | 1.051 | 0.302 | -3.756 | -8.362 | -12.044 | -15.714 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - System Transformation | 12.554 | 12.449 | 12.304 | 12.145 | 12.018 | 11.881 | 11.723 | 10.806 | 8.97 | 6.384 | 2.383 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - System Transformation | 13.996 | 14.045 | 14.08 | 14.106 | 14.129 | 14.145 | 14.151 | 14.112 | 13.823 | 13.437 | 12.88 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - System Transformation | 14.957 | 14.982 | 14.991 | 14.985 | 14.979 | 14.966 | 14.94 | 14.774 | 14.047 | 13.322 | 12.414 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - System Transformation | 9.564 | 9.046 | 8.376 | 7.62 | 6.872 | 6.102 | 5.302 | 1.6 | -1.786 | -6.037 | -12.235 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - System Transformation | 15.727 | 15.623 | 15.496 | 15.354 | 15.23 | 15.095 | 14.942 | 14.033 | 12.15 | 10.028 | 7.22 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - System Transformation | 5.433 | 5.359 | 5.244 | 5.1 | 4.965 | 4.816 | 4.641 | 3.649 | 1.273 | -1.515 | -5.387 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - System Transformation | 13.954 | 13.776 | 13.536 | 13.261 | 12.984 | 12.691 | 12.377 | 10.853 | 8.965 | 7.001 | 4.395 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - System Transformation | 18.266 | 14.797 | 14.725 | 14.646 | 14.56 | 14.466 | 14.364 | 13.989 | 13.734 | 13.513 | 13.253 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - System Transformation | 11.532 | 11.317 | 11.054 | 10.774 | 10.493 | 10.2 | 9.888 | 8.349 | 6.758 | 4.915 | 2.349 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - System Transformation | 2.5 | 2.318 | 2.08 | 1.805 | 1.517 | 1.199 | 0.848 | -1.137 | -3.219 | -5.117 | -7.442 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - System Transformation | 10.858 | 10.542 | 10.152 | 9.744 | 9.325 | 8.894 | 8.445 | 6.407 | 4.785 | 2.37 | -1.409 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - System Transformation | 9.969 | 9.665 | 9.26 | 8.805 | 8.379 | 7.933 | 7.456 | 6.315 | 3.915 | 1.092 | -3.03 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - System Transformation | 5.597 | 5.316 | 4.962 | 4.529 | 4.042 | 3.48 | 2.833 | -0.735 | -5.58 | -9.932 | -14.832 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - System Transformation | 16.327 | 16.163 | 15.959 | 15.731 | 15.505 | 15.27 | 15.024 | 13.787 | 12.191 | 10.539 | 8.407 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - System Transformation | 8.75 | 6.962 | 6.572 | 6.108 | 5.605 | 5.036 | 4.396 | 7.659 | 2.931 | -2.152 | -8.761 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - System Transformation | 3.769 | 3.612 | 3.419 | 3.205 | 2.993 | 2.775 | 2.548 | 1.488 | 0.342 | -0.836 | -2.362 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - System Transformation | 14.328 | 14.037 | 13.643 | 13.194 | 12.762 | 12.315 | 11.846 | 9.724 | 7.554 | 5.205 | 1.925 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - System Transformation | -0.383 | -0.636 | -0.948 | -0.294 | -0.644 | -1.014 | -1.41 | -3.232 | -5.645 | -7.953 | -10.811 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - System Transformation | 9.126 | 8.79 | 8.356 | 7.867 | 7.37 | 6.853 | 6.304 | 3.649 | 0.053 | -3.815 | -8.909 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - System Transformation | 7.646 | 7.339 | 6.923 | 6.449 | 6.001 | 5.529 | 5.018 | 2.5 | -0.838 | -4.365 | -9.244 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - System Transformation | 4.889 | 4.399 | 3.784 | 3.096 | 2.422 | 1.72 | 0.968 | -2.554 | -7.684 | -13.019 | -19.921 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - System Transformation | 16.009 | 15.704 | 15.301 | 14.84 | 14.375 | 13.883 | 13.351 | 10.85 | 8.185 | 5.459 | 1.819 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - System Transformation | 7.81 | 7.835 | 7.825 | 7.782 | 7.732 | 7.66 | 7.556 | 6.867 | 5.275 | 3.765 | 1.944 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - System Transformation | 13.753 | 14.441 | 14.066 | 5.667 | 4.883 | 4.072 | 3.238 | 0.398 | -2.547 | -5.834 | -10.31 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - System Transformation | 10.86 | 10.442 | 9.906 | 9.289 | 8.628 | 7.939 | 7.223 | 3.74 | 0.446 | -3.373 | -8.564 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - System Transformation | 6.551 | 6.545 | 6.494 | 6.407 | 6.332 | 6.237 | 6.106 | 5.49 | 3.965 | 2.424 | 0.43 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - System Transformation | 11.659 | 11.299 | 10.831 | 10.302 | 9.767 | 9.217 | 8.644 | 5.977 | 3.435 | 0.139 | -4.768 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - System Transformation | 4.958 | 4.405 | 3.72 | 2.94 | 2.128 | 1.261 | 0.32 | -4.698 | -11.276 | -17.335 | -24.367 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - System Transformation | 10.314 | 10.383 | 10.445 | 10.497 | 10.542 | 10.581 | 10.611 | 10.702 | 10.4 | 10.143 | 9.895 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - System Transformation | 11.241 | 11.314 | 11.366 | 11.391 | 11.39 | 11.361 | 11.301 | 10.678 | 9.506 | 8.843 | 8.422 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - System Transformation | 2.456 | 2.514 | 2.562 | 2.601 | 2.632 | 2.654 | 2.667 | 2.648 | 2.252 | 1.915 | 1.572 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - System Transformation | 6.321 | 6.086 | 5.816 | 5.548 | 5.294 | 5.026 | 4.735 | 3.549 | 2.198 | 0.698 | -1.34 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - System Transformation | 0.547 | 0.332 | 0.084 | -0.177 | -0.45 | -0.737 | -1.036 | -2.546 | -4.113 | -5.689 | -7.648 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - System Transformation | 12.425 | 12.167 | 11.828 | 11.436 | 11.046 | 10.628 | 10.175 | 7.852 | 5.034 | 2.463 | -0.73 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - System Transformation | 12.837 | 10.897 | 10.876 | 10.821 | 10.73 | 10.604 | 10.425 | 9.708 | 8.276 | 7.138 | 5.972 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - System Transformation | 9.088 | 8.699 | 15.268 | 14.861 | 14.466 | 14.056 | 13.623 | 11.58 | 9.126 | 6.322 | 2.308 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - System Transformation | 9.988 | 9.84 | 9.661 | 9.455 | 9.251 | 9.02 | 8.756 | 7.059 | 4.323 | 1.438 | -2.201 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - System Transformation | 3.007 | 1.22 | 0.699 | 0.301 | -0.093 | -0.508 | -0.952 | -3.126 | -6.528 | -10.409 | -15.801 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - System Transformation | 12.513 | 12.458 | 12.39 | 12.31 | 12.232 | 12.147 | 12.052 | 11.491 | 10.422 | 9.186 | 7.633 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - System Transformation | 8.348 | 8.196 | 14.967 | 14.697 | 14.447 | 14.18 | 13.882 | 12.327 | 9.956 | 7.216 | 3.323 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - System Transformation | 4.766 | 3.423 | 2.767 | 2.251 | 1.719 | 1.149 | 0.531 | -2.432 | -6.306 | -10.05 | -14.681 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - System Transformation | 10.126 | 9.713 | 9.174 | 8.574 | 8.017 | 7.446 | 6.852 | 4.079 | 1.183 | -2.81 | -9.016 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - System Transformation | 10.221 | 10.041 | 7.641 | 7.269 | 6.827 | 6.283 | 5.626 | 1.595 | -2.916 | -6.05 | -8.923 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - System Transformation | 8.228 | 7.811 | 7.283 | 6.688 | 6.077 | 5.438 | 4.762 | 1.456 | -1.549 | -4.983 | -9.725 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - System Transformation | 6.757 | 4.736 | 4.177 | 3.605 | 3.052 | 2.472 | 1.851 | -0.753 | -3.812 | -7.429 | -12.667 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - System Transformation | 8.482 | 7.804 | 7.848 | 7.851 | 7.818 | 7.749 | 7.631 | 6.771 | 4.675 | 3.243 | 2.045 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - System Transformation | 18.737 | 18.707 | 18.648 | 18.556 | 18.428 | 18.258 | 18.04 | 16.514 | 14.521 | 13.337 | 12.446 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - System Transformation | 8.591 | 8.465 | 8.271 | 8.038 | 7.822 | 7.594 | 7.349 | 6.147 | 4.49 | 2.294 | -1.092 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - System Transformation | 10.666 | 10.479 | 10.227 | 9.928 | 9.593 | 9.235 | 8.851 | 6.882 | 4.342 | 1.931 | -1.118 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - System Transformation | 11.984 | 11.727 | 11.378 | 10.978 | 10.616 | 10.242 | 9.841 | 8.026 | 5.29 | 2.178 | -2.235 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - System Transformation | 12.263 | 12.252 | 12.21 | 12.147 | 12.071 | 11.979 | 11.864 | 11.178 | 9.982 | 8.666 | 6.933 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - System Transformation | 8.286 | 8.36 | 8.428 | 8.497 | 8.555 | 8.601 | 8.631 | 8.669 | 8.062 | 7.526 | 6.939 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - System Transformation | 7.974 | 6.144 | 6.002 | 5.844 | 5.704 | 5.537 | 5.336 | 4.087 | 2.116 | -0.343 | -3.941 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - System Transformation | 9.876 | 8.683 | 8.739 | 8.773 | 8.789 | 8.794 | 8.781 | 8.668 | 7.79 | 7.013 | 6.182 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - System Transformation | 1.145 | 0.92 | 0.65 | 0.356 | 0.071 | -0.225 | -0.539 | -2.034 | -3.957 | -5.934 | -8.506 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 2.848 | 2.82 | 2.782 | 2.745 | 2.706 | 2.663 | 2.612 | 2.334 | 1.783 | 0.995 | -0.172 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - System Transformation | 12.835 | 12.737 | 12.597 | 12.419 | 12.21 | 11.963 | 11.672 | 9.809 | 7.442 | 5.508 | 3.498 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - System Transformation | 24.413 | 24.412 | 24.402 | 24.377 | 24.341 | 24.298 | 24.241 | 23.961 | 23.086 | 22.251 | 21.393 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - System Transformation | 13.77 | 13.785 | 13.777 | 13.751 | 13.724 | 13.689 | 13.645 | 13.424 | 12.781 | 12.094 | 11.199 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - System Transformation | -1.906 | -2.095 | -2.323 | -2.585 | -2.86 | -3.157 | -3.482 | -5.34 | -7.972 | -10.641 | -13.644 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - System Transformation | 3.12 | 2.823 | 2.459 | 2.018 | 1.528 | 0.952 | 0.273 | -3.944 | -10.116 | -15.221 | -20.611 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - System Transformation | 10.947 | 10.775 | 10.517 | 10.213 | 9.924 | 9.625 | 9.306 | 7.82 | 5.821 | 3.42 | -0.103 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - System Transformation | 11.297 | 11.374 | 11.434 | 11.477 | 11.502 | 11.508 | 11.494 | 11.208 | 10.64 | 10.339 | 10.177 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - System Transformation | 7.988 | 7.56 | 7.01 | 6.387 | 5.774 | 5.124 | 4.427 | 0.873 | -3.599 | -8.345 | -14.666 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - System Transformation | 11.677 | 10.925 | 10.738 | 10.526 | 10.311 | 10.084 | 9.837 | 8.847 | 7.027 | 4.757 | 1.614 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - System Transformation | 3.96 | 3.596 | 3.198 | 2.825 | 2.459 | 2.085 | 1.704 | -0.025 | -2.15 | -4.711 | -8.472 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - System Transformation | 10.926 | 10.724 | 10.426 | 10.067 | 9.725 | 9.368 | 8.994 | 7.18 | 4.548 | 1.439 | -3.156 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - System Transformation | -1.288 | -1.481 | -1.72 | -1.981 | -0.232 | -0.493 | -0.769 | -2.092 | -4.064 | -6.389 | -9.714 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - System Transformation | 15.247 | 15.178 | 15.083 | 14.957 | 14.81 | 14.635 | 14.424 | 13.103 | 10.706 | 8.735 | 6.663 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - System Transformation | 14.206 | 13.482 | 12.864 | 12.476 | 12.087 | 11.676 | 11.237 | 9.046 | 6.107 | 3.24 | -0.526 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - System Transformation | 10.059 | 9.764 | 9.34 | 8.849 | 8.345 | 7.822 | 7.268 | 4.653 | 2.391 | -0.649 | -5.244 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - System Transformation | 23.731 | 23.759 | 23.784 | 23.809 | 23.831 | 23.848 | 23.859 | 23.867 | 23.576 | 23.308 | 22.997 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - System Transformation | 8.482 | 8.499 | 8.516 | 8.534 | 8.542 | 8.543 | 8.525 | 8.448 | 7.496 | 6.695 | 5.874 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - System Transformation | 11.234 | 10.97 | 10.601 | 10.172 | 9.771 | 9.359 | 8.926 | 6.942 | 4.845 | 2.076 | -2.178 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - System Transformation | 4.322 | 4.29 | 4.25 | 4.206 | 4.163 | 4.116 | 4.065 | 3.759 | 3.311 | 2.773 | 2.1 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - System Transformation | 8.764 | 8.634 | 8.476 | 8.296 | 8.115 | 7.921 | 7.708 | 6.535 | 4.6 | 2.527 | -0.031 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - System Transformation | 13.798 | 13.536 | 13.19 | 12.804 | 12.438 | 12.061 | 11.665 | 9.777 | 7.501 | 4.578 | 0.108 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - System Transformation | 10.667 | 10.342 | 9.947 | 9.51 | 9.076 | 8.622 | 8.143 | 5.939 | 3.577 | 0.791 | -3 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - System Transformation | 7.7 | 7.346 | 6.875 | 6.318 | 5.681 | 5.014 | 4.322 | 1.052 | -2.017 | -5.401 | -9.815 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - System Transformation | 12.951 | 12.648 | 12.306 | 11.924 | 11.519 | 11.079 | 10.593 | 7.907 | 4.022 | 0.383 | -3.639 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - System Transformation | 7.67 | 7.632 | 7.54 | 7.399 | 7.232 | 7.029 | 6.782 | 5.131 | 2.052 | -1.007 | -4.961 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - System Transformation | 13.748 | 13.533 | 13.233 | 12.89 | 12.557 | 12.215 | 11.854 | 10.177 | 8.385 | 6.012 | 2.384 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - System Transformation | 7.071 | 6.611 | 6.102 | 5.618 | 5.141 | 4.644 | 4.121 | 18.736 | 15.498 | 11.707 | 6.276 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - System Transformation | 7.368 | 7.18 | 6.956 | 6.694 | 6.42 | 6.121 | 5.781 | 3.869 | 0.345 | -3.126 | -7.162 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NPg Best View | 13.323 | 13.179 | 13.015 | 12.96 | 12.95 | 12.933 | 12.903 | 12.768 | 11.275 | 10.048 | 8.892 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NPg Best View | 12.3 | 10.691 | 10.599 | 10.436 | 10.308 | 10.123 | 9.871 | 8.348 | 5.773 | 4.073 | 2.578 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NPg Best View | 11.53 | 11.299 | 10.957 | 10.556 | 10.112 | 9.657 | 9.149 | 6.807 | 2.484 | -0.926 | -3.974 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NPg Best View | 6.091 | 4.805 | 4.871 | 4.862 | 4.843 | 4.786 | 4.676 | 4.043 | 2.061 | 0.624 | -0.642 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NPg Best View | 15.556 | 15.265 | 14.884 | 14.508 | 14.27 | 14.017 | 13.703 | 12.284 | 9.176 | 6.78 | 4.573 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NPg Best View | 17.183 | 17.201 | 17.194 | 17.18 | 17.189 | 17.192 | 17.184 | 17.117 | 16.499 | 15.996 | 15.508 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NPg Best View | 9.13 | 8.687 | 8.061 | 7.334 | 6.851 | 6.348 | 5.768 | 3.082 | -2.144 | -6.12 | -9.962 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NPg Best View | 17.254 | 17.337 | 17.368 | 17.377 | 17.399 | 17.417 | 17.422 | 17.455 | 16.217 | 15.193 | 14.231 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NPg Best View | 1.105 | 0.965 | 0.741 | 0.457 | 0.209 | -0.059 | -0.378 | -1.923 | -5.604 | -8.603 | -11.342 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NPg Best View | 3.469 | 3.046 | 3.231 | 3.377 | 3.531 | 3.668 | 3.777 | 4.162 | 3.561 | 3.099 | 2.651 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NPg Best View | 12.059 | 11.865 | 11.551 | 11.165 | 10.924 | 10.666 | 10.355 | 9.943 | 7.065 | 4.851 | 2.667 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NPg Best View | 2.766 | 2.543 | 2.198 | 1.845 | 1.561 | 1.23 | 0.81 | -1.33 | -4.782 | -7.067 | -9.158 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NPg Best View | 3.347 | 3.356 | 3.351 | 3.338 | 3.326 | 3.307 | 3.279 | 3.13 | 2.834 | 2.605 | 2.388 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NPg Best View | 15.784 | 15.638 | 15.389 | 15.082 | 14.929 | 14.768 | 14.57 | 13.651 | 10.82 | 8.619 | 6.484 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NPg Best View | 13.1 | 12.618 | 12.596 | 12.557 | 12.542 | 12.522 | 12.49 | 12.348 | 11.49 | 10.759 | 10.039 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NPg Best View | 10.654 | 10.691 | 10.655 | 10.581 | 10.523 | 10.451 | 10.354 | 9.865 | 8.002 | 6.652 | 5.444 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NPg Best View | 15.65 | 15.371 | 14.96 | 14.473 | 14.126 | 13.745 | 13.29 | 11.072 | 7.687 | 5.334 | 3.161 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NPg Best View | 8.382 | 8.427 | 8.439 | 8.426 | 8.415 | 8.39 | 8.344 | 8.016 | 6.78 | 5.853 | 5.044 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NPg Best View | 5.863 | 5.771 | 5.586 | 5.354 | 5.176 | 4.992 | 4.787 | 3.794 | 0.322 | -2.665 | -5.581 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NPg Best View | 21.471 | 21.463 | 21.397 | 21.292 | 21.23 | 21.159 | 21.058 | 20.614 | 19.425 | 18.514 | 17.679 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NPg Best View | 3.713 | 3.607 | 3.455 | 3.284 | 3.168 | 3.047 | 2.914 | 2.236 | 0.43 | -1.148 | -2.727 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NPg Best View | 11.653 | 11.279 | 10.714 | 10.031 | 9.564 | 9.053 | 8.444 | 5.383 | -0.08 | -4.096 | -7.909 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NPg Best View | 9.532 | 9.194 | 8.698 | 8.158 | 7.785 | 7.385 | 6.897 | 4.799 | 0.686 | -2.411 | -5.258 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NPg Best View | 14.775 | 14.576 | 14.295 | 14.007 | 13.807 | 13.596 | 13.338 | 12.206 | 10.211 | 8.786 | 7.482 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NPg Best View | 3.045 | 3.042 | 2.897 | 2.675 | 2.55 | 2.384 | 2.157 | 0.834 | -2.462 | -4.772 | -6.962 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NPg Best View | 5.455 | 5.29 | 5.035 | 4.717 | 4.476 | 4.204 | 3.874 | 2.212 | -0.189 | -1.877 | -3.43 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 15.193 | 15.184 | 15.128 | 15.048 | 14.972 | 14.884 | 14.778 | 14.347 | 13.036 | 12.004 | 11.073 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 4.388 | 1.479 | 1.465 | 1.365 | 1.271 | 1.11 | 0.865 | -0.616 | -4.405 | -7.139 | -9.545 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NPg Best View | 7.469 | 7.397 | 7.197 | 6.931 | 6.687 | 6.397 | 6.045 | 4.087 | 0.478 | -2.064 | -4.396 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NPg Best View | 11.763 | 11.536 | 11.162 | 10.696 | 10.416 | 10.118 | 9.757 | 8.043 | 3.61 | 0.098 | -3.21 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NPg Best View | 5.903 | 5.558 | 4.99 | 4.299 | 3.788 | 3.229 | 2.556 | -0.779 | -7.112 | -11.839 | -16.205 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NPg Best View | 6.885 | 6.873 | 6.855 | 6.833 | 6.814 | 6.795 | 6.773 | 6.671 | 6.361 | 6.087 | 5.82 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NPg Best View | 3.717 | 3.696 | 3.654 | 3.602 | 3.552 | 3.494 | 3.423 | 3.034 | 2.375 | 1.872 | 1.405 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NPg Best View | 11.642 | 11.303 | 10.783 | 10.171 | 9.808 | 9.425 | 8.974 | 6.898 | 2.5 | -0.842 | -4.14 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 13.591 | 13.534 | 13.469 | 13.388 | 13.3 | 13.206 | 13.103 | 12.57 | 11.355 | 10.158 | 8.957 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NPg Best View | 4.638 | 4.544 | 4.408 | 4.25 | 4.138 | 4.023 | 3.888 | 3.259 | 2.235 | 1.487 | 0.787 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 9.532 | 9.295 | 8.89 | 8.394 | 8.108 | 7.801 | 7.417 | 5.547 | 1.049 | -2.355 | -5.585 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NPg Best View | 11.644 | 11.451 | 11.118 | 10.711 | 10.41 | 10.077 | 9.663 | 7.626 | 3.763 | 0.919 | -1.653 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NPg Best View | 9.367 | 9.437 | 9.437 | 9.394 | 9.407 | 9.398 | 9.36 | 9.065 | 7.427 | 6.187 | 4.995 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NPg Best View | 10.299 | 10.351 | 10.345 | 10.293 | 10.286 | 10.26 | 10.19 | 9.745 | 8.642 | 7.87 | 7.152 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NPg Best View | 17.498 | 17.354 | 17.142 | 16.886 | 16.691 | 16.471 | 16.205 | 14.89 | 13.279 | 12.264 | 11.371 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NPg Best View | 7.755 | 22.328 | 22.119 | 21.868 | 21.687 | 21.493 | 21.255 | 20.097 | 16.974 | 14.49 | 12.239 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NPg Best View | 10.221 | 9.873 | 9.347 | 8.707 | 8.226 | 7.731 | 7.155 | 21.736 | 16.07 | 11.439 | 7.1 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NPg Best View | 3.906 | 3.81 | 3.677 | 3.542 | 3.471 | 3.394 | 3.296 | 2.891 | 2.142 | 1.614 | 1.099 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NPg Best View | 6.116 | 5.335 | 4.336 | 3.338 | 2.537 | 1.685 | 0.699 | -3.227 | -8.946 | -13.064 | -16.626 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NPg Best View | 3.838 | 3.54 | 3.08 | 2.529 | 1.931 | 1.299 | 0.561 | -3.085 | -9.793 | -15.231 | -20.19 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NPg Best View | 5.138 | 4.658 | 3.943 | 3.078 | 2.434 | 1.757 | 0.964 | 21.378 | 14.033 | 8.162 | 2.64 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NPg Best View | 4.118 | 4.207 | 4.28 | 4.339 | 4.39 | 4.428 | 4.451 | 4.483 | 4.298 | 4.2 | 4.12 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NPg Best View | 8.03 | 7.642 | 7.025 | 6.251 | 5.67 | 5.003 | 4.186 | 16.872 | 10.554 | 6.256 | 2.351 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NPg Best View | 12.866 | 12.986 | 13.085 | 13.156 | 13.214 | 13.258 | 13.284 | 13.314 | 12.569 | 12.036 | 11.581 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NPg Best View | 9.581 | 9.77 | 9.943 | 10.098 | 10.241 | 10.371 | 10.484 | 10.936 | 11.038 | 11.131 | 11.218 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NPg Best View | 11.257 | 11.452 | 11.593 | 11.717 | 11.838 | 11.938 | 12.002 | 12.198 | 10.565 | 9.28 | 8.109 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NPg Best View | 9.092 | 9.213 | 9.292 | 9.351 | 9.417 | 9.472 | 9.504 | 9.613 | 8.881 | 8.323 | 7.793 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NPg Best View | 10.843 | 10.6 | 10.201 | 9.716 | 9.374 | 8.98 | 8.489 | 5.96 | 2.367 | 0.068 | -2.021 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NPg Best View | 5.137 | 5.103 | 5.045 | 4.975 | 4.907 | 4.833 | 4.738 | 4.309 | 4.031 | 3.887 | 3.788 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NPg Best View | 7.712 | 7.743 | 7.743 | 7.73 | 7.711 | 7.681 | 7.632 | 7.381 | 6.88 | 6.433 | 5.989 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NPg Best View | 13.247 | 12.875 | 12.376 | 11.867 | 11.517 | 11.14 | 10.678 | 8.461 | 3.922 | 0.504 | -2.583 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NPg Best View | 0.842 | 0.861 | 0.866 | 0.862 | 0.857 | 0.845 | 0.823 | 0.676 | 0.364 | 0.12 | -0.113 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NPg Best View | 2.46 | 2.275 | 2.024 | 1.741 | 1.531 | 1.313 | 1.057 | -0.14 | -1.954 | -3.284 | -4.548 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 9.623 | 9.445 | 9.121 | 8.716 | 8.447 | 8.144 | 7.776 | 5.941 | 2.796 | 0.686 | -1.35 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NPg Best View | 8.525 | 8.461 | 8.339 | 8.233 | 8.177 | 8.106 | 7.992 | 7.393 | 5.163 | 3.427 | 1.832 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NPg Best View | 5.263 | 5.009 | 4.63 | 4.196 | 3.879 | 3.542 | 3.15 | 1.321 | -2.436 | -5.409 | -8.298 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NPg Best View | 4.213 | 4.25 | 4.278 | 4.296 | 4.31 | 4.317 | 4.315 | 4.253 | 4.002 | 3.833 | 3.69 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NPg Best View | 21.996 | 21.866 | 21.66 | 21.433 | 21.314 | 21.186 | 21.024 | 20.272 | 17.828 | 15.916 | 14.125 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NPg Best View | 7.521 | 7.633 | 7.7 | 7.749 | 7.821 | 7.88 | 7.918 | 8.023 | 6.912 | 6.028 | 5.184 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NPg Best View | 13.174 | 12.935 | 12.621 | 12.33 | 12.144 | 11.941 | 11.679 | 10.416 | 7.515 | 5.303 | 3.313 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NPg Best View | 8.525 | 8.558 | 8.51 | 8.403 | 8.334 | 8.245 | 8.108 | 7.322 | 4.878 | 3.003 | 1.279 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NPg Best View | 2.436 | 1.833 | 0.971 | 0.017 | -0.519 | -1.105 | -1.832 | -5.265 | -12.398 | -17.655 | -22.615 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NPg Best View | 1.012 | 0.907 | 0.765 | 0.587 | 0.412 | 0.22 | -0.001 | -0.694 | -1.427 | -2.045 | -2.645 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NPg Best View | 2.922 | 2.854 | 2.724 | 2.543 | 2.369 | 2.16 | 1.902 | 0.412 | -2.216 | -4.238 | -6.119 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NPg Best View | 13.006 | 12.984 | 12.886 | 12.734 | 12.619 | 12.488 | 12.314 | 12.596 | 10.947 | 9.71 | 8.63 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NPg Best View | 14.532 | 14.378 | 15.102 | 14.748 | 14.533 | 14.306 | 14.022 | 12.659 | 9.241 | 6.574 | 4.054 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NPg Best View | 22.208 | 22.228 | 22.12 | 21.877 | 21.58 | 21.167 | 20.619 | 17.227 | 12.482 | 9.61 | 7.286 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NPg Best View | 9.844 | 9.603 | 9.241 | 8.817 | 8.471 | 8.105 | 7.685 | 12.691 | 8.775 | 5.646 | 2.675 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NPg Best View | 1.95 | 1.665 | 1.275 | 0.82 | 0.537 | 0.231 | -0.133 | -1.7 | -4.265 | -6.2 | -8.148 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NPg Best View | 8.067 | 7.77 | 7.238 | 6.567 | 6.25 | 5.914 | 5.496 | 3.586 | -2.434 | -7.227 | -11.929 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NPg Best View | 5.265 | 2.98 | 2.975 | 2.938 | 2.897 | 2.837 | 2.746 | 2.25 | 0.941 | -0.053 | -0.939 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NPg Best View | 7.624 | 7.27 | 6.737 | 6.102 | 5.711 | 5.29 | 4.767 | 2.247 | -2.662 | -6.291 | -9.667 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NPg Best View | 3.458 | 3.262 | 17.631 | 17.223 | 16.907 | 16.561 | 16.134 | 14.003 | 9.334 | 5.788 | 2.645 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NPg Best View | -0.428 | -0.542 | -0.71 | -0.915 | -1.076 | -1.242 | -1.436 | -2.357 | -4.373 | -6.049 | -7.641 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NPg Best View | 2.567 | 2.588 | 2.578 | 2.55 | 2.532 | 2.507 | 2.469 | 2.255 | 1.49 | 0.945 | 0.45 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NPg Best View | 10.422 | 10.199 | 9.822 | 9.363 | 9.056 | 8.732 | 8.337 | 6.581 | 2.794 | -0.071 | -2.706 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NPg Best View | 8.323 | 8.018 | 7.527 | 6.934 | 6.605 | 6.244 | 5.8 | 3.617 | -1.003 | -4.384 | -7.666 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NPg Best View | 11.299 | 11.23 | 11.087 | 10.893 | 10.773 | 10.627 | 10.43 | 9.356 | 7.654 | 6.494 | 5.413 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NPg Best View | 3.672 | 2.808 | 2.841 | 2.82 | 2.796 | 2.734 | 2.621 | 1.891 | -0.362 | -1.974 | -3.42 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NPg Best View | 14.923 | 14.861 | 14.75 | 14.593 | 14.432 | 14.237 | 14.004 | 12.643 | 10.402 | 8.76 | 7.247 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NPg Best View | 4.468 | 4.396 | 4.289 | 4.161 | 4.073 | 3.979 | 3.87 | 3.36 | 2.197 | 1.267 | 0.38 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NPg Best View | 2.078 | 2.029 | 1.939 | 1.826 | 1.756 | 1.681 | 1.588 | 1.16 | -0.053 | -0.997 | -1.871 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NPg Best View | 15.048 | 14.763 | 14.312 | 13.756 | 13.377 | 12.953 | 12.438 | 9.786 | 4.887 | 1.228 | -2.255 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NPg Best View | 2.805 | 2.715 | 4.481 | 4.17 | 3.913 | 3.635 | 3.285 | 1.557 | -2.982 | -6.559 | -9.835 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NPg Best View | 14.812 | 14.759 | 14.612 | 14.433 | 14.347 | 14.256 | 14.151 | 13.651 | 11.447 | 9.745 | 8.076 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NPg Best View | 4.441 | 4.355 | 4.233 | 4.089 | 3.967 | 3.839 | 3.69 | 2.995 | 1.703 | 0.684 | -0.264 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NPg Best View | 4.708 | 4.289 | 3.659 | 2.923 | 2.381 | 1.804 | 1.121 | -2.083 | -7.138 | -10.8 | -14.301 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NPg Best View | 11.625 | 11.307 | 10.845 | 10.316 | 9.967 | 9.605 | 9.179 | 7.261 | 3.634 | 0.87 | -1.84 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NPg Best View | 12.157 | 10.568 | 10.425 | 10.17 | 9.918 | 9.557 | 9.075 | 6.368 | 3.134 | 1.362 | -0.074 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NPg Best View | 1.022 | 0.739 | 0.41 | 0.16 | -0.036 | -0.242 | -0.493 | -1.539 | -2.805 | -3.577 | -4.223 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NPg Best View | 7.43 | 6.783 | 5.889 | 4.871 | 4.199 | 3.5 | 2.693 | -0.878 | -6.782 | -11.093 | -15.247 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NPg Best View | 9.201 | 9.216 | 9.217 | 9.21 | 9.199 | 9.181 | 9.15 | 9.007 | 8.836 | 8.667 | 8.495 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NPg Best View | 1.691 | 1.485 | 1.155 | 0.706 | 0.199 | -0.435 | -1.224 | -5.915 | -10.345 | -12.683 | -14.418 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NPg Best View | 10.525 | 10.2 | 9.756 | 9.312 | 9.041 | 8.743 | 8.378 | 6.603 | 2 | -1.579 | -4.936 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NPg Best View | 8.801 | 8.459 | 7.915 | 7.244 | 6.826 | 6.363 | 5.8 | 2.985 | -2.017 | -5.603 | -9.012 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NPg Best View | 1.351 | 1.27 | 1.138 | 0.964 | 0.789 | 0.572 | 0.304 | -1.249 | -2.789 | -3.682 | -4.424 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NPg Best View | 7.287 | 7.022 | 6.591 | 6.066 | 5.709 | 5.336 | 4.888 | 2.861 | -2.147 | -6.146 | -9.928 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NPg Best View | 1.008 | 1.022 | 0.935 | 0.791 | 0.74 | 0.669 | 0.559 | 0.033 | -2.174 | -3.841 | -5.405 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NPg Best View | 1.501 | 1.502 | 1.503 | 1.503 | 1.502 | 1.502 | 1.501 | 1.492 | 1.477 | 1.462 | 1.448 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 24.118 | 24.194 | 24.2 | 24.174 | 24.182 | 24.185 | 24.17 | 24.135 | 22.602 | 21.381 | 20.2 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 33.871 | 33.843 | 33.767 | 33.669 | 33.614 | 33.554 | 33.475 | 33.135 | 32.167 | 31.433 | 30.721 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 20.528 | 20.472 | 20.384 | 20.275 | 20.187 | 20.093 | 19.978 | 19.456 | 18.698 | 18.148 | 17.66 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 14.686 | 14.494 | 14.209 | 13.882 | 13.653 | 13.393 | 13.075 | 11.419 | 8.767 | 6.882 | 5.12 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NPg Best View | 13.603 | 13.348 | 12.986 | 13.545 | 13.156 | 12.756 | 12.297 | 10.241 | 6.768 | 4.175 | 1.88 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NPg Best View | 10.432 | 9.403 | 8.992 | 8.482 | 8.193 | 7.887 | 7.514 | 5.948 | 2.374 | -0.404 | -3.13 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NPg Best View | 1.476 | 15.27 | 14.975 | 14.618 | 14.252 | 13.836 | 13.337 | 10.704 | 7.327 | 4.92 | 2.783 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NPg Best View | 10.888 | 10.349 | 9.742 | 9.325 | 9.09 | 8.835 | 8.518 | 7.096 | 3.232 | 0.251 | -2.564 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NPg Best View | 15.398 | 15.386 | 15.354 | 15.31 | 15.28 | 15.246 | 15.205 | 14.976 | 14.101 | 13.299 | 12.499 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NPg Best View | 3.901 | 3.079 | 1.893 | 0.486 | -0.502 | -1.548 | -2.79 | -7.692 | -15.789 | -22.02 | -27.874 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NPg Best View | 6.281 | 5.715 | 4.964 | 4.196 | 3.752 | 3.283 | 2.717 | 0.257 | -4.233 | -7.36 | -10.29 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NPg Best View | 4.458 | 4.517 | 4.461 | 4.337 | 4.393 | 4.43 | 4.434 | 4.278 | 1.316 | -1.156 | -3.722 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NPg Best View | 17.173 | 14.178 | 13.93 | 13.635 | 13.408 | 13.173 | 12.91 | 11.87 | 9.739 | 7.902 | 6.078 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NPg Best View | 14.777 | 14.766 | 14.724 | 14.655 | 14.576 | 14.475 | 14.349 | 13.597 | 12.369 | 11.468 | 10.642 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NPg Best View | 9.288 | 9.118 | 8.877 | 8.564 | 8.22 | 7.805 | 7.307 | 4.385 | 0.942 | -1.458 | -3.601 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NPg Best View | 11.745 | 11.762 | 11.699 | 11.601 | 11.567 | 11.529 | 11.478 | 11.252 | 9.093 | 7.338 | 5.613 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NPg Best View | 11.328 | 11.406 | 11.435 | 11.439 | 11.471 | 11.494 | 11.499 | 11.51 | 10.745 | 10.177 | 9.624 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 3.817 | 3.676 | 3.484 | 3.233 | 2.941 | 2.585 | 2.158 | -0.395 | -3.12 | -4.99 | -6.639 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NPg Best View | 14.745 | 14.686 | 14.561 | 14.4 | 14.313 | 14.209 | 14.082 | 13.337 | 11.314 | 9.736 | 8.205 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NPg Best View | 10.682 | 10.426 | 10 | 9.478 | 9.221 | 8.945 | 8.607 | 7.08 | 3.062 | 0.022 | -2.96 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NPg Best View | 9.49 | 9.396 | 9.156 | 8.858 | 8.704 | 8.538 | 8.343 | 7.367 | 3.905 | 1.27 | -1.281 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NPg Best View | 7.166 | 6.879 | 6.399 | 5.803 | 5.416 | 4.985 | 4.449 | 1.755 | -2.935 | -6.198 | -9.198 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NPg Best View | 4.495 | 4.106 | 3.521 | 2.832 | 2.319 | 1.742 | 1.046 | 14.904 | 10.195 | 6.863 | 3.81 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NPg Best View | 11.054 | 11.087 | 11.06 | 10.985 | 10.878 | 10.709 | 10.46 | 8.972 | 7.745 | 7.246 | 6.942 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NPg Best View | 15.413 | 15.141 | 14.705 | 14.173 | 13.914 | 13.645 | 13.322 | 11.862 | 7.997 | 5.008 | 2.039 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NPg Best View | 8.904 | 8.499 | 7.879 | 7.113 | 6.516 | 5.834 | 5.004 | 0.611 | -5.482 | -9.626 | -13.405 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NPg Best View | 3.301 | 3.206 | 3.07 | 3.411 | 3.29 | 3.162 | 3.012 | 2.286 | 1.044 | 0.077 | -0.841 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NPg Best View | 7.227 | 7.099 | 6.841 | 6.51 | 6.271 | 6.013 | 5.681 | 11.142 | 6.623 | 3.017 | -0.209 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NPg Best View | 4.177 | 4.009 | 3.751 | 3.453 | 3.292 | 3.124 | 2.921 | 2.026 | 0.018 | -1.509 | -3.021 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 12.345 | 12.365 | 12.347 | 12.305 | 12.283 | 12.25 | 12.199 | 11.912 | 10.878 | 10.017 | 9.164 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 25.335 | 25.311 | 25.257 | 25.185 | 25.135 | 25.081 | 25.019 | 24.705 | 23.507 | 22.51 | 21.535 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NPg Best View | 14.634 | 14.491 | 14.289 | 14.048 | 13.824 | 13.578 | 13.286 | 11.926 | 10.402 | 9.409 | 8.583 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NPg Best View | 12.726 | 12.816 | 12.875 | 12.907 | 12.947 | 12.977 | 12.993 | 13.021 | 12.058 | 11.296 | 10.587 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NPg Best View | 19.999 | 19.991 | 19.956 | 19.897 | 19.858 | 19.813 | 19.757 | 19.557 | 18.861 | 18.23 | 17.599 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NPg Best View | 6.946 | 6.672 | 6.222 | 5.67 | 5.365 | 5.041 | 4.644 | 3.07 | -0.022 | -2.256 | -4.425 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 21.118 | 21.16 | 21.085 | 20.971 | 20.899 | 20.817 | 20.708 | 20.197 | 17.711 | 15.79 | 13.945 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NPg Best View | 14.046 | 14.007 | 13.895 | 13.749 | 13.723 | 13.693 | 13.65 | 13.389 | 10.901 | 8.869 | 6.886 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NPg Best View | 4.274 | 4.195 | 4.065 | 3.906 | 3.82 | 3.726 | 3.608 | 3.04 | 1.814 | 0.906 | 0.028 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NPg Best View | 0.948 | 0.895 | 0.808 | 0.703 | 0.593 | 0.469 | 0.316 | -0.293 | -0.839 | -1.241 | -1.61 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NPg Best View | 16.265 | 16.224 | 16.108 | 15.943 | 15.811 | 15.653 | 15.459 | 14.442 | 12.054 | 10.199 | 8.432 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NPg Best View | 22.226 | 22.077 | 21.837 | 21.534 | 21.325 | 21.1 | 20.818 | 19.453 | 16.584 | 14.414 | 12.49 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NPg Best View | 26.349 | 26.272 | 26.141 | 25.979 | 25.887 | 25.789 | 25.669 | 25.107 | 23.447 | 22.133 | 20.912 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NPg Best View | 2.409 | 2.295 | 2.142 | 1.97 | 1.807 | 1.636 | 1.437 | 0.503 | -1.093 | -2.402 | -3.594 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NPg Best View | 2.315 | 2.131 | 1.837 | 1.473 | 1.245 | 0.986 | 0.68 | -1.059 | -5.459 | -8.975 | -12.457 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NPg Best View | 14.366 | 14.34 | 14.256 | 14.128 | 14.015 | 13.86 | 13.656 | 12.615 | 11.418 | 10.677 | 10.025 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NPg Best View | 4.615 | 4.548 | 4.438 | 4.31 | 4.222 | 4.132 | 4.023 | 3.517 | 2.182 | 1.116 | 0.136 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NPg Best View | 14.544 | 14.562 | 14.546 | 14.517 | 14.506 | 14.478 | 14.422 | 14.094 | 13.03 | 12.204 | 11.45 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NPg Best View | 9.18 | 9.345 | 9.478 | 9.584 | 9.691 | 9.776 | 9.837 | 10.997 | 10.61 | 10.381 | 10.174 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NPg Best View | 1.262 | 0.981 | 0.583 | 0.095 | -0.259 | -0.646 | -1.115 | -3.402 | -6.353 | -8.337 | -10.121 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NPg Best View | 16.84 | 16.819 | 16.753 | 16.671 | 16.609 | 16.542 | 16.466 | 16.095 | 14.957 | 14.066 | 13.205 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NPg Best View | 16.775 | 16.746 | 16.674 | 16.58 | 16.502 | 16.406 | 16.287 | 15.603 | 14.497 | 13.745 | 13.05 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NPg Best View | 4.464 | 4.112 | 3.598 | 2.99 | 2.535 | 2.047 | 1.469 | 13.524 | 9.124 | 5.777 | 2.641 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NPg Best View | 14.361 | 14.284 | 14.141 | 13.962 | 13.846 | 13.721 | 13.58 | 12.898 | 10.837 | 9.173 | 7.57 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NPg Best View | 8.088 | 7.672 | 7.118 | 6.558 | 6.139 | 5.693 | 5.14 | 19.556 | 14.537 | 10.699 | 7.253 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NPg Best View | 4.986 | 4.969 | 4.848 | 4.699 | 4.568 | 4.411 | 4.209 | 3.188 | 0.006 | -2.432 | -4.662 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NPg Best View | 10.453 | 10.226 | 9.824 | 9.31 | 9.005 | 8.684 | 8.293 | 6.477 | 1.026 | -3.403 | -7.621 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NPg Best View | 0.167 | 0.104 | -0.002 | -0.139 | -0.236 | -0.344 | -0.473 | -1.142 | -2.703 | -3.963 | -5.178 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NPg Best View | 13.369 | 13.133 | 12.758 | 12.322 | 12.025 | 11.705 | 11.312 | 9.45 | 5.774 | 3.044 | 0.514 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NPg Best View | 17.515 | 17.524 | 17.508 | 17.475 | 17.445 | 17.409 | 17.361 | 17.095 | 16.064 | 15.274 | 14.556 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NPg Best View | 12.623 | 12.431 | 12.149 | 11.831 | 11.665 | 11.491 | 11.298 | 10.332 | 7.586 | 5.309 | 2.93 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NPg Best View | 6.951 | 6.86 | 6.703 | 6.503 | 6.328 | 6.137 | 5.912 | 4.743 | 1.949 | -0.318 | -2.414 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NPg Best View | 9.438 | 9.349 | 9.161 | 8.897 | 8.695 | 8.441 | 8.121 | 6.149 | 2.203 | -0.772 | -3.535 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NPg Best View | 15.336 | 15.344 | 15.346 | 15.342 | 15.334 | 15.319 | 15.295 | 16.143 | 15.939 | 15.72 | 15.502 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NPg Best View | 16.429 | 16.376 | 16.261 | 16.105 | 15.98 | 15.844 | 15.671 | 14.819 | 12.933 | 11.505 | 10.213 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NPg Best View | 12.875 | 12.771 | 12.578 | 12.337 | 12.166 | 11.991 | 11.788 | 10.994 | 8.479 | 6.369 | 4.38 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NPg Best View | 10.57 | 10.182 | 9.692 | 9.268 | 9.045 | 8.806 | 8.513 | 7.233 | 3.852 | 1.296 | -1.183 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NPg Best View | 9.616 | 9.236 | 8.69 | 8.095 | 7.749 | 7.377 | 6.912 | 4.709 | 0.191 | -3.186 | -6.37 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NPg Best View | 2.22 | 2.285 | 2.335 | 2.375 | 2.41 | 2.437 | 2.451 | 2.476 | 2.323 | 2.243 | 2.183 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NPg Best View | 9.988 | 9.463 | 8.816 | 8.264 | 7.9 | 7.517 | 7.055 | 21.964 | 16.725 | 12.609 | 8.788 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NPg Best View | 4.599 | 4.451 | 4.158 | 3.762 | 3.451 | 3.082 | 2.635 | 0.14 | -5.08 | -9.017 | -12.736 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NPg Best View | 3.38 | 3.037 | 2.54 | 1.96 | 1.54 | 1.111 | 0.617 | -1.538 | -5.859 | -9.286 | -12.576 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NPg Best View | 23.166 | 23.184 | 23.093 | 22.94 | 22.895 | 22.841 | 22.765 | 22.38 | 19.378 | 16.973 | 14.661 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NPg Best View | 6.407 | 6.285 | 6.08 | 5.824 | 5.63 | 5.411 | 5.143 | 3.778 | 1.347 | -0.532 | -2.343 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NPg Best View | 6.753 | 6.747 | 6.733 | 6.715 | 6.705 | 6.694 | 6.681 | 6.61 | 6.435 | 6.307 | 6.186 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NPg Best View | 11.636 | 11.056 | 10.169 | 9.109 | 8.505 | 7.867 | 7.112 | 3.843 | -2.875 | -8.033 | -13.147 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NPg Best View | 21.184 | 21.222 | 21.199 | 21.107 | 20.95 | 20.705 | 20.367 | 18.305 | 16.817 | 16.315 | 16.086 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NPg Best View | 11.287 | 11.105 | 10.785 | 10.398 | 10.173 | 9.931 | 9.635 | 8.238 | 4.66 | 1.976 | -0.58 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NPg Best View | 12.631 | 12.495 | 12.236 | 11.875 | 11.412 | 10.829 | 10.115 | 6.131 | 1.74 | -0.927 | -3.048 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NPg Best View | 0.182 | 0.117 | 0.005 | -0.142 | -0.276 | -0.431 | -0.622 | -1.668 | -3.352 | -4.614 | -5.777 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NPg Best View | 6.952 | 1.123 | 0.831 | 0.483 | 0.232 | -0.036 | -0.356 | 6.825 | 4.306 | 2.474 | 0.77 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NPg Best View | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NPg Best View | 3.651 | 3.415 | 3.067 | 2.658 | 2.388 | 2.101 | 1.762 | 0.126 | -3.013 | -5.49 | -7.939 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NPg Best View | 12.421 | 12.239 | 11.92 | 11.503 | 11.073 | 10.527 | 9.841 | 5.745 | 1.208 | -1.286 | -3.243 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NPg Best View | 5.559 | 5.377 | 5.05 | 4.678 | 4.456 | 4.205 | 3.883 | 2.523 | -0.026 | -1.791 | -3.451 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NPg Best View | 1.095 | 0.92 | 0.687 | 0.481 | 0.369 | 0.249 | 0.098 | -0.547 | -1.877 | -2.813 | -3.728 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NPg Best View | 12.709 | 12.593 | 12.362 | 12.067 | 11.932 | 11.784 | 11.592 | 10.635 | 7.901 | 5.835 | 3.843 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NPg Best View | 7.28 | 7.404 | 7.492 | 7.559 | 7.622 | 7.672 | 7.699 | 7.77 | 6.552 | 5.602 | 4.748 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NPg Best View | 13.507 | 13.464 | 13.34 | 13.167 | 13.111 | 13.046 | 12.961 | 12.465 | 10.09 | 8.232 | 6.403 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NPg Best View | 7.058 | 6.764 | 6.344 | 5.84 | 5.441 | 5.012 | 4.493 | 1.874 | -2.044 | -5.029 | -7.808 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NPg Best View | 9.755 | 9.722 | 9.571 | 9.318 | 9.113 | 8.813 | 8.405 | 5.909 | 2.864 | 1.144 | -0.31 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NPg Best View | 14.756 | 14.805 | 14.846 | 14.88 | 14.913 | 14.942 | 14.965 | 15.056 | 14.938 | 14.846 | 14.761 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NPg Best View | 5.571 | 5.562 | 5.539 | 5.508 | 5.499 | 5.487 | 5.465 | 5.338 | 5.074 | 4.888 | 4.692 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NPg Best View | 14.032 | 14.093 | 14.119 | 14.119 | 14.126 | 14.128 | 14.119 | 14.064 | 12.945 | 12.077 | 11.292 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NPg Best View | 4.041 | 3.775 | 3.337 | 2.798 | 2.499 | 2.181 | 1.8 | 0.116 | -3.576 | -6.305 | -8.928 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NPg Best View | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NPg Best View | 8.804 | 7.782 | 7.193 | 6.493 | 6.037 | 5.562 | 5.004 | 2.542 | -3.178 | -7.695 | -11.946 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NPg Best View | 8.847 | 8.354 | 7.64 | 6.849 | 23.537 | 23.101 | 22.564 | 20.03 | 14.653 | 10.655 | 6.73 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NPg Best View | 3.294 | 3.429 | 3.519 | 3.576 | 3.609 | 3.628 | 3.623 | 3.519 | 1.766 | 0.323 | -0.968 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NPg Best View | 1.901 | 1.647 | 1.274 | 0.828 | 0.38 | -0.082 | -0.618 | -2.984 | -7.816 | -11.796 | -15.341 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NPg Best View | 14.46 | 14.33 | 14.112 | 13.853 | 13.676 | 13.487 | 13.253 | 12.166 | 9.199 | 6.843 | 4.674 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NPg Best View | 5.695 | 5.268 | 4.591 | 3.765 | 3.271 | 2.737 | 2.094 | -1.012 | -6.799 | -11.056 | -15.273 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NPg Best View | 5.015 | 4.104 | 3.783 | 3.439 | 3.202 | 2.931 | 2.587 | 0.947 | -2.672 | -5.343 | -7.818 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NPg Best View | 14.981 | 14.818 | 14.552 | 14.241 | 14.089 | 13.927 | 13.725 | 12.881 | 10.729 | 9.053 | 7.4 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NPg Best View | 3.57 | 3.31 | 2.883 | 2.366 | 2.065 | 1.732 | 1.319 | 13.944 | 9.778 | 6.746 | 3.838 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NPg Best View | 6.779 | 6.558 | 6.204 | 5.777 | 5.445 | 5.078 | 4.66 | 2.489 | -1.647 | -4.756 | -7.755 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NPg Best View | 8.332 | 7.956 | 7.381 | 6.694 | 6.284 | 5.851 | 5.334 | 2.966 | -1.41 | -4.473 | -7.448 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NPg Best View | 5.987 | 5.688 | 5.27 | 4.78 | 4.391 | 3.984 | 3.505 | 1.355 | -1.726 | -3.905 | -5.818 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NPg Best View | 1.486 | 0.923 | 0.212 | -0.441 | -0.89 | -1.374 | -1.983 | -4.877 | -11.576 | -16.758 | -21.341 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NPg Best View | 9.844 | 9.412 | 8.805 | 8.178 | 7.863 | 7.531 | 7.126 | 5.291 | 0.634 | -2.907 | -6.359 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NPg Best View | 10.815 | 10.424 | 9.876 | 9.307 | 8.902 | 8.443 | 7.871 | 4.948 | 0.324 | -2.84 | -5.699 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NPg Best View | 12.387 | 12.411 | 12.363 | 12.252 | 12.148 | 11.996 | 11.789 | 10.44 | 8.093 | 6.651 | 5.445 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NPg Best View | 8.619 | 8.526 | 8.358 | 8.159 | 8.016 | 7.867 | 7.686 | 6.795 | 4.587 | 2.875 | 1.29 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NPg Best View | 2.891 | 2.843 | 2.702 | 2.517 | 2.372 | 2.193 | 1.971 | 0.702 | -1.316 | -2.556 | -3.683 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NPg Best View | 12.89 | 12.713 | 12.414 | 12.05 | 11.838 | 11.614 | 11.342 | 10.101 | 6.975 | 4.575 | 2.295 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NPg Best View | 18.322 | 18.267 | 18.151 | 17.993 | 17.879 | 17.756 | 17.599 | 16.841 | 15.243 | 14.017 | 12.902 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NPg Best View | 15.466 | 15.385 | 15.232 | 15.043 | 14.951 | 14.855 | 14.746 | 14.204 | 12.038 | 10.27 | 8.483 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NPg Best View | 2.76 | 2.458 | 1.957 | 1.278 | 0.598 | -0.253 | -1.297 | -6.183 | -11.155 | -14.279 | -16.973 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NPg Best View | 9.86 | 9.952 | 9.99 | 9.987 | 9.994 | 9.982 | 9.944 | 9.677 | 8.16 | 7.048 | 6.04 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NPg Best View | 6.159 | 6.046 | 5.844 | 5.584 | 5.405 | 5.191 | 4.93 | 3.601 | 1.19 | -0.599 | -2.284 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NPg Best View | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NPg Best View | 6.927 | 6.461 | 5.813 | 5.125 | 4.718 | 4.269 | 3.715 | 1.146 | -3.196 | -6.271 | -9.281 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NPg Best View | 14.389 | 14.112 | 13.689 | 13.172 | 12.91 | 12.632 | 12.298 | 10.728 | 6.935 | 4.004 | 1.089 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NPg Best View | 3.143 | 3.007 | 2.811 | 2.582 | 2.428 | 2.269 | 2.081 | 1.219 | -0.49 | -1.854 | -3.193 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NPg Best View | 8.797 | 8.494 | 8.016 | 7.374 | 6.731 | 5.924 | 4.937 | -1.074 | -7.985 | -12.154 | -15.747 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NPg Best View | 13.226 | 12.833 | 12.326 | 11.839 | 11.524 | 11.193 | 10.796 | 8.929 | 5.09 | 2.215 | -0.506 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NPg Best View | 5 | 4.923 | 4.811 | 4.681 | 4.582 | 4.481 | 4.364 | 3.838 | 2.68 | 1.741 | 0.864 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NPg Best View | 6.135 | 5.743 | 5.158 | 4.456 | 4.001 | 3.524 | 2.963 | 0.459 | -5.254 | -9.821 | -14.282 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NPg Best View | 10.026 | 9.787 | 9.372 | 8.854 | 8.549 | 8.224 | 7.825 | 6.093 | 1.549 | -1.985 | -5.266 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NPg Best View | 15.681 | 15.457 | 15.163 | 14.859 | 14.666 | 14.459 | 14.202 | 13.078 | 10.493 | 8.49 | 6.67 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NPg Best View | 6.104 | 5.931 | 5.574 | 5.119 | 4.864 | 4.589 | 4.25 | 2.749 | -1.165 | -4.093 | -6.917 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NPg Best View | 13.001 | 12.643 | 12.146 | 11.566 | 11.005 | 10.4 | 9.685 | 6.336 | 1.477 | -2.207 | -5.516 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NPg Best View | 12.796 | 12.761 | 12.661 | 12.531 | 12.461 | 12.387 | 12.301 | 11.952 | 10.493 | 9.311 | 8.151 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NPg Best View | 9.355 | 9.037 | 8.558 | 8.005 | 7.638 | 7.229 | 6.734 | 4.434 | 1.048 | -1.268 | -3.503 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NPg Best View | 11.393 | 11.437 | 11.402 | 11.316 | 11.22 | 11.081 | 10.891 | 9.762 | 8.059 | 7.06 | 6.22 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NPg Best View | 5.608 | 5.577 | 5.411 | 5.155 | 4.981 | 4.749 | 4.444 | 2.687 | -0.5 | -2.569 | -4.468 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NPg Best View | 28.601 | 28.549 | 28.433 | 28.277 | 28.135 | 27.962 | 27.746 | 26.524 | 24.862 | 23.761 | 22.77 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NPg Best View | 3.214 | 3.05 | 2.82 | 2.541 | 2.327 | 2.092 | 1.821 | 0.295 | -3.483 | -6.818 | -10.053 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NPg Best View | 1.93 | 1.916 | 1.879 | 1.831 | 1.792 | 1.748 | 1.69 | 1.41 | 0.994 | 0.672 | 0.362 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NPg Best View | 11.693 | 11.425 | 11.042 | 10.603 | 10.316 | 10.012 | 9.652 | 7.94 | 4.26 | 1.385 | -1.413 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NPg Best View | 9.933 | 9.967 | 9.946 | 9.884 | 9.873 | 9.844 | 9.788 | 9.412 | 7.924 | 6.802 | 5.734 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NPg Best View | 10.749 | 10.717 | 10.577 | 10.375 | 10.255 | 10.126 | 9.971 | 9.144 | 4.466 | 0.526 | -3.175 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NPg Best View | 1.823 | 1.772 | 1.678 | 1.554 | 1.443 | 1.311 | 1.154 | 0.379 | -0.876 | -1.814 | -2.701 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NPg Best View | 11.91 | 11.939 | 11.892 | 11.758 | 11.545 | 11.233 | 10.816 | 8.071 | 5.011 | 3.43 | 2.311 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NPg Best View | 15.726 | 15.714 | 15.665 | 15.606 | 15.575 | 15.529 | 15.457 | 15.027 | 13.915 | 13.131 | 12.405 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NPg Best View | 7.823 | 6.693 | 6.112 | 5.417 | 4.908 | 4.374 | 3.749 | 0.954 | -4.716 | -9.251 | -13.567 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NPg Best View | 12.016 | 11.956 | 11.814 | 11.629 | 11.518 | 11.395 | 11.233 | 10.496 | 8.422 | 6.809 | 5.341 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NPg Best View | 15.992 | 16.086 | 16.052 | 15.881 | 15.594 | 15.146 | 14.518 | 10.323 | 6.76 | 5.376 | 4.616 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NPg Best View | 8.829 | 8.518 | 7.983 | 7.322 | 7.004 | 6.649 | 6.199 | 3.961 | -1.595 | -5.741 | -9.761 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NPg Best View | 4.266 | 4.222 | 4.152 | 4.066 | 4.009 | 3.948 | 3.873 | 3.504 | 2.805 | 2.26 | 1.733 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NPg Best View | 8.904 | 8.586 | 8.109 | 7.601 | 7.346 | 7.072 | 6.735 | 5.216 | 1.202 | -1.813 | -4.677 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 14.497 | 14.386 | 14.136 | 13.832 | 13.577 | 13.302 | 12.988 | 11.475 | 7.846 | 4.945 | 2.134 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 13.511 | 13.45 | 13.271 | 13.017 | 12.813 | 12.58 | 12.303 | 10.801 | 6.354 | 2.693 | -0.849 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NPg Best View | 12.335 | 12.372 | 12.353 | 12.306 | 12.261 | 12.202 | 12.122 | 11.667 | 10.157 | 9.113 | 8.192 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NPg Best View | 8.151 | 8.216 | 8.219 | 8.193 | 8.218 | 8.238 | 8.246 | 8.282 | 6.991 | 5.923 | 4.862 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NPg Best View | 17.531 | 17.422 | 17.241 | 17.022 | 16.891 | 16.75 | 16.58 | 15.8 | 14.345 | 13.329 | 12.346 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NPg Best View | 5.028 | 5.079 | 5.102 | 5.1 | 5.077 | 5.029 | 4.947 | 4.377 | 3.541 | 2.871 | 2.254 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NPg Best View | 2.361 | 1.985 | 1.46 | 0.925 | 0.633 | 0.323 | -0.057 | -1.813 | -6.249 | -9.614 | -12.806 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NPg Best View | 11.603 | 11.292 | 10.856 | 10.401 | 10.106 | 9.796 | 9.425 | 7.758 | 3.791 | 0.757 | -2.044 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NPg Best View | 10.179 | 9.775 | 9.17 | 8.493 | 8.093 | 7.637 | 7.069 | 4.17 | -1.108 | -4.729 | -8.074 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 13.007 | 13.038 | 13.005 | 12.935 | 12.83 | 12.686 | 12.497 | 11.34 | 9.885 | 9.125 | 8.556 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NPg Best View | 16.101 | 15.934 | 15.662 | 15.324 | 15.16 | 14.983 | 14.76 | 13.683 | 11.233 | 9.409 | 7.654 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NPg Best View | 12.887 | 12.823 | 12.664 | 12.451 | 12.274 | 12.085 | 11.851 | 10.74 | 7.774 | 5.465 | 3.423 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NPg Best View | 9.461 | 9.265 | 8.915 | 8.475 | 8.199 | 7.88 | 7.477 | 5.391 | 1.604 | -1.002 | -3.429 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NPg Best View | 11.594 | 9.932 | 9.745 | 9.49 | 9.361 | 9.22 | 9.035 | 8.277 | 5.788 | 3.803 | 1.891 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NPg Best View | 4.156 | 4.06 | 3.923 | 3.77 | 3.649 | 3.52 | 3.367 | 2.652 | 1.434 | 0.52 | -0.326 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NPg Best View | 14.043 | 13.68 | 13.152 | 12.536 | 12.162 | 11.763 | 11.275 | 8.895 | 4.524 | 1.259 | -1.884 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NPg Best View | 2.27 | 2.016 | 1.551 | 0.977 | 0.581 | 0.16 | -0.362 | -2.706 | -8.699 | -13.378 | -17.644 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NPg Best View | 14.688 | 14.476 | 14.148 | 13.769 | 13.546 | 13.302 | 12.995 | 11.518 | 8.651 | 6.555 | 4.552 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NPg Best View | 7.748 | 7.4 | 6.86 | 6.238 | 5.895 | 5.531 | 5.086 | 3.023 | -2.082 | -5.987 | -9.808 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NPg Best View | 18.662 | 18.767 | 18.763 | 18.693 | 18.649 | 18.581 | 18.473 | 17.79 | 14.229 | 11.399 | 8.778 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NPg Best View | 12.561 | 12.441 | 12.237 | 12.017 | 11.807 | 11.588 | 11.337 | 10.249 | 8.441 | 7.221 | 6.182 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NPg Best View | 3.384 | 3.108 | 2.662 | 2.127 | 1.743 | 1.332 | 0.844 | -1.549 | -6.035 | -9.439 | -12.704 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NPg Best View | 3.652 | 2.939 | 1.997 | 0.914 | -0.145 | -1.271 | -2.601 | -8.778 | -17.369 | -23.847 | -29.417 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NPg Best View | 4.073 | 3.761 | 3.284 | 2.766 | 2.391 | 1.985 | 1.484 | 16.403 | 11.329 | 7.28 | 3.577 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NPg Best View | 12.57 | 12.135 | 11.523 | 10.825 | 10.399 | 9.961 | 9.454 | 7.211 | 2.835 | -0.533 | -3.874 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NPg Best View | 21.759 | 18.829 | 18.964 | 19.072 | 19.168 | 19.256 | 19.332 | 19.528 | 19.328 | 19.169 | 19.028 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NPg Best View | 3.504 | 3.246 | 2.83 | 2.284 | 1.759 | 1.098 | 0.286 | -3.86 | -8.284 | -11.087 | -13.591 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NPg Best View | 12.647 | 12.556 | 12.36 | 12.112 | 12.055 | 11.99 | 11.902 | 11.383 | 8.222 | 5.627 | 3.001 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NPg Best View | 14.076 | 14.17 | 14.236 | 14.287 | 14.356 | 14.418 | 14.467 | 14.657 | 14.383 | 14.172 | 13.944 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NPg Best View | 15.027 | 15.097 | 15.133 | 15.145 | 15.175 | 15.199 | 15.209 | 15.223 | 14.449 | 13.836 | 13.25 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NPg Best View | 9.748 | 9.274 | 8.572 | 7.742 | 7.228 | 6.685 | 6.04 | 3.123 | -2.125 | -6.004 | -9.754 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NPg Best View | 15.812 | 15.743 | 15.616 | 15.451 | 15.367 | 15.272 | 15.16 | 14.506 | 12.157 | 10.198 | 8.265 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NPg Best View | 5.532 | 5.491 | 5.343 | 5.141 | 5.046 | 4.944 | 4.82 | 4.179 | 0.723 | -2.041 | -4.699 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NPg Best View | 14.057 | 13.924 | 13.692 | 13.403 | 13.206 | 12.993 | 12.73 | 11.464 | 8.952 | 7.156 | 5.5 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NPg Best View | 18.317 | 14.876 | 14.826 | 14.767 | 14.72 | 14.664 | 14.583 | 14.331 | 14.007 | 13.823 | 13.666 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NPg Best View | 11.616 | 11.422 | 11.14 | 10.82 | 10.623 | 10.409 | 10.153 | 8.915 | 6.667 | 5.003 | 3.366 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NPg Best View | 2.533 | 2.345 | 2.065 | 1.722 | 1.461 | 1.158 | 0.795 | -1.162 | -3.74 | -5.403 | -6.908 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NPg Best View | 11.017 | 10.723 | 10.295 | 9.821 | 9.587 | 9.334 | 9.019 | 7.595 | 4.657 | 2.505 | 0.318 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NPg Best View | 10.106 | 9.86 | 9.435 | 8.921 | 8.639 | 8.333 | 7.955 | 7.305 | 3.724 | 1.079 | -1.471 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NPg Best View | 5.802 | 5.637 | 5.332 | 4.901 | 4.461 | 3.92 | 3.258 | -0.164 | -5.176 | -8.83 | -12.093 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NPg Best View | 16.399 | 16.28 | 16.107 | 15.898 | 15.731 | 15.553 | 15.344 | 14.318 | 12.46 | 10.986 | 9.61 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NPg Best View | 8.859 | 7.073 | 6.586 | 5.967 | 5.476 | 4.904 | 4.23 | 7.613 | 1.193 | -3.598 | -8 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NPg Best View | 3.826 | 3.701 | 3.525 | 3.321 | 3.167 | 3.009 | 2.824 | 1.957 | 0.572 | -0.485 | -1.493 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NPg Best View | 14.427 | 14.176 | 13.783 | 13.307 | 13.012 | 12.696 | 12.313 | 10.582 | 7.551 | 5.43 | 3.453 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NPg Best View | -0.265 | -0.446 | -0.719 | -0.048 | -0.316 | -0.607 | -0.956 | -2.556 | -5.353 | -7.493 | -9.462 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NPg Best View | 9.278 | 9.01 | 8.597 | 8.1 | 7.75 | 7.374 | 6.925 | 4.791 | 0.28 | -3.263 | -6.655 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NPg Best View | 7.81 | 7.571 | 7.157 | 6.642 | 6.339 | 6.007 | 5.592 | 3.534 | -0.961 | -4.272 | -7.419 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NPg Best View | 5.106 | 4.716 | 4.125 | 3.407 | 2.927 | 2.416 | 1.808 | -1.054 | -7.306 | -12.268 | -17.127 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NPg Best View | 16.155 | 15.9 | 15.482 | 14.971 | 14.634 | 14.266 | 13.814 | 11.691 | 8.075 | 5.553 | 3.184 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NPg Best View | 7.914 | 7.994 | 7.994 | 7.947 | 7.925 | 7.88 | 7.802 | 7.332 | 5.542 | 4.276 | 3.127 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NPg Best View | 13.903 | 14.676 | 14.358 | 6.006 | 5.409 | 4.789 | 4.061 | 1.665 | -2.303 | -5.581 | -8.553 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NPg Best View | 11.033 | 10.668 | 10.139 | 9.505 | 9.023 | 8.512 | 7.909 | 5.04 | 0.296 | -3.215 | -6.448 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NPg Best View | 6.666 | 6.728 | 6.692 | 6.59 | 6.571 | 6.532 | 6.459 | 6.09 | 4.26 | 2.832 | 1.466 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NPg Best View | 11.847 | 11.504 | 10.989 | 10.386 | 10.035 | 9.668 | 9.226 | 7.219 | 3.014 | -0.133 | -3.157 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NPg Best View | 5.162 | 4.714 | 4.059 | 3.272 | 2.59 | 1.842 | 0.967 | -3.602 | -10.566 | -15.848 | -20.881 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NPg Best View | 10.404 | 10.528 | 10.64 | 10.737 | 10.826 | 10.906 | 10.975 | 11.263 | 11.162 | 11.088 | 11.026 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NPg Best View | 11.353 | 11.491 | 11.594 | 11.658 | 11.686 | 11.676 | 11.62 | 11.07 | 10.329 | 10.044 | 9.889 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NPg Best View | 2.555 | 2.67 | 2.769 | 2.852 | 2.929 | 2.994 | 3.045 | 3.224 | 3.008 | 2.876 | 2.766 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NPg Best View | 6.47 | 6.323 | 6.079 | 5.805 | 5.658 | 5.492 | 5.277 | 4.414 | 2.554 | 1.234 | 0.033 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NPg Best View | 0.668 | 0.514 | 0.309 | 0.077 | -0.114 | -0.321 | -0.57 | -1.827 | -3.664 | -5.012 | -6.221 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NPg Best View | 12.523 | 12.312 | 11.98 | 11.57 | 11.256 | 10.911 | 10.501 | 8.439 | 5.014 | 2.668 | 0.634 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NPg Best View | 12.974 | 11.133 | 11.185 | 11.166 | 11.115 | 11.02 | 10.865 | 10.212 | 8.792 | 7.77 | 6.895 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NPg Best View | 9.33 | 9.053 | 15.652 | 15.243 | 14.976 | 14.692 | 14.341 | 12.728 | 9.232 | 6.598 | 4.134 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NPg Best View | 9.994 | 9.815 | 9.518 | 9.159 | 8.86 | 8.525 | 8.124 | 6.349 | 2.912 | 0.227 | -2.345 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NPg Best View | 3.458 | 1.888 | 1.461 | 1.116 | 0.878 | 0.615 | 0.28 | -1.279 | -5.8 | -9.409 | -12.742 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NPg Best View | 12.63 | 12.637 | 12.612 | 12.566 | 12.555 | 12.536 | 12.504 | 12.293 | 11.232 | 10.301 | 9.366 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NPg Best View | 8.48 | 8.376 | 15.134 | 14.812 | 14.669 | 14.504 | 14.286 | 13.167 | 9.748 | 7.194 | 4.741 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NPg Best View | 5.205 | 4.065 | 3.473 | 2.969 | 2.57 | 2.121 | 1.57 | -1.012 | -5.458 | -8.749 | -11.79 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NPg Best View | 10.273 | 9.885 | 9.281 | 8.568 | 8.202 | 7.82 | 7.362 | 5.299 | 0.282 | -3.532 | -7.298 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NPg Best View | 10.303 | 10.143 | 7.707 | 7.242 | 6.763 | 6.134 | 5.34 | 0.881 | -3.274 | -5.551 | -7.405 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NPg Best View | 8.396 | 8.008 | 7.429 | 6.763 | 6.308 | 5.821 | 5.243 | 2.525 | -1.745 | -4.798 | -7.737 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NPg Best View | 6.953 | 5.02 | 4.446 | 3.798 | 3.428 | 3.021 | 2.515 | 0.463 | -4.106 | -7.578 | -10.883 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NPg Best View | 8.613 | 8.01 | 8.109 | 8.139 | 8.126 | 8.063 | 7.943 | 7.114 | 5.33 | 4.233 | 3.36 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NPg Best View | 18.761 | 18.735 | 18.655 | 18.519 | 18.343 | 18.105 | 17.802 | 15.971 | 14.145 | 13.247 | 12.613 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NPg Best View | 8.731 | 8.668 | 8.492 | 8.253 | 8.153 | 8.04 | 7.882 | 7.152 | 4.542 | 2.494 | 0.479 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NPg Best View | 10.77 | 10.648 | 10.44 | 10.182 | 9.919 | 9.631 | 9.282 | 7.545 | 4.479 | 2.187 | 0.243 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NPg Best View | 12.096 | 11.876 | 11.505 | 11.038 | 10.797 | 10.544 | 10.237 | 8.841 | 4.862 | 1.796 | -1.144 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NPg Best View | 12.337 | 12.349 | 12.294 | 12.201 | 12.165 | 12.111 | 12.029 | 11.567 | 9.982 | 8.852 | 7.767 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NPg Best View | 8.47 | 8.649 | 8.805 | 8.95 | 9.083 | 9.2 | 9.296 | 9.668 | 9.357 | 9.126 | 8.917 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NPg Best View | 8.11 | 6.323 | 6.138 | 5.905 | 5.809 | 5.686 | 5.523 | 4.626 | 1.655 | -0.567 | -2.732 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NPg Best View | 9.991 | 8.859 | 8.959 | 9.036 | 9.094 | 9.144 | 9.179 | 9.336 | 8.58 | 8.003 | 7.477 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NPg Best View | 1.246 | 1.074 | 0.828 | 0.538 | 0.334 | 0.118 | -0.137 | -1.367 | -3.662 | -5.478 | -7.249 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 2.886 | 2.862 | 2.806 | 2.741 | 2.731 | 2.719 | 2.698 | 2.591 | 1.703 | 0.984 | 0.228 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NPg Best View | 12.887 | 12.805 | 12.63 | 12.408 | 12.174 | 11.894 | 11.56 | 9.667 | 7.283 | 5.821 | 4.548 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NPg Best View | 24.544 | 24.636 | 24.712 | 24.764 | 24.803 | 24.832 | 24.848 | 24.867 | 24.25 | 23.68 | 23.127 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NPg Best View | 13.857 | 13.926 | 13.952 | 13.953 | 13.981 | 14.001 | 14.006 | 14.016 | 13.103 | 12.356 | 11.64 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NPg Best View | -1.639 | -1.676 | -1.78 | -1.938 | -2.073 | -2.236 | -2.445 | -3.597 | -5.86 | -7.69 | -9.422 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NPg Best View | 3.308 | 3.084 | 2.715 | 2.204 | 1.718 | 1.115 | 0.375 | -3.921 | -10.074 | -14.337 | -18.221 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NPg Best View | 11.046 | 10.916 | 10.659 | 10.331 | 10.154 | 9.965 | 9.725 | 8.651 | 5.671 | 3.405 | 1.242 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NPg Best View | 11.415 | 11.562 | 11.683 | 11.778 | 11.849 | 11.891 | 11.901 | 11.764 | 11.565 | 11.585 | 11.657 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NPg Best View | 8.208 | 7.879 | 7.35 | 6.696 | 6.262 | 5.776 | 5.183 | 2.229 | -3.515 | -7.772 | -11.736 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NPg Best View | 11.782 | 11.074 | 10.866 | 10.617 | 10.441 | 10.265 | 10.077 | 9.421 | 6.875 | 4.643 | 2.46 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NPg Best View | 4.193 | 3.945 | 3.611 | 3.277 | 3.039 | 2.789 | 2.484 | 1.157 | -1.941 | -4.38 | -6.581 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NPg Best View | 11.04 | 10.908 | 10.641 | 10.29 | 10.056 | 9.809 | 9.505 | 8.076 | 4.183 | 1.068 | -1.848 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NPg Best View | -1.19 | -1.348 | -1.593 | -1.883 | -0.058 | -0.242 | -0.464 | -1.504 | -4.402 | -6.699 | -8.886 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NPg Best View | 15.308 | 15.271 | 15.182 | 15.043 | 14.886 | 14.693 | 14.457 | 13.09 | 10.661 | 8.915 | 7.363 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NPg Best View | 14.67 | 14.155 | 13.595 | 13.218 | 12.918 | 12.588 | 12.187 | 10.235 | 6.58 | 3.891 | 1.499 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NPg Best View | 10.143 | 9.828 | 9.316 | 8.702 | 8.374 | 8.021 | 7.591 | 5.605 | 1.674 | -1.156 | -3.995 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NPg Best View | 23.807 | 23.877 | 23.937 | 23.992 | 24.044 | 24.09 | 24.127 | 24.268 | 24.075 | 23.921 | 23.78 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NPg Best View | 8.596 | 8.686 | 8.758 | 8.811 | 8.853 | 8.888 | 8.91 | 8.969 | 8.06 | 7.33 | 6.681 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NPg Best View | 11.317 | 11.066 | 10.649 | 10.144 | 9.877 | 9.598 | 9.26 | 7.774 | 4.296 | 1.666 | -0.957 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NPg Best View | 4.365 | 4.349 | 4.308 | 4.251 | 4.207 | 4.157 | 4.091 | 3.892 | 3.498 | 3.143 | 2.784 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NPg Best View | 8.868 | 8.793 | 8.653 | 8.483 | 8.348 | 8.202 | 8.036 | 7.197 | 5.087 | 3.337 | 1.613 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NPg Best View | 13.917 | 13.697 | 13.34 | 12.915 | 12.682 | 12.435 | 12.131 | 10.714 | 7.117 | 4.281 | 1.509 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NPg Best View | 10.822 | 10.566 | 10.182 | 9.716 | 9.398 | 9.057 | 8.657 | 6.906 | 3.559 | 1.024 | -1.348 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NPg Best View | 7.861 | 7.54 | 7.07 | 6.507 | 6.012 | 5.486 | 4.868 | 2.031 | -2.183 | -5.28 | -8.046 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NPg Best View | 13.124 | 12.926 | 12.645 | 12.306 | 11.967 | 11.583 | 11.142 | 8.819 | 5.13 | 2.199 | -0.551 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NPg Best View | 7.762 | 7.77 | 7.665 | 7.495 | 7.336 | 7.137 | 6.879 | 5.358 | 1.471 | -1.401 | -3.957 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NPg Best View | 13.814 | 13.601 | 13.254 | 12.839 | 12.624 | 12.397 | 12.12 | 10.867 | 7.869 | 5.6 | 3.336 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NPg Best View | 7.352 | 7.018 | 6.54 | 6.045 | 5.725 | 5.383 | 4.963 | 20.101 | 15.402 | 11.713 | 8.276 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NPg Best View | 7.521 | 7.403 | 7.2 | 6.934 | 6.726 | 6.49 | 6.213 | 4.69 | 0.999 | -2.013 | -4.971 | Primary
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Falling Short | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - System Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NPg Best View | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 33.647 | 31.045 | 29.529 | 27.748 | 26.504 | 25.427 | 24.121 | 18.015 | 2.695 | -8.977 | -20.499 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Consumer Transformation | 43.555 | 43.516 | 42.138 | 42.054 | 42.171 | 42.343 | 42.412 | 42.329 | 35.987 | 31.108 | 26.224 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Consumer Transformation | 53.972 | 52.03 | 50.669 | 49.167 | 48.14 | 47.264 | 46.204 | 41.471 | 25.47 | 12.281 | -0.56 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Consumer Transformation | 32.971 | 30.953 | 28.444 | 25.703 | 23.521 | 21.503 | 19.093 | 7.57 | -18.684 | -39.682 | -59.925 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Consumer Transformation | 22.994 | 20.869 | 18.903 | 16.82 | 15.236 | 13.814 | 12.07 | 4.258 | -13.377 | -27.302 | -40.976 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Consumer Transformation | 14.598 | 13.746 | 12.52 | 11.379 | 10.443 | 9.564 | 8.429 | 3.34 | -5.297 | -11.198 | -16.62 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 31.433 | 30.743 | 30.023 | 29.204 | 28.599 | 28.025 | 27.274 | 23.399 | 12.22 | 3.706 | -4.002 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Consumer Transformation | 40.427 | 38.979 | 37.662 | 36.137 | 35.032 | 34.039 | 26.962 | -11.591 | -24.482 | -33.625 | -42.26 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 98.985 | 97.128 | 96.259 | 95.134 | 94.465 | 93.885 | 93.037 | 88.222 | 67.363 | 50.633 | 34.901 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Consumer Transformation | 28.109 | 27.369 | 26.688 | 25.898 | 25.218 | 24.547 | 23.721 | 19.701 | 8.825 | -0.136 | -8.395 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Consumer Transformation | 40.937 | 39.354 | 38.025 | 36.556 | 35.571 | 34.753 | 33.697 | 28.777 | 15.281 | 4.91 | -5.464 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Consumer Transformation | 68.844 | 66.968 | 65.495 | 62.312 | 61.18 | 60.171 | 58.914 | 53.627 | 43.54 | 35.972 | 28.476 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 19.114 | 17.875 | 17.504 | 17.07 | 16.721 | 16.38 | 15.964 | 13.685 | 8.048 | 3.431 | -0.948 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Consumer Transformation | 44.629 | 42.651 | 41.028 | 39.163 | 37.51 | 35.878 | 33.968 | 23.939 | 4.227 | -11.282 | -25.658 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Consumer Transformation | 14.478 | 9.945 | 7.451 | 4.971 | 2.735 | 0.542 | -2.219 | -13.659 | -30.547 | -42.511 | -53.286 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Consumer Transformation | 16.552 | 14.542 | 13.136 | 11.585 | 10.335 | 9.189 | 7.758 | 1.059 | -15.661 | -28.652 | -41.003 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 60.837 | 55.415 | 52.704 | 49.835 | 47.674 | 45.783 | 43.376 | 32.654 | 6.43 | -13.469 | -32.812 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 26.301 | 24.721 | 23.009 | 20.907 | 19.313 | 17.8 | 15.944 | 5.945 | -17.775 | -35.959 | -53.001 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.046 | 19.574 | 17.96 | 16.179 | 14.929 | 13.872 | 12.583 | 6.824 | -9.141 | -21.758 | -34.468 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Consumer Transformation | 34.881 | 34.117 | 33.917 | 33.484 | 33.122 | 32.681 | 31.488 | 25.2 | 16.53 | 11.437 | 7.7 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 28.81 | 27.634 | 26.249 | 24.583 | 23.214 | 21.904 | 20.214 | 12.343 | -7.974 | -23.852 | -38.602 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Consumer Transformation | 64.307 | 64.211 | 64.181 | 64.141 | 64.094 | 64.04 | 63.979 | 63.688 | 63.303 | 62.881 | 62.453 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | 2.509 | 2.493 | 2.467 | 2.44 | 2.416 | 2.393 | 2.361 | 2.212 | 1.924 | 1.719 | 1.529 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Consumer Transformation | 92.554 | 78.138 | 59.726 | 51.737 | 45.346 | 39.467 | 32.331 | 1.953 | -44.476 | -76.771 | -107.202 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 56.419 | 55.658 | 54.755 | 53.618 | 52.977 | 52.476 | 51.855 | 47.974 | 31.684 | 18.339 | 5.196 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 28.175 | 26.933 | 26.468 | 25.86 | 25.437 | 25.044 | 24.513 | 20.788 | 11.098 | 4.127 | -2.201 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 33.604 | 31.447 | 30.79 | 29.975 | 28.964 | 27.825 | 26.69 | 21.58 | 17.396 | 14.162 | 11.899 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Falling Short | 43.56 | 43.528 | 42.148 | 42.055 | 42.173 | 42.339 | 42.415 | 41.977 | 40.992 | 40.234 | 39.823 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Falling Short | 53.996 | 52.087 | 50.736 | 49.23 | 48.221 | 47.348 | 46.309 | 42.295 | 40.09 | 38.536 | 37.537 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Falling Short | 33.012 | 31.046 | 28.545 | 25.784 | 23.623 | 21.592 | 19.213 | 8.689 | 0.331 | -6.315 | -11.335 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Falling Short | 23.046 | 20.982 | 19.048 | 16.983 | 15.469 | 14.104 | 12.475 | 6.006 | 1.847 | -1.053 | -3.078 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Falling Short | 14.648 | 13.85 | 12.639 | 11.494 | 10.586 | 9.717 | 8.624 | 4.369 | 1.701 | 0.083 | -0.648 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 31.448 | 30.778 | 30.053 | 29.212 | 28.596 | 27.993 | 27.225 | 23.894 | 21.358 | 19.651 | 18.828 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Falling Short | 40.444 | 39.023 | 37.701 | 36.146 | 35.032 | 33.998 | 26.902 | -11.916 | -16.068 | -19.026 | -20.703 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 99 | 97.165 | 96.285 | 95.125 | 94.433 | 93.802 | 92.918 | 88.672 | 85.243 | 82.832 | 81.653 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Falling Short | 28.117 | 27.391 | 26.706 | 25.897 | 25.209 | 24.512 | 23.668 | 19.957 | 17.002 | 14.697 | 13.07 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Falling Short | 40.968 | 39.423 | 38.107 | 36.637 | 35.681 | 34.877 | 33.868 | 29.654 | 26.878 | 24.956 | 23.781 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Falling Short | 68.904 | 67.092 | 65.647 | 62.481 | 61.408 | 60.447 | 59.285 | 54.836 | 52.052 | 50.181 | 48.874 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 19.115 | 17.877 | 17.498 | 17.048 | 16.685 | 16.323 | 15.89 | 13.381 | 10.727 | 8.342 | 6.341 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Falling Short | 44.623 | 42.645 | 40.983 | 39.042 | 37.308 | 35.55 | 33.509 | 22.866 | 12.002 | 2.529 | -5.068 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Falling Short | 14.562 | 10.132 | 7.687 | 5.232 | 3.113 | 1.018 | -1.537 | -10.754 | -15.698 | -18.412 | -19.595 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Falling Short | 16.586 | 14.618 | 13.224 | 11.667 | 10.445 | 9.31 | 7.93 | 2.011 | -2.392 | -5.556 | -7.643 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 60.915 | 55.585 | 52.906 | 50.042 | 47.957 | 46.119 | 43.85 | 34.799 | 28.987 | 25.105 | 22.865 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 26.285 | 24.696 | 22.923 | 20.712 | 18.997 | 17.304 | 15.257 | 4.894 | -5.393 | -14.017 | -20.247 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 21.085 | 19.66 | 18.067 | 16.293 | 15.082 | 14.05 | 12.819 | 7.411 | 3.157 | -0.248 | -2.987 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Falling Short | 34.842 | 34.035 | 33.751 | 33.188 | 32.655 | 31.988 | 30.53 | 24.082 | 18.819 | 14.827 | 13.174 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 28.846 | 27.72 | 26.361 | 24.71 | 23.415 | 22.171 | 20.62 | 14.437 | 10.516 | 8.121 | 6.897 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Falling Short | 64.307 | 64.211 | 64.181 | 64.141 | 64.094 | 64.04 | 63.979 | 63.301 | 62.333 | 61.302 | 60.242 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | 2.51 | 2.496 | 2.471 | 2.444 | 2.424 | 2.403 | 2.376 | 2.264 | 2.189 | 2.146 | 2.125 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Falling Short | 92.677 | 78.432 | 60.062 | 52.021 | 45.719 | 39.81 | 32.778 | 6.473 | -10.171 | -21.072 | -26.867 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 56.412 | 55.647 | 54.726 | 53.555 | 52.882 | 52.333 | 51.667 | 47.982 | 44.348 | 41.301 | 39.106 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 28.153 | 26.891 | 26.375 | 25.688 | 25.165 | 24.637 | 23.952 | 20.107 | 15.858 | 12.493 | 10.6 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 33.513 | 30.596 | 28.656 | 26.495 | 25.117 | 24.06 | 22.22 | 3.799 | -9.754 | -18.862 | -17.765 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Leading the Way | 43.487 | 43.308 | 41.745 | 41.499 | 41.561 | 41.751 | 41.589 | 34.194 | 28.663 | 24.961 | 27.049 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Leading the Way | 53.871 | 51.664 | 49.915 | 48.021 | 46.839 | 45.967 | 44.131 | 24.341 | 9.824 | -0.674 | 0.949 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Leading the Way | 32.803 | 30.429 | 27.394 | 24.119 | 21.753 | 19.748 | 16.49 | -14.617 | -38.352 | -55.528 | -55.66 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Leading the Way | 22.888 | 20.533 | 18.209 | 15.767 | 14.116 | 12.791 | 10.464 | -11.274 | -27.166 | -38.251 | -37.538 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Leading the Way | 14.567 | 13.616 | 12.208 | 10.882 | 9.902 | 9.05 | 7.671 | -3.478 | -10.936 | -15.314 | -14.196 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 31.391 | 30.582 | 29.668 | 28.646 | 27.966 | 27.374 | 26.174 | 12.944 | 3.293 | -3.096 | -1.533 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Leading the Way | 40.321 | 38.641 | 36.983 | 35.121 | 33.892 | 32.896 | 25.377 | -23.586 | -34.68 | -41.485 | -39.929 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 98.871 | 96.732 | 95.438 | 93.876 | 93.031 | 92.416 | 90.574 | 66.063 | 47.637 | 34.721 | 37.859 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Leading the Way | 28.057 | 27.194 | 26.324 | 25.332 | 24.575 | 23.88 | 22.576 | 9.554 | -0.343 | -7.734 | -7.495 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Leading the Way | 40.82 | 39.008 | 37.336 | 35.523 | 34.435 | 33.671 | 32.117 | 15.664 | 3.757 | -4.127 | -2.611 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Leading the Way | 68.8 | 66.804 | 65.125 | 61.751 | 60.599 | 59.674 | 58.197 | 45.261 | 36.149 | 30.013 | 30.569 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 19.093 | 17.794 | 17.331 | 16.801 | 16.41 | 16.053 | 15.448 | 8.934 | 3.826 | -0.049 | -0.367 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Leading the Way | 44.532 | 42.323 | 40.378 | 38.206 | 36.381 | 34.639 | 32.196 | 9.772 | -7.959 | -21.136 | -23.186 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Leading the Way | 14.485 | 9.843 | 7.103 | 4.379 | 2.164 | 0.092 | -2.984 | -26.466 | -41.591 | -51.233 | -49.89 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Leading the Way | 16.454 | 14.2 | 12.452 | 10.595 | 9.244 | 8.126 | 6.245 | -14.079 | -29.102 | -39.731 | -38.418 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 60.704 | 54.871 | 51.547 | 48.122 | 45.801 | 44.027 | 40.916 | 7.675 | -15.645 | -31.405 | -28.134 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 26.135 | 24.145 | 21.869 | 19.21 | 17.317 | 15.654 | 12.916 | -15.404 | -36.434 | -51.177 | -51.036 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 20.939 | 19.173 | 17.154 | 15.009 | 13.651 | 12.657 | 10.91 | -8.386 | -22.819 | -33.118 | -32.052 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Leading the Way | 34.789 | 33.768 | 33.256 | 32.541 | 31.933 | 31.263 | 29.601 | 17.465 | 10.638 | 7.353 | 8.505 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 28.73 | 27.325 | 25.61 | 23.643 | 22.232 | 21.008 | 18.72 | -6.296 | -24.437 | -37.07 | -34.765 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Leading the Way | 64.307 | 64.21 | 64.178 | 64.138 | 64.091 | 64.037 | 63.976 | 63.579 | 63.195 | 62.774 | 62.427 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | 2.508 | 2.49 | 2.46 | 2.43 | 2.408 | 2.388 | 2.356 | 1.973 | 1.718 | 1.553 | 1.6 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Leading the Way | 92.192 | 77.05 | 57.462 | 48.256 | 41.499 | 35.724 | 27.059 | -34.869 | -75.376 | -99.641 | -97.405 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 56.263 | 55.22 | 53.927 | 52.401 | 51.594 | 51.076 | 49.759 | 31.395 | 16.948 | 6.538 | 7.675 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 28.074 | 26.661 | 25.95 | 25.09 | 24.503 | 24.003 | 23.048 | 11.851 | 3.49 | -1.902 | -1.502 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 33.353 | 30.998 | 30.036 | 29.009 | 27.874 | 26.638 | 25.196 | 17.605 | 6.922 | -5.711 | -23.569 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - System Transformation | 43.181 | 43.137 | 41.869 | 41.976 | 41.998 | 41.945 | 41.759 | 40.153 | 34.4 | 28.315 | 20.065 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - System Transformation | 53.722 | 51.915 | 50.956 | 49.999 | 48.954 | 47.84 | 46.678 | 40.496 | 30.781 | 17.784 | -2.28 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - System Transformation | 32.495 | 30.632 | 28.65 | 26.641 | 24.461 | 22.15 | 19.656 | 6.374 | -13.308 | -35.06 | -64.938 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - System Transformation | 22.763 | 20.903 | 19.52 | 18.173 | 16.718 | 15.188 | 13.519 | 4.977 | -7.689 | -21.738 | -42.129 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - System Transformation | 14.348 | 13.558 | 12.588 | 11.766 | 10.85 | 9.863 | 8.771 | 3.26 | -3.211 | -9.692 | -18.525 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 31.204 | 30.546 | 30.008 | 29.462 | 28.828 | 28.125 | 27.34 | 22.676 | 14.295 | 5.723 | -6.145 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - System Transformation | 40.1 | 38.851 | 37.992 | 37.059 | 35.987 | 34.799 | 27.667 | -11.772 | -21.691 | -31.974 | -45.729 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 98.492 | 96.658 | 96.098 | 95.467 | 94.673 | 93.745 | 92.664 | 85.524 | 70.428 | 53.511 | 28.731 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - System Transformation | 27.866 | 27.057 | 26.404 | 25.707 | 24.93 | 24.094 | 23.199 | 18.192 | 9.824 | 0.888 | -11.686 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - System Transformation | 40.643 | 39.286 | 38.468 | 37.643 | 36.714 | 35.708 | 34.57 | 28.49 | 18.955 | 7.816 | -8.546 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - System Transformation | 68.634 | 66.924 | 65.841 | 63.125 | 62.097 | 61.018 | 59.816 | 54.208 | 46.253 | 38.084 | 27.02 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 18.885 | 17.582 | 17.204 | 16.801 | 16.347 | 15.852 | 15.304 | 12.109 | 6.846 | 1.492 | -5.219 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - System Transformation | 43.942 | 41.819 | 40.224 | 38.513 | 36.625 | 34.584 | 32.31 | 19.769 | 1.302 | -16.744 | -38.002 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - System Transformation | 14.21 | 9.747 | 7.639 | 5.681 | 3.55 | 1.312 | -1.08 | -12.073 | -25.469 | -37.265 | -52.402 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - System Transformation | 16.173 | 14.251 | 13.153 | 12.038 | 10.793 | 9.453 | 7.963 | 0.126 | -12.657 | -26.161 | -44.218 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 60.263 | 55.216 | 53.355 | 51.57 | 49.573 | 47.409 | 44.969 | 32.761 | 13.556 | -7.352 | -36.007 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 25.662 | 24.136 | 22.771 | 21.223 | 19.44 | 17.432 | 15.122 | 2.091 | -18.049 | -38.661 | -64.738 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 20.631 | 19.377 | 18.281 | 17.19 | 15.984 | 14.69 | 13.222 | 5.808 | -6.304 | -20.286 | -39.504 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - System Transformation | 34.599 | 33.798 | 33.667 | 33.418 | 33.013 | 32.412 | 30.968 | 23.329 | 16.619 | 10.762 | 4.284 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 28.496 | 27.393 | 26.332 | 25.17 | 23.855 | 22.43 | 20.837 | 12.185 | -3.351 | -18.799 | -40.104 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - System Transformation | 64.135 | 63.918 | 63.759 | 63.584 | 63.394 | 63.189 | 62.968 | 62.006 | 60.996 | 59.936 | 58.869 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | 2.502 | 2.487 | 2.468 | 2.45 | 2.428 | 2.405 | 2.376 | 2.226 | 1.959 | 1.743 | 1.495 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - System Transformation | 92.133 | 78.754 | 62.676 | 57.351 | 51.629 | 45.584 | 38.977 | 8.367 | -23.253 | -56.687 | -102.977 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 56.127 | 55.581 | 55.13 | 54.597 | 53.97 | 53.259 | 52.418 | 46.854 | 35.086 | 21.323 | 1.496 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 27.927 | 26.764 | 26.507 | 26.183 | 25.747 | 25.201 | 24.485 | 19.758 | 11.502 | 3.808 | -5.766 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 33.808 | 31.396 | 30.019 | 28.401 | 27.235 | 26.229 | 25.05 | 19.544 | 5.075 | -6.006 | -17.159 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NPg Best View | 43.767 | 43.917 | 42.641 | 42.669 | 42.792 | 42.956 | 43.015 | 42.987 | 36.923 | 32.245 | 27.446 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NPg Best View | 54.115 | 52.368 | 51.1 | 49.726 | 48.683 | 47.799 | 46.788 | 42.524 | 27.057 | 14.247 | 1.667 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NPg Best View | 33.275 | 31.575 | 29.308 | 26.822 | 24.796 | 22.92 | 20.744 | 10.233 | -14.428 | -34.286 | -53.817 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NPg Best View | 23.269 | 21.412 | 19.702 | 17.881 | 16.54 | 15.364 | 13.975 | 7.394 | -9.141 | -22.275 | -35.321 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NPg Best View | 15.105 | 14.633 | 13.792 | 12.962 | 12.359 | 11.775 | 10.972 | 6.874 | -0.844 | -6.13 | -11.152 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 31.605 | 31.079 | 30.472 | 29.764 | 29.207 | 28.666 | 27.977 | 24.41 | 14.016 | 6.052 | -1.37 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NPg Best View | 40.635 | 39.418 | 38.266 | 36.913 | 35.894 | 34.963 | 27.986 | -9.521 | -21.386 | -29.833 | -38.131 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 99.318 | 97.777 | 97.121 | 96.208 | 95.608 | 95.069 | 94.289 | 89.843 | 70.119 | 54.2 | 38.893 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NPg Best View | 28.229 | 27.626 | 27.032 | 26.34 | 25.686 | 25.03 | 24.244 | 20.491 | 10.235 | 1.715 | -6.307 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NPg Best View | 41.162 | 39.807 | 38.636 | 37.34 | 36.438 | 35.701 | 34.785 | 30.477 | 17.688 | 7.808 | -2.259 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NPg Best View | 69.204 | 67.637 | 66.43 | 63.492 | 62.572 | 61.77 | 60.794 | 56.509 | 47.102 | 40.003 | 32.889 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 19.236 | 18.102 | 17.809 | 17.442 | 17.128 | 16.805 | 16.402 | 14.159 | 8.859 | 4.49 | 0.216 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NPg Best View | 44.861 | 43.173 | 41.684 | 40 | 38.281 | 36.561 | 34.598 | 24.678 | 6.427 | -8.052 | -22.028 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NPg Best View | 15.047 | 11.024 | 9.095 | 7.136 | 5.472 | 3.842 | 1.834 | -7.292 | -22.351 | -33.057 | -42.921 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NPg Best View | 16.82 | 15.075 | 13.87 | 12.529 | 11.404 | 10.378 | 9.14 | 3.202 | -12.526 | -24.816 | -36.735 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 61.328 | 56.395 | 54.041 | 51.545 | 49.6 | 47.929 | 45.895 | 36.616 | 11.875 | -6.985 | -25.665 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 26.607 | 25.37 | 23.877 | 21.976 | 20.41 | 18.859 | 16.951 | 6.916 | -14.992 | -31.89 | -48.441 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 21.309 | 20.113 | 18.696 | 17.128 | 15.985 | 15.033 | 13.911 | 8.9 | -6.362 | -18.49 | -30.838 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NPg Best View | 34.968 | 34.291 | 34.075 | 33.595 | 33.054 | 32.376 | 30.895 | 23.783 | 16.429 | 12.266 | 8.696 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 29.061 | 28.161 | 26.998 | 25.594 | 24.419 | 23.316 | 21.959 | 15.223 | -3.995 | -19.08 | -33.314 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NPg Best View | 64.468 | 64.515 | 64.603 | 64.664 | 64.697 | 64.697 | 64.649 | 64.384 | 64.005 | 63.588 | 63.167 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | 2.517 | 2.51 | 2.491 | 2.471 | 2.455 | 2.44 | 2.42 | 2.301 | 2.032 | 1.841 | 1.66 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NPg Best View | 93.668 | 80.276 | 63.158 | 56.378 | 51.415 | 46.848 | 41.334 | 16.118 | -24.356 | -52.617 | -80.174 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 56.405 | 55.719 | 54.749 | 53.609 | 52.767 | 52.08 | 51.311 | 47.226 | 31.336 | 18.259 | 5.106 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 28.241 | 27.081 | 26.601 | 25.973 | 25.405 | 24.839 | 24.119 | 19.896 | 11.109 | 4.779 | -1.423 | BSP
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Consumer Transformation | 5.471 | 5.1 | 4.494 | 3.787 | 3.339 | 3.001 | 2.587 | 0.798 | -4.782 | -9.102 | -13.631 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Consumer Transformation | 10.897 | 9.841 | 7.554 | 6.297 | 5.327 | 4.489 | 3.48 | -0.468 | -9.822 | -16.849 | -23.739 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 7.99 | 7.608 | 9.021 | 8.35 | 7.871 | 7.448 | 6.929 | 4.556 | -0.761 | -4.82 | -8.872 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Consumer Transformation | 5.747 | 5.464 | 4.971 | 4.387 | 3.992 | 3.663 | 3.25 | 1.455 | -3.989 | -8.302 | -12.626 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Consumer Transformation | 22.754 | 22.794 | 22.832 | 22.867 | 22.9 | 22.931 | 22.96 | 23.013 | 23.016 | 23.019 | 23.021 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Consumer Transformation | 2.057 | 2.011 | 1.896 | 1.748 | 1.67 | 1.61 | 1.52 | 1.012 | -0.99 | -2.525 | -4.039 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Consumer Transformation | 3.658 | 3.615 | 3.561 | 3.507 | 3.454 | 3.399 | 3.331 | 3.026 | 2.67 | 2.4 | 2.157 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Consumer Transformation | 2.638 | 2.457 | 2.196 | 1.887 | 1.633 | 1.394 | 1.112 | -0.428 | -3.716 | -6.27 | -8.712 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Consumer Transformation | 7.233 | 7.105 | 6.877 | 6.604 | 6.439 | 6.317 | 6.157 | 5.337 | 2.11 | -0.474 | -3.114 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Consumer Transformation | 11.891 | 11.577 | 11.082 | 10.562 | 10.15 | 9.765 | 9.273 | 7.06 | 3.292 | 0.72 | -1.64 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Consumer Transformation | 4.763 | 4.128 | 3.6 | 3.031 | 2.585 | 2.174 | 1.679 | -0.587 | -6.946 | -12.135 | -17.078 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Consumer Transformation | 11.045 | 10.48 | 10.144 | 9.742 | 9.487 | 9.27 | 8.99 | 7.557 | 2.612 | -1.363 | -5.24 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Consumer Transformation | 7.479 | 7.076 | 6.528 | 5.932 | 5.493 | 5.085 | 4.6 | 1.969 | -2.969 | -6.531 | -9.846 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Consumer Transformation | 3.537 | 2.84 | 2.374 | 1.851 | 1.499 | 1.185 | 0.793 | -1.106 | -6.212 | -10.226 | -14.086 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 13.303 | 13.131 | 12.845 | 12.511 | 12.224 | 11.92 | 10.929 | 6.975 | 3.569 | 1.487 | -0.101 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 16.526 | 16.54 | 16.505 | 16.4 | 16.306 | 16.208 | 16.088 | 15.407 | 14.229 | 13.656 | 13.236 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Consumer Transformation | 9.535 | 8.62 | 8.44 | 8.213 | 8.028 | 7.835 | 7.58 | 6.125 | 1.803 | -1.538 | -4.463 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Consumer Transformation | 10.192 | 9.549 | 9.142 | 8.685 | 8.316 | 7.969 | 7.549 | 5.537 | 0.191 | -4.155 | -8.19 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Consumer Transformation | 15.555 | 15.307 | 14.939 | 14.539 | 14.239 | 13.971 | 13.64 | 12.212 | 8.409 | 5.357 | 2.482 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Consumer Transformation | 7.136 | 7.014 | 6.817 | 6.557 | 6.308 | 6.024 | 5.661 | 2.952 | -1.503 | -4.163 | -6.058 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Consumer Transformation | 20.245 | 19.936 | 19.517 | 19.061 | 18.653 | 18.248 | 17.763 | 15.123 | 9.763 | 5.654 | 1.919 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 17.765 | 17.609 | 17.393 | 17.152 | 16.943 | 16.738 | 16.496 | 15.287 | 12.39 | 9.93 | 7.596 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Consumer Transformation | 11.79 | 11.006 | 10.241 | 9.368 | 8.742 | 8.192 | 7.53 | 4.563 | -2.304 | -7.632 | -12.905 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Consumer Transformation | 7.86 | 7.329 | 7.199 | 7.045 | 6.954 | 6.891 | 6.801 | 6.386 | 4.343 | 2.739 | 1.132 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Consumer Transformation | 8.8 | 8.411 | 7.76 | 6.994 | 6.461 | 6.019 | 5.458 | 2.575 | -4.111 | -8.837 | -13.524 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Consumer Transformation | 6.911 | 6.236 | 5.596 | 4.962 | 4.446 | 3.988 | 3.426 | 1.073 | -3.179 | -6.28 | -9.313 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Consumer Transformation | 8.077 | 7.791 | 7.347 | 6.836 | 6.459 | 6.135 | 5.73 | 3.818 | -1.028 | -4.68 | -8.214 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Consumer Transformation | 8.044 | 7.815 | 7.445 | 7.011 | 6.637 | 6.281 | 5.838 | 3.855 | -0.841 | -4.629 | -8.18 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Consumer Transformation | 4.028 | 3.75 | 3.268 | 2.685 | 2.269 | 1.892 | 1.418 | -0.824 | -7 | -11.832 | -16.42 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Consumer Transformation | 7.798 | 7.424 | 6.906 | 6.324 | 5.832 | 5.371 | 4.828 | 2.308 | -2.873 | -7.134 | -11.325 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Consumer Transformation | 8.429 | 8.256 | 8.352 | 8.411 | 8.493 | 8.573 | 8.621 | 8.714 | 6.97 | 5.62 | 4.349 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Consumer Transformation | 5.552 | 4.578 | 4.255 | 3.928 | 3.651 | 3.385 | 3.044 | 1.598 | -1.417 | -3.758 | -5.943 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Consumer Transformation | 14.635 | 13.283 | 12.486 | 11.546 | 10.855 | 10.237 | 9.485 | 5.924 | -1.764 | -7.356 | -12.782 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Consumer Transformation | 12.841 | 12.817 | 12.738 | 12.633 | 12.577 | 12.535 | 12.465 | 12.14 | 10.745 | 9.677 | 8.579 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Consumer Transformation | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 12.647 | 12.647 | 12.599 | 12.516 | 12.474 | 12.44 | 12.383 | 11.968 | 10.087 | 8.67 | 7.35 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 14.683 | 14.628 | 14.513 | 14.351 | 14.251 | 14.162 | 14.039 | 13.109 | 10.488 | 8.651 | 6.988 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Consumer Transformation | 4.492 | 4.442 | 4.366 | 4.283 | 4.243 | 4.222 | 4.194 | 4.04 | 2.994 | 2.114 | 1.171 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Consumer Transformation | 8.957 | 8.793 | 8.553 | 8.298 | 8.128 | 7.983 | 7.807 | 6.995 | 4.759 | 3.028 | 1.334 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Consumer Transformation | 8.337 | 8.113 | 7.745 | 7.329 | 7.02 | 6.734 | 6.37 | 4.677 | -0.335 | -4.301 | -8.02 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 23.137 | 22.857 | 22.819 | 22.772 | 22.744 | 22.72 | 22.674 | 22.471 | 21.215 | 20.178 | 19.235 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Consumer Transformation | 6.812 | 6.71 | 6.502 | 6.255 | 6.077 | 5.898 | 5.65 | 4.116 | 0.089 | -2.711 | -5.094 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Consumer Transformation | 5.103 | 4.268 | 3.587 | 2.796 | 2.19 | 1.635 | 0.941 | -2.443 | -8.899 | -13.252 | -17.199 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Consumer Transformation | 9.92 | 8.617 | 8.143 | 7.585 | 7.169 | 6.789 | 6.308 | 4.073 | -2.321 | -7.27 | -11.942 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 8.63 | 8.48 | 8.226 | 7.957 | 7.707 | 7.448 | 7.102 | 5.548 | 2.384 | -0.03 | -2.147 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 13.377 | 13.085 | 12.632 | 12.153 | 11.784 | 11.443 | 11.013 | 9.08 | 3.412 | -1.229 | -5.603 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Consumer Transformation | 4.249 | 3.778 | 3.642 | 3.478 | 3.358 | 3.255 | 3.118 | 2.5 | 0.132 | -1.826 | -3.79 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Consumer Transformation | 8.073 | 7.729 | 7.153 | 6.461 | 5.899 | 5.37 | 4.708 | 1.455 | -7.317 | -14.175 | -20.49 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Consumer Transformation | 18.02 | 18.009 | 17.971 | 17.917 | 17.888 | 17.864 | 17.828 | 17.625 | 16.421 | 15.383 | 14.375 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Consumer Transformation | 6.605 | 6.408 | 6.086 | 5.746 | 5.496 | 5.279 | 4.982 | 3.64 | 0.693 | -1.484 | -3.666 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Consumer Transformation | 8.999 | 8.991 | 8.953 | 8.898 | 8.848 | 8.791 | 8.707 | 8.138 | 6.975 | 6.179 | 5.506 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Consumer Transformation | 0.513 | 0.324 | -0.043 | -0.512 | -0.815 | -1.054 | -1.368 | 14.324 | 9.273 | 5.231 | 1.154 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Consumer Transformation | 5.325 | 4.563 | 3.588 | 2.75 | 2.037 | 1.347 | 0.498 | -3.284 | -9.528 | -13.974 | -17.935 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Consumer Transformation | 10.145 | 9.66 | 8.209 | 7.401 | 6.827 | 6.346 | 5.769 | 3.089 | -3.343 | -8.174 | -13.047 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Consumer Transformation | 14.374 | 14.051 | 13.997 | 13.913 | 13.831 | 13.736 | 13.602 | 12.772 | 11.055 | 9.859 | 8.869 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Consumer Transformation | 7.312 | 5.852 | 5.44 | 4.93 | 4.579 | 4.276 | 3.873 | 1.879 | -5.52 | -11.307 | -16.817 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Consumer Transformation | 7.275 | 6.821 | 6.129 | 5.359 | 4.778 | 4.256 | 3.607 | 0.617 | -5.801 | -10.686 | -15.447 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Consumer Transformation | 28.91 | 28.36 | 27.595 | 26.877 | 26.284 | 25.722 | 24.997 | 21.812 | 16.989 | 13.658 | 10.484 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Consumer Transformation | 5.173 | 4.908 | 4.485 | 3.989 | 3.639 | 3.341 | 2.974 | 1.238 | -3.439 | -7.119 | -10.778 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Consumer Transformation | 11.695 | 11.453 | 11.085 | 10.686 | 10.442 | 10.258 | 10.03 | 9.09 | 6.234 | 3.998 | 1.617 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Consumer Transformation | 18.285 | 18.181 | 17.979 | 17.726 | 17.537 | 17.363 | 17.138 | 15.987 | 12.29 | 9.366 | 6.637 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Consumer Transformation | 8.639 | 8.646 | 7.15 | 7.035 | 6.979 | 6.933 | 6.849 | 6.26 | 4.198 | 2.759 | 1.443 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Consumer Transformation | 25.865 | 25.918 | 25.947 | 25.944 | 25.918 | 25.864 | 25.775 | 24.897 | 23.336 | 22.524 | 22.104 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Consumer Transformation | 14.564 | 14.089 | 14.055 | 13.995 | 14.012 | 14.06 | 14.086 | 14.162 | 12.994 | 12.065 | 10.982 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Consumer Transformation | 4.881 | 4.662 | 4.273 | 3.794 | 3.254 | 2.626 | 1.815 | -2.942 | -7.848 | -10.152 | -11.206 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Consumer Transformation | 15.814 | 15.946 | 16.059 | 16.154 | 16.249 | 16.341 | 16.422 | 16.75 | 16.52 | 16.308 | 16.069 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 7.483 | 6.947 | 6.436 | 5.86 | 5.39 | 4.949 | 4.411 | 18.049 | 13.445 | 9.978 | 6.687 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Consumer Transformation | 2.477 | 2.334 | 2.059 | 1.722 | 1.57 | 1.485 | 1.367 | 0.793 | -2.668 | -5.441 | -8.397 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Consumer Transformation | 14.309 | 13.969 | 13.478 | 12.954 | 12.515 | 12.088 | 11.555 | 9.031 | 4.952 | 2.066 | -0.596 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Consumer Transformation | 14.998 | 12.6 | 12.602 | 12.569 | 12.563 | 12.547 | 12.479 | 12.005 | 10.035 | 8.579 | 7.314 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Consumer Transformation | 8.679 | 7.884 | 7.193 | 6.485 | 5.958 | 5.493 | 4.913 | 2.226 | -4.634 | -9.945 | -15.145 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Consumer Transformation | 18.458 | 18.35 | 18.185 | 18.019 | 17.903 | 17.812 | 17.692 | 17.156 | 15.385 | 13.978 | 12.532 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Consumer Transformation | 10.998 | 10.4 | 9.522 | 8.564 | 7.885 | 7.321 | 6.627 | 3.56 | -3.272 | -8.406 | -13.743 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Consumer Transformation | 3.531 | 2.716 | 2.009 | 1.18 | 0.52 | -0.102 | -0.856 | -4.176 | -10.542 | -15.167 | -19.443 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Consumer Transformation | 2.668 | 2.225 | 1.632 | 1.058 | 0.63 | 0.274 | -0.165 | -2.016 | -5.652 | -8.318 | -11.037 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Consumer Transformation | 8.521 | 8.486 | 8.421 | 8.338 | 8.274 | 8.212 | 8.13 | 7.546 | 6.414 | 5.736 | 5.186 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Consumer Transformation | 21.021 | 20.738 | 20.709 | 20.663 | 20.636 | 20.618 | 20.598 | 20.517 | 19.739 | 19.116 | 18.513 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Consumer Transformation | 19.203 | 19.013 | 18.698 | 18.334 | 18.093 | 17.912 | 17.686 | 16.644 | 13.383 | 10.921 | 8.385 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Consumer Transformation | 14.59 | 14.736 | 14.873 | 15.003 | 15.127 | 15.244 | 15.355 | 15.833 | 16.154 | 16.425 | 16.669 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Consumer Transformation | 14.661 | 14.749 | 14.78 | 14.789 | 14.829 | 14.871 | 14.876 | 14.788 | 13.66 | 12.917 | 12.219 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Consumer Transformation | 1.154 | 1.162 | 1.068 | 0.885 | 20.643 | 20.46 | 20.192 | 17.825 | 12.167 | 8.398 | 5.447 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Consumer Transformation | 7.545 | 7.173 | 6.636 | 6.057 | 5.636 | 5.264 | 4.811 | 2.814 | -1.682 | -5.177 | -8.685 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Consumer Transformation | 6.871 | 6.487 | 5.909 | 5.266 | 4.77 | 4.313 | 3.753 | 1.233 | -3.444 | -6.685 | -9.722 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Consumer Transformation | 16.233 | 16.148 | 16.016 | 15.867 | 15.717 | 15.558 | 15.36 | 14.353 | 12.17 | 10.433 | 8.911 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Consumer Transformation | 6.69 | 6.549 | 6.331 | 6.099 | 5.922 | 5.762 | 5.555 | 4.603 | 2.041 | 0.104 | -1.73 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 1.699 | 1.171 | 0.467 | -0.238 | -0.856 | -1.456 | -2.19 | -5.586 | -11.233 | -15.489 | -19.5 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Consumer Transformation | 18.432 | 18.419 | 18.376 | 18.318 | 18.278 | 18.242 | 18.189 | 17.885 | 16.954 | 16.255 | 15.605 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Consumer Transformation | 6.562 | 6.275 | 5.842 | 5.392 | 5.078 | 4.809 | 4.472 | 3.094 | -0.18 | -2.692 | -5.224 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Consumer Transformation | 2.77 | 2.75 | 2.72 | 2.688 | 2.661 | 2.633 | 2.597 | 2.43 | 2.122 | 1.902 | 1.697 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Consumer Transformation | 9.159 | 8.821 | 8.679 | 8.504 | 8.386 | 8.281 | 8.143 | 7.334 | 4.732 | 2.699 | 0.791 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Consumer Transformation | 14.281 | 14.088 | 13.796 | 13.478 | 13.223 | 12.987 | 12.69 | 11.375 | 8.749 | 6.758 | 4.826 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Consumer Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Consumer Transformation | 20.801 | 20.625 | 20.371 | 20.108 | 19.912 | 19.741 | 19.528 | 18.542 | 15.863 | 13.798 | 11.795 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Consumer Transformation | 8.324 | 8.013 | 7.542 | 7.037 | 6.734 | 6.511 | 6.231 | 4.986 | 0.949 | -2.199 | -5.509 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Consumer Transformation | 14.262 | 14.01 | 13.63 | 13.207 | 12.925 | 12.689 | 12.402 | 11.033 | 7.524 | 4.873 | 2.233 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Consumer Transformation | 33.156 | 32.766 | 32.717 | 32.661 | 32.626 | 32.603 | 32.568 | 32.444 | 31.815 | 31.329 | 30.841 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Consumer Transformation | 4.362 | 3.511 | 2.763 | 1.94 | 1.329 | 0.819 | 0.193 | -2.398 | -7.704 | -11.558 | -15.518 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Consumer Transformation | 14.566 | 13.816 | 13.479 | 13.069 | 12.727 | 12.397 | 12.019 | 17.899 | 12.844 | 8.804 | 4.92 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Consumer Transformation | 9.527 | 9.421 | 9.227 | 8.994 | 8.772 | 8.543 | 8.25 | 6.663 | 1.804 | -2.105 | -5.592 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Consumer Transformation | 15.39 | 15.342 | 15.257 | 15.152 | 15.085 | 15.03 | 14.957 | 14.515 | 12.928 | 11.67 | 10.441 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 24.317 | 22.474 | 22.034 | 21.567 | 21.198 | 20.853 | 20.428 | 18.737 | 15.668 | 13.345 | 11.136 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Consumer Transformation | 5.261 | 4.737 | 4.34 | 3.893 | 3.531 | 3.186 | 2.784 | 0.876 | -4.044 | -8.169 | -12.113 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Consumer Transformation | 1.467 | 0.641 | -0.014 | -0.695 | -1.201 | -1.634 | -2.163 | -4.507 | -10.654 | -15.663 | -20.716 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Consumer Transformation | 3.134 | 3.089 | 1.702 | 1.613 | 1.532 | 1.45 | 1.344 | 0.874 | 0.348 | 0.019 | -0.252 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Consumer Transformation | 7.505 | 7.011 | 8.618 | 8.21 | 7.889 | 7.581 | 7.177 | 5.269 | -0.008 | -4.144 | -7.994 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Consumer Transformation | 5.647 | 5.497 | 5.193 | 4.795 | 4.629 | 4.54 | 4.409 | 3.652 | -1.45 | -5.65 | -10.048 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Consumer Transformation | 32.128 | 30.756 | 30.683 | 30.589 | 30.504 | 30.411 | 30.293 | 29.65 | 27.639 | 25.957 | 24.455 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Consumer Transformation | 12.227 | 12.097 | 11.869 | 11.599 | 11.386 | 11.183 | 10.928 | 9.759 | 5.825 | 2.553 | -0.483 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Consumer Transformation | 8.787 | 8.017 | 7.644 | 7.313 | 7.057 | 6.822 | 6.53 | 5.452 | 3.089 | 1.259 | -0.47 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Consumer Transformation | 6.53 | 6.602 | 6.629 | 6.627 | 6.676 | 6.736 | 6.779 | 6.87 | 5.823 | 5.011 | 4.161 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Consumer Transformation | 13.507 | 13.466 | 13.363 | 13.216 | 13.089 | 12.961 | 12.793 | 11.96 | 8.933 | 6.482 | 4.267 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 14.687 | 14.664 | 14.58 | 14.43 | 14.244 | 14.001 | 13.676 | 11.242 | 7.393 | 5.084 | 3.503 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 13.001 | 12.855 | 12.631 | 12.353 | 12.183 | 12.041 | 11.874 | 10.965 | 7.531 | 4.543 | 1.467 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Consumer Transformation | 4.613 | 3.544 | 3.161 | 2.708 | 2.357 | 2.033 | 1.663 | -0.126 | -4.339 | -7.791 | -11.184 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Consumer Transformation | 4.811 | 3.088 | 1.704 | 0.158 | -1.059 | -2.124 | -3.366 | -8.523 | -17.237 | -23.692 | -30.197 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Consumer Transformation | 11.531 | 10.579 | 9.982 | 9.448 | 9.027 | 8.66 | 8.21 | 6.35 | 2.812 | 0.198 | -2.432 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Consumer Transformation | 15.797 | 14.947 | 14.462 | 13.912 | 13.517 | 13.163 | 12.722 | 10.797 | 5.805 | 1.916 | -1.801 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Consumer Transformation | 8.13 | 7.953 | 7.625 | 7.227 | 6.923 | 6.643 | 6.279 | 4.639 | 0.287 | -3.138 | -6.352 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Consumer Transformation | 12.772 | 12.811 | 12.845 | 12.874 | 12.899 | 12.921 | 12.936 | 12.984 | 12.909 | 12.834 | 12.756 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Consumer Transformation | 21.706 | 21.634 | 21.494 | 21.312 | 21.192 | 21.09 | 20.964 | 20.399 | 18.824 | 17.606 | 16.372 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Consumer Transformation | 15.073 | 15.223 | 15.351 | 15.459 | 15.57 | 15.676 | 15.767 | 16.139 | 15.542 | 15.063 | 14.606 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 10.706 | 10.289 | 9.692 | 9.039 | 8.557 | 8.136 | 7.634 | 5.396 | 0.323 | -3.571 | -7.442 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.908 | 21.877 | 21.819 | 21.756 | 21.717 | 21.687 | 21.643 | 21.443 | 20.817 | 20.32 | 19.798 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Consumer Transformation | 2.596 | 2.345 | 1.922 | 1.428 | 1.096 | 0.823 | 0.481 | -0.998 | -5.821 | -9.624 | -13.371 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Consumer Transformation | 6.601 | 6.587 | 6.562 | 6.533 | 6.514 | 6.497 | 6.474 | 6.369 | 6.013 | 5.735 | 5.466 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Consumer Transformation | 6.073 | 5.264 | 4.934 | 4.601 | 4.378 | 4.215 | 4.001 | 3.108 | 0.626 | -1.199 | -3.14 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Consumer Transformation | 12.03 | 11.422 | 10.523 | 9.5 | 8.648 | 7.843 | 6.861 | 1.993 | -8.697 | -16.899 | -24.441 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Consumer Transformation | 10.511 | 9.011 | 8.082 | 7.506 | 7.079 | 6.689 | 6.199 | 3.842 | -2.185 | -6.726 | -10.962 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 15.164 | 14.993 | 14.764 | 14.513 | 14.28 | 14.041 | 13.757 | 12.265 | 9.31 | 6.963 | 4.855 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 15.946 | 15.886 | 15.815 | 15.741 | 15.667 | 15.592 | 15.508 | 15.106 | 14.571 | 14.1 | 13.659 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Consumer Transformation | 2.096 | 1.693 | 22.725 | 22.396 | 22.157 | 21.941 | 21.658 | 19.83 | 15.685 | 12.809 | 10.163 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Consumer Transformation | 13.667 | 13.1 | 12.645 | 12.174 | 11.769 | 11.385 | 10.906 | 8.931 | 6.522 | 4.998 | 3.624 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Consumer Transformation | 3.266 | 3.061 | 2.773 | 2.467 | 2.229 | 2.009 | 1.749 | 0.643 | -1.26 | -2.701 | -4.09 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Consumer Transformation | 2.822 | 2.674 | 2.476 | 2.268 | 2.077 | 1.885 | 1.651 | 0.509 | -1.25 | -2.553 | -3.712 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 12.409 | 11.749 | 11.292 | 10.742 | 10.305 | 9.904 | 9.39 | 7.069 | 0.845 | -4.07 | -8.768 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Consumer Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Consumer Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Consumer Transformation | 17.645 | 17.109 | 16.868 | 16.589 | 16.402 | 16.241 | 16.036 | 15.125 | 12.015 | 9.521 | 7.107 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Consumer Transformation | 11.195 | 10.122 | 9.998 | 9.85 | 9.7 | 9.536 | 9.328 | 8.288 | 6.569 | 5.277 | 4.17 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Consumer Transformation | 10.469 | 10.215 | 9.829 | 9.418 | 9.137 | 8.902 | 8.602 | 7.148 | 3.622 | 1.043 | -1.526 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Consumer Transformation | 12.97 | 12.668 | 12.265 | 11.869 | 11.53 | 11.205 | 10.801 | 8.915 | 5.706 | 3.31 | 1.052 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Consumer Transformation | 10.511 | 9.719 | 9.487 | 9.201 | 8.975 | 8.761 | 8.498 | 7.262 | 3.944 | 1.241 | -1.311 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Consumer Transformation | 10.341 | 10.176 | 9.892 | 9.556 | 9.348 | 9.182 | 8.964 | 7.823 | 4.303 | 1.604 | -1.063 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Consumer Transformation | 16.844 | 16.063 | 16.023 | 15.945 | 15.913 | 15.895 | 15.84 | 15.476 | 13.314 | 11.604 | 9.943 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Consumer Transformation | 15.768 | 15.422 | 14.9 | 14.328 | 13.899 | 13.497 | 12.991 | 10.337 | 5.018 | 1.255 | -2.208 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | 5.547 | 5.401 | 5.179 | 4.948 | 4.739 | 4.53 | 4.265 | 3.097 | 1.393 | 0.196 | -0.868 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Consumer Transformation | 12.485 | 12.008 | 10.017 | 9.345 | 8.903 | 8.52 | 8.042 | 5.737 | -0.331 | -4.709 | -8.894 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Consumer Transformation | 23.246 | 13.673 | 2.514 | 1.777 | 1.233 | 0.753 | 0.164 | -2.374 | -7.673 | -11.591 | -15.352 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Consumer Transformation | 0.668 | -0.205 | -1.014 | -3.592 | -4.239 | -4.814 | -5.529 | -8.512 | -14.396 | -18.883 | -23.316 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Consumer Transformation | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Consumer Transformation | 3.276 | 3.121 | 2.906 | 2.653 | 2.463 | 2.285 | 2.074 | 0.858 | -2.278 | -4.788 | -7.173 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Consumer Transformation | 12.067 | 11.223 | 10.818 | 10.3 | 9.924 | 9.592 | 9.201 | 7.395 | 3.19 | 0.116 | -2.874 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 5.89 | 4.219 | 4.017 | 3.734 | 3.585 | 3.473 | 3.307 | 2.444 | -1.05 | -3.684 | -6.236 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 27.96 | 27.983 | 28.006 | 28.028 | 28.048 | 28.068 | 28.087 | 28.168 | 28.233 | 28.287 | 28.335 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Consumer Transformation | 19.994 | 18.92 | 18.48 | 17.981 | 17.621 | 17.307 | 16.926 | 15.299 | 11.499 | 8.511 | 5.533 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Consumer Transformation | 8.44 | 7.869 | 8.045 | 8.147 | 8.209 | 8.207 | 8.117 | 6.835 | 4.227 | 2.97 | 2.371 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Consumer Transformation | 3.183 | 3.098 | 3.079 | 3.053 | 3.023 | 2.988 | 2.949 | 2.723 | 2.369 | 1.981 | 1.588 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Consumer Transformation | 13.824 | 13.446 | 12.892 | 12.306 | 11.913 | 11.594 | 11.206 | 9.458 | 3.941 | -0.584 | -5.156 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Consumer Transformation | 2.336 | 2.007 | 1.549 | 1.051 | 0.592 | 0.132 | -0.428 | -3.161 | -7.774 | -11.275 | -14.451 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Consumer Transformation | 7.792 | 6.82 | 6.424 | 6.005 | 5.634 | 5.29 | 4.862 | 3.1 | 0.769 | -0.827 | -2.382 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 23.554 | 22.973 | 22.422 | 21.792 | 21.291 | 20.82 | 20.244 | 17.537 | 11.059 | 5.914 | 1.074 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Consumer Transformation | 11.23 | 10.88 | 10.308 | 9.639 | 9.201 | 8.85 | 8.412 | 6.471 | 1.204 | -2.744 | -6.754 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Consumer Transformation | 11.146 | 10.77 | 10.219 | 9.613 | 9.159 | 8.753 | 8.255 | 5.988 | 0.45 | -3.986 | -8.367 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Consumer Transformation | 12.908 | 12.733 | 12.836 | 12.912 | 13.016 | 13.125 | 13.215 | 13.568 | 12.82 | 12.229 | 11.602 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Consumer Transformation | 5.991 | 5.529 | 4.918 | 4.301 | 3.779 | 3.278 | 2.684 | -0.041 | -6.221 | -11.36 | -16.264 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Consumer Transformation | 8.569 | 6.987 | 6.889 | 6.755 | 6.647 | 6.532 | 6.358 | 5.439 | 2.996 | 1.157 | -0.451 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Consumer Transformation | 7.821 | 7.085 | 6.698 | 6.25 | 5.899 | 5.57 | 5.166 | 3.348 | -1.421 | -5.344 | -9.102 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Consumer Transformation | 31.099 | 31.107 | 31.114 | 31.12 | 31.127 | 31.134 | 31.141 | 31.171 | 31.168 | 31.166 | 31.159 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Consumer Transformation | 10.303 | 10.282 | 10.209 | 10.108 | 25.465 | 25.445 | 25.409 | 25.231 | 23.627 | 22.298 | 20.93 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Consumer Transformation | 7.597 | 5.859 | 20.334 | 19.781 | 19.324 | 18.882 | 18.324 | 16.009 | 10.6 | 6.331 | 2.357 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Consumer Transformation | 8.989 | 8.726 | 8.368 | 7.97 | 7.596 | 7.222 | 6.772 | 4.508 | 0.599 | -2.449 | -5.289 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Consumer Transformation | 11.67 | 11.548 | 11.372 | 11.195 | 11.04 | 10.89 | 10.71 | 9.989 | 8.635 | 7.58 | 6.631 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Consumer Transformation | 19.935 | 19.402 | 19.297 | 19.162 | 19.082 | 19.012 | 18.907 | 18.395 | 15.78 | 13.576 | 11.483 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Consumer Transformation | 10.595 | 10.12 | 9.449 | 8.806 | 8.284 | 7.8 | 7.189 | 4.383 | -0.988 | -4.841 | -8.437 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Consumer Transformation | 11.934 | 11.528 | 11.179 | 10.777 | 10.487 | 10.236 | 9.933 | 8.566 | 4.074 | 0.337 | -3.313 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Consumer Transformation | 10.918 | 10.313 | 9.899 | 9.442 | 9.059 | 8.699 | 8.248 | 6.332 | 2.168 | -1.152 | -4.287 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 13.921 | 13.909 | 13.866 | 13.803 | 13.779 | 13.762 | 13.733 | 13.55 | 12.473 | 11.64 | 10.832 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 14.113 | 14.102 | 14.064 | 14.003 | 13.964 | 13.93 | 13.882 | 13.555 | 12.302 | 11.393 | 10.572 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 18.662 | 18.543 | 18.359 | 18.152 | 17.987 | 17.838 | 17.649 | 16.811 | 15.302 | 14.226 | 13.177 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 18.873 | 18.757 | 18.577 | 18.369 | 18.216 | 18.085 | 17.922 | 17.191 | 15.333 | 13.924 | 12.519 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Consumer Transformation | 12.143 | 11.909 | 11.565 | 11.187 | 10.864 | 10.55 | 10.174 | 8.533 | 3.902 | -0.122 | -3.911 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 22.115 | 21.693 | 21.126 | 20.589 | 20.182 | 19.824 | 19.378 | 17.383 | 13.548 | 10.737 | 7.938 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Consumer Transformation | 26.993 | 26.086 | 26.02 | 25.946 | 25.871 | 25.787 | 25.689 | 25.262 | 24.787 | 24.417 | 24.1 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Consumer Transformation | 5.591 | 5.171 | 5.131 | 5.087 | 5.052 | 5.02 | 4.98 | 4.808 | 4.297 | 3.893 | 3.501 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Consumer Transformation | 11.175 | 11.206 | 11.195 | 11.16 | 11.157 | 11.163 | 11.152 | 11.06 | 9.29 | 7.811 | 6.424 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Falling Short | 5.528 | 5.425 | 5.258 | 5.03 | 4.73 | 4.388 | 4.054 | 2.72 | 1.918 | 1.373 | 1.016 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Falling Short | 11.029 | 10.412 | 8.805 | 8.288 | 7.619 | 6.867 | 6.143 | 3.384 | 1.683 | 0.705 | 0.181 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 8.013 | 7.821 | 9.569 | 9.258 | 8.869 | 8.433 | 8.002 | 6.119 | 4.749 | 3.747 | 3.043 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Falling Short | 5.748 | 5.635 | 5.461 | 5.225 | 4.916 | 4.563 | 4.221 | 2.855 | 2.122 | 1.691 | 1.437 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Falling Short | 22.752 | 22.771 | 22.789 | 22.805 | 22.818 | 22.83 | 22.841 | 22.859 | 22.86 | 22.86 | 22.86 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Falling Short | 1.92 | 1.871 | 1.8 | 1.707 | 1.587 | 1.448 | 1.304 | 0.583 | -0.124 | -0.739 | -1.224 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Falling Short | 3.658 | 3.627 | 3.591 | 3.551 | 3.503 | 3.451 | 3.4 | 3.167 | 2.981 | 2.837 | 2.72 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Falling Short | 2.42 | 2.207 | 1.967 | 1.694 | 1.382 | 1.043 | 0.691 | -1.152 | -3.097 | -4.828 | -6.235 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Falling Short | 7.052 | 6.94 | 6.799 | 6.63 | 6.424 | 6.194 | 5.958 | 4.814 | 3.701 | 2.691 | 1.828 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Falling Short | 11.959 | 11.841 | 11.662 | 11.43 | 11.114 | 10.742 | 10.374 | 8.755 | 7.639 | 6.977 | 6.688 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Falling Short | 4.76 | 4.262 | 3.988 | 3.664 | 3.268 | 2.826 | 2.385 | 0.505 | -0.909 | -1.958 | -2.686 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Falling Short | 11.019 | 10.546 | 10.408 | 10.226 | 9.993 | 9.724 | 9.448 | 8.256 | 7.448 | 6.883 | 6.59 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Falling Short | 7.433 | 7.142 | 6.809 | 6.435 | 5.998 | 5.512 | 5.01 | 2.484 | 0.076 | -1.886 | -3.233 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Falling Short | 3.482 | 2.889 | 2.655 | 2.378 | 2.039 | 1.657 | 1.275 | -0.429 | -1.734 | -2.751 | -3.489 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 13.262 | 13.151 | 12.997 | 12.799 | 12.535 | 12.213 | 11.261 | 7.718 | 5.892 | 4.588 | 4.083 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 16.431 | 16.419 | 16.392 | 16.351 | 16.292 | 16.219 | 16.136 | 15.529 | 14.463 | 13.515 | 12.904 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Falling Short | 9.501 | 8.609 | 8.516 | 8.384 | 8.203 | 7.984 | 7.75 | 6.603 | 5.586 | 4.89 | 4.612 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Falling Short | 10.23 | 9.671 | 9.438 | 9.156 | 8.816 | 8.436 | 8.05 | 6.434 | 5.454 | 4.802 | 4.453 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Falling Short | 15.612 | 15.486 | 15.326 | 15.136 | 14.896 | 14.621 | 14.35 | 13.303 | 12.654 | 12.219 | 11.993 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Falling Short | 7.119 | 7.047 | 6.947 | 6.809 | 6.619 | 6.375 | 6.079 | 4.036 | 1.338 | -0.632 | -1.373 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Falling Short | 20.241 | 20.018 | 19.758 | 19.458 | 19.099 | 18.695 | 18.276 | 16.131 | 14.057 | 12.472 | 11.508 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 17.615 | 17.424 | 17.212 | 16.977 | 16.712 | 16.426 | 16.139 | 14.746 | 13.46 | 12.3 | 11.266 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Falling Short | 11.887 | 11.355 | 11.03 | 10.637 | 10.158 | 9.624 | 9.104 | 6.893 | 5.343 | 4.196 | 3.368 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Falling Short | 7.826 | 7.351 | 7.327 | 7.283 | 7.216 | 7.136 | 7.057 | 6.709 | 6.452 | 6.29 | 6.198 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Falling Short | 8.815 | 8.707 | 8.522 | 8.258 | 7.899 | 7.474 | 7.035 | 4.925 | 3.123 | 1.931 | 1.444 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Falling Short | 7.074 | 6.662 | 6.398 | 6.089 | 5.703 | 5.27 | 4.85 | 3.156 | 2.117 | 1.444 | 1.019 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Falling Short | 8.168 | 8.068 | 7.923 | 7.737 | 7.486 | 7.196 | 6.909 | 5.605 | 4.509 | 3.738 | 3.312 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Falling Short | 8.032 | 7.879 | 7.676 | 7.417 | 7.092 | 6.728 | 6.373 | 4.878 | 3.913 | 3.264 | 2.822 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Falling Short | 4.062 | 3.945 | 3.767 | 3.524 | 3.201 | 2.827 | 2.452 | 0.85 | -0.258 | -0.975 | -1.322 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Falling Short | 7.703 | 7.396 | 7.044 | 6.64 | 6.172 | 5.667 | 5.167 | 2.845 | 0.858 | -0.825 | -2.274 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Falling Short | 8.201 | 7.96 | 8.019 | 8.053 | 8.061 | 8.05 | 8.032 | 7.848 | 7.565 | 7.352 | 7.242 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Falling Short | 5.516 | 4.613 | 4.436 | 4.227 | 3.963 | 3.662 | 3.365 | 2.131 | 1.231 | 0.565 | 0.095 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Falling Short | 14.627 | 13.514 | 13.179 | 12.764 | 12.244 | 11.653 | 11.063 | 8.269 | 5.704 | 3.71 | 2.382 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Falling Short | 12.786 | 12.793 | 12.782 | 12.753 | 12.703 | 12.639 | 12.575 | 12.288 | 12.074 | 11.935 | 11.852 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Falling Short | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 12.576 | 12.582 | 12.572 | 12.543 | 12.492 | 12.427 | 12.353 | 11.939 | 11.484 | 11.149 | 10.995 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 14.651 | 14.641 | 14.613 | 14.563 | 14.487 | 14.388 | 14.272 | 13.529 | 12.614 | 11.944 | 11.688 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Falling Short | 4.48 | 4.464 | 4.444 | 4.421 | 4.392 | 4.36 | 4.327 | 4.166 | 4.018 | 3.888 | 3.772 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Falling Short | 9.016 | 8.953 | 8.873 | 8.778 | 8.658 | 8.523 | 8.392 | 7.846 | 7.516 | 7.32 | 7.222 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Falling Short | 8.359 | 8.258 | 8.112 | 7.922 | 7.67 | 7.38 | 7.095 | 5.89 | 5.118 | 4.649 | 4.397 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 23.088 | 22.804 | 22.786 | 22.755 | 22.706 | 22.645 | 22.585 | 22.352 | 22.243 | 22.176 | 22.134 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Falling Short | 6.757 | 6.717 | 6.643 | 6.532 | 6.368 | 6.161 | 5.936 | 4.693 | 3.39 | 2.493 | 2.163 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Falling Short | 5.174 | 4.612 | 4.387 | 4.071 | 3.642 | 3.135 | 2.618 | 0.198 | -1.852 | -3.174 | -3.684 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Falling Short | 9.931 | 8.785 | 8.608 | 8.368 | 8.05 | 7.684 | 7.323 | 5.746 | 4.58 | 3.851 | 3.479 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 8.633 | 8.547 | 8.423 | 8.262 | 8.042 | 7.782 | 7.523 | 6.436 | 5.722 | 5.288 | 5.093 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 13.441 | 13.293 | 13.097 | 12.857 | 12.546 | 12.191 | 11.843 | 10.456 | 9.708 | 9.257 | 9.003 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Falling Short | 4.098 | 3.615 | 3.509 | 3.376 | 3.213 | 3.034 | 2.856 | 2.019 | 1.248 | 0.571 | -0.049 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Falling Short | 8.09 | 7.924 | 7.682 | 7.352 | 6.918 | 6.417 | 5.916 | 3.641 | 1.886 | 0.76 | 0.237 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Falling Short | 17.943 | 17.913 | 17.875 | 17.827 | 17.769 | 17.705 | 17.639 | 17.324 | 17.046 | 16.784 | 16.537 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Falling Short | 6.611 | 6.548 | 6.449 | 6.317 | 6.135 | 5.919 | 5.706 | 4.782 | 4.177 | 3.818 | 3.637 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Falling Short | 8.89 | 8.848 | 8.793 | 8.724 | 8.636 | 8.531 | 8.415 | 7.753 | 7.008 | 6.389 | 5.987 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Falling Short | 0.468 | 0.395 | 0.266 | 0.078 | -0.173 | -0.464 | -0.752 | 15.191 | 14.471 | 13.958 | 13.595 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Falling Short | 5.643 | 5.245 | 4.788 | 4.308 | 3.713 | 3.037 | 2.376 | -0.422 | -2.202 | -3.295 | -3.826 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Falling Short | 10.217 | 10.018 | 9.013 | 8.684 | 8.274 | 7.811 | 7.348 | 5.267 | 3.502 | 2.19 | 1.336 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Falling Short | 14.205 | 13.825 | 13.739 | 13.627 | 13.485 | 13.318 | 13.135 | 12.14 | 11.044 | 10.131 | 9.516 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Falling Short | 7.235 | 5.918 | 5.789 | 5.588 | 5.308 | 4.976 | 4.643 | 3.108 | 1.848 | 1.017 | 0.586 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Falling Short | 7.394 | 7.189 | 6.912 | 6.565 | 6.127 | 5.631 | 5.138 | 3.065 | 1.79 | 1.014 | 0.655 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Falling Short | 29.129 | 28.92 | 28.649 | 28.337 | 27.922 | 27.439 | 26.974 | 24.979 | 23.665 | 22.929 | 22.584 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Falling Short | 5.099 | 4.944 | 4.739 | 4.482 | 4.165 | 3.809 | 3.453 | 1.859 | 0.62 | -0.349 | -1.061 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Falling Short | 11.748 | 11.662 | 11.544 | 11.398 | 11.213 | 11.004 | 10.799 | 10.031 | 9.675 | 9.438 | 9.278 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Falling Short | 18.25 | 18.197 | 18.114 | 17.996 | 17.837 | 17.651 | 17.462 | 16.583 | 15.883 | 15.41 | 15.164 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Falling Short | 8.553 | 8.579 | 7.146 | 7.125 | 7.074 | 6.998 | 6.909 | 6.375 | 5.733 | 5.269 | 5.083 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Falling Short | 25.776 | 25.796 | 25.8 | 25.784 | 25.744 | 25.678 | 25.587 | 24.843 | 23.757 | 22.981 | 22.754 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Falling Short | 14.421 | 13.945 | 13.957 | 13.952 | 13.93 | 13.894 | 13.853 | 13.661 | 13.525 | 13.386 | 13.261 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Falling Short | 4.818 | 4.656 | 4.412 | 4.075 | 3.613 | 3.042 | 2.409 | -1.194 | -5.175 | -7.958 | -8.965 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Falling Short | 15.574 | 15.595 | 15.606 | 15.604 | 15.591 | 15.569 | 15.542 | 15.33 | 15.011 | 14.648 | 14.268 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 7.513 | 7.116 | 6.864 | 6.558 | 6.179 | 5.755 | 5.342 | 19.558 | 18.24 | 17.284 | 16.622 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Falling Short | 2.455 | 2.446 | 2.407 | 2.339 | 2.237 | 2.114 | 1.991 | 1.484 | 1.156 | 0.912 | 0.736 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Falling Short | 14.359 | 14.178 | 13.95 | 13.675 | 13.33 | 12.938 | 12.548 | 10.736 | 9.282 | 8.286 | 7.697 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Falling Short | 14.865 | 12.428 | 12.433 | 12.408 | 12.341 | 12.242 | 12.129 | 11.572 | 11.057 | 10.697 | 10.573 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Falling Short | 8.705 | 8.156 | 7.865 | 7.524 | 7.089 | 6.595 | 6.109 | 3.883 | 2.056 | 0.7 | -0.263 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Falling Short | 18.401 | 18.34 | 18.264 | 18.175 | 18.06 | 17.931 | 17.804 | 17.21 | 16.7 | 16.278 | 15.909 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Falling Short | 11.162 | 10.95 | 10.659 | 10.294 | 9.827 | 9.299 | 8.784 | 6.632 | 5.263 | 4.405 | 3.897 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Falling Short | 3.547 | 2.917 | 2.573 | 2.145 | 1.609 | 1.003 | 0.398 | -2.181 | -4.21 | -5.697 | -6.591 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Falling Short | 2.821 | 2.645 | 2.427 | 2.179 | 1.867 | 1.512 | 1.166 | -0.207 | -0.985 | -1.462 | -1.716 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Falling Short | 8.509 | 8.503 | 8.487 | 8.46 | 8.418 | 8.363 | 8.297 | 7.856 | 7.277 | 6.86 | 6.714 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Falling Short | 21.002 | 20.73 | 20.725 | 20.711 | 20.691 | 20.668 | 20.646 | 20.554 | 20.47 | 20.413 | 20.371 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Falling Short | 19.21 | 19.163 | 19.082 | 18.968 | 18.814 | 18.633 | 18.453 | 17.653 | 16.98 | 16.488 | 16.189 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Falling Short | 14.436 | 14.508 | 14.573 | 14.632 | 14.686 | 14.734 | 14.777 | 14.932 | 15.006 | 15.033 | 15.044 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Falling Short | 14.498 | 14.555 | 14.592 | 14.61 | 14.601 | 14.572 | 14.535 | 14.273 | 13.95 | 13.711 | 13.603 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Falling Short | 1.022 | 1.016 | 0.974 | 0.884 | 20.635 | 20.426 | 20.158 | 18.27 | 15.789 | 14.009 | 13.456 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Falling Short | 7.59 | 7.394 | 7.15 | 6.863 | 6.511 | 6.119 | 5.737 | 4.139 | 3.126 | 2.419 | 1.907 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Falling Short | 6.962 | 6.8 | 6.58 | 6.302 | 5.941 | 5.529 | 5.123 | 3.324 | 1.91 | 0.959 | 0.442 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Falling Short | 16.197 | 16.118 | 16.018 | 15.895 | 15.743 | 15.57 | 15.394 | 14.555 | 13.837 | 13.309 | 12.98 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Falling Short | 6.637 | 6.547 | 6.429 | 6.284 | 6.1 | 5.889 | 5.678 | 4.745 | 4.047 | 3.54 | 3.209 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 1.829 | 1.529 | 1.177 | 0.776 | 0.285 | -0.262 | -0.8 | -3.25 | -5.165 | -6.503 | -7.384 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Falling Short | 18.402 | 18.397 | 18.382 | 18.356 | 18.316 | 18.267 | 18.215 | 17.955 | 17.715 | 17.547 | 17.469 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Falling Short | 6.616 | 6.491 | 6.323 | 6.123 | 5.869 | 5.581 | 5.298 | 4.227 | 3.641 | 3.24 | 2.976 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Falling Short | 2.774 | 2.768 | 2.758 | 2.745 | 2.727 | 2.706 | 2.685 | 2.59 | 2.513 | 2.47 | 2.448 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Falling Short | 9.042 | 8.702 | 8.605 | 8.486 | 8.338 | 8.169 | 7.991 | 7.08 | 6.17 | 5.406 | 4.857 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Falling Short | 14.296 | 14.195 | 14.064 | 13.902 | 13.699 | 13.471 | 13.249 | 12.299 | 11.658 | 11.236 | 10.947 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Falling Short | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Falling Short | 20.847 | 20.777 | 20.686 | 20.575 | 20.432 | 20.269 | 20.108 | 19.41 | 18.93 | 18.639 | 18.496 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Falling Short | 8.363 | 8.251 | 8.102 | 7.924 | 7.698 | 7.442 | 7.19 | 6.164 | 5.552 | 5.115 | 4.793 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Falling Short | 14.284 | 14.174 | 14.032 | 13.858 | 13.642 | 13.399 | 13.157 | 12.074 | 11.25 | 10.652 | 10.267 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Falling Short | 33.138 | 32.766 | 32.755 | 32.736 | 32.705 | 32.668 | 32.633 | 32.498 | 32.417 | 32.368 | 32.337 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Falling Short | 4.469 | 3.938 | 3.7 | 3.387 | 2.976 | 2.506 | 2.055 | 0.233 | -0.845 | -1.471 | -1.812 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Falling Short | 14.426 | 13.691 | 13.425 | 13.12 | 12.774 | 12.398 | 12.004 | 17.89 | 15.404 | 13.215 | 11.528 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Falling Short | 9.381 | 9.243 | 9.067 | 8.847 | 8.573 | 8.264 | 7.944 | 6.396 | 5.041 | 4.014 | 3.362 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Falling Short | 15.324 | 15.279 | 15.224 | 15.156 | 15.073 | 14.979 | 14.879 | 14.357 | 13.822 | 13.368 | 13.034 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 24.411 | 22.706 | 22.527 | 22.307 | 22.03 | 21.717 | 21.413 | 20.293 | 19.705 | 19.363 | 19.192 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Falling Short | 5.147 | 4.631 | 4.324 | 3.976 | 3.576 | 3.141 | 2.706 | 0.747 | -0.864 | -2.245 | -3.403 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Falling Short | 1.532 | 0.94 | 0.659 | 0.332 | -0.072 | -0.521 | -0.959 | -2.8 | -4.043 | -4.949 | -5.643 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Falling Short | 3.101 | 3.06 | 1.69 | 1.614 | 1.522 | 1.416 | 1.308 | 0.836 | 0.446 | 0.134 | -0.084 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Falling Short | 7.524 | 7.144 | 8.968 | 8.751 | 8.465 | 8.133 | 7.806 | 6.382 | 5.427 | 4.846 | 4.561 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Falling Short | 5.612 | 5.611 | 5.579 | 5.515 | 5.415 | 5.294 | 5.17 | 4.612 | 4.177 | 3.851 | 3.628 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Falling Short | 32.102 | 30.714 | 30.64 | 30.549 | 30.44 | 30.315 | 30.18 | 29.605 | 29.195 | 28.891 | 28.748 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Falling Short | 12.217 | 12.132 | 12.015 | 11.863 | 11.666 | 11.443 | 11.226 | 10.349 | 9.873 | 9.587 | 9.421 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Falling Short | 8.839 | 8.181 | 7.993 | 7.793 | 7.548 | 7.275 | 7.008 | 6.093 | 5.711 | 5.482 | 5.339 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Falling Short | 6.402 | 6.44 | 6.464 | 6.474 | 6.468 | 6.451 | 6.427 | 6.252 | 6 | 5.757 | 5.576 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Falling Short | 13.458 | 13.43 | 13.379 | 13.296 | 13.183 | 13.05 | 12.918 | 12.316 | 11.855 | 11.57 | 11.425 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 14.455 | 14.35 | 14.213 | 14.03 | 13.795 | 13.505 | 13.165 | 10.909 | 7.989 | 5.709 | 4.523 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 12.811 | 12.636 | 12.443 | 12.227 | 11.988 | 11.737 | 11.482 | 10.215 | 9 | 7.829 | 6.693 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Falling Short | 4.439 | 3.363 | 3.046 | 2.693 | 2.298 | 1.877 | 1.449 | -0.588 | -2.572 | -4.377 | -5.947 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Falling Short | 4.866 | 3.534 | 2.829 | 2.001 | 1.019 | -0.059 | -1.107 | -5.535 | -9.042 | -11.967 | -14.361 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Falling Short | 11.694 | 11.004 | 10.784 | 10.549 | 10.251 | 9.914 | 9.592 | 8.256 | 7.357 | 6.763 | 6.354 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Falling Short | 15.859 | 15.18 | 15 | 14.766 | 14.458 | 14.104 | 13.758 | 12.382 | 11.569 | 11.07 | 10.807 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Falling Short | 8.125 | 8.045 | 7.916 | 7.734 | 7.489 | 7.204 | 6.927 | 5.786 | 5.12 | 4.726 | 4.525 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Falling Short | 12.674 | 12.665 | 12.653 | 12.637 | 12.617 | 12.593 | 12.567 | 12.405 | 12.2 | 11.979 | 11.754 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Falling Short | 21.638 | 21.578 | 21.499 | 21.4 | 21.28 | 21.146 | 21.013 | 20.399 | 19.834 | 19.326 | 18.894 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Falling Short | 14.886 | 14.961 | 15.025 | 15.076 | 15.114 | 15.144 | 15.169 | 15.225 | 15.195 | 15.157 | 15.125 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 10.801 | 10.599 | 10.346 | 10.045 | 9.675 | 9.262 | 8.859 | 7.131 | 5.908 | 5.017 | 4.386 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 21.849 | 21.816 | 21.774 | 21.725 | 21.665 | 21.597 | 21.529 | 21.214 | 20.941 | 20.687 | 20.45 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Falling Short | 2.618 | 2.517 | 2.364 | 2.158 | 1.886 | 1.575 | 1.27 | 0.068 | -0.577 | -0.994 | -1.262 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Falling Short | 6.6 | 6.595 | 6.587 | 6.576 | 6.561 | 6.544 | 6.527 | 6.453 | 6.405 | 6.377 | 6.361 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Falling Short | 6.06 | 5.388 | 5.281 | 5.149 | 4.976 | 4.775 | 4.575 | 3.767 | 3.284 | 2.951 | 2.755 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Falling Short | 12.149 | 11.813 | 11.377 | 10.833 | 10.15 | 9.373 | 8.591 | 4.989 | 2.089 | 0.075 | -0.992 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Falling Short | 10.504 | 9.141 | 8.492 | 8.229 | 7.879 | 7.472 | 7.06 | 5.246 | 3.881 | 2.99 | 2.604 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Falling Short | 15.095 | 14.923 | 14.731 | 14.515 | 14.266 | 13.992 | 13.712 | 12.301 | 10.942 | 9.815 | 8.966 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Falling Short | 15.827 | 15.709 | 15.586 | 15.457 | 15.321 | 15.18 | 15.036 | 14.352 | 13.683 | 13.019 | 12.379 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Falling Short | 1.99 | 1.663 | 22.851 | 22.7 | 22.501 | 22.261 | 21.994 | 20.409 | 18.547 | 17.105 | 16.316 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Falling Short | 13.769 | 13.375 | 13.195 | 12.969 | 12.672 | 12.332 | 12.007 | 10.684 | 9.909 | 9.485 | 9.289 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Falling Short | 3.292 | 3.163 | 3.009 | 2.833 | 2.623 | 2.393 | 2.172 | 1.243 | 0.63 | 0.164 | -0.217 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Falling Short | 2.817 | 2.704 | 2.573 | 2.425 | 2.248 | 2.051 | 1.853 | 0.903 | 0.073 | -0.57 | -1.018 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 12.416 | 11.915 | 11.751 | 11.518 | 11.206 | 10.845 | 10.495 | 8.989 | 7.936 | 7.29 | 6.924 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Falling Short | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Falling Short | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Falling Short | 17.614 | 17.138 | 17.03 | 16.892 | 16.714 | 16.512 | 16.313 | 15.492 | 14.954 | 14.564 | 14.283 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Falling Short | 11.071 | 9.956 | 9.813 | 9.647 | 9.451 | 9.232 | 9.002 | 7.91 | 6.864 | 5.978 | 5.318 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Falling Short | 10.513 | 10.423 | 10.297 | 10.141 | 9.936 | 9.697 | 9.455 | 8.366 | 7.548 | 7.002 | 6.74 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Falling Short | 13.027 | 12.85 | 12.641 | 12.405 | 12.116 | 11.791 | 11.47 | 10.005 | 8.875 | 8.068 | 7.528 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Falling Short | 10.431 | 9.647 | 9.487 | 9.291 | 9.053 | 8.788 | 8.523 | 7.361 | 6.479 | 5.775 | 5.243 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Falling Short | 10.338 | 10.288 | 10.205 | 10.09 | 9.933 | 9.744 | 9.548 | 8.649 | 7.913 | 7.401 | 7.165 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Falling Short | 16.741 | 15.964 | 15.969 | 15.95 | 15.907 | 15.846 | 15.781 | 15.425 | 15.063 | 14.799 | 14.654 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Falling Short | 15.78 | 15.605 | 15.378 | 15.102 | 14.75 | 14.341 | 13.918 | 11.827 | 9.903 | 8.505 | 7.747 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | 5.587 | 5.515 | 5.416 | 5.293 | 5.13 | 4.943 | 4.761 | 3.988 | 3.496 | 3.222 | 3.109 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Falling Short | 12.457 | 12.141 | 10.474 | 10.225 | 9.893 | 9.505 | 9.109 | 7.265 | 5.535 | 4.213 | 3.437 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Falling Short | 23.178 | 13.728 | 2.976 | 2.603 | 2.136 | 1.604 | 1.058 | -1.196 | -3.041 | -4.477 | -5.405 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Falling Short | 0.84 | 0.29 | -0.034 | -2.199 | -2.703 | -3.275 | -3.827 | -6.059 | -7.461 | -8.392 | -9.029 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Falling Short | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Falling Short | 3.204 | 3.065 | 2.908 | 2.731 | 2.528 | 2.307 | 2.077 | 0.87 | -0.366 | -1.428 | -2.246 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Falling Short | 12.004 | 11.242 | 11.036 | 10.785 | 10.478 | 10.137 | 9.796 | 8.16 | 6.478 | 5.038 | 3.96 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 5.8 | 4.206 | 4.183 | 4.115 | 4.001 | 3.854 | 3.7 | 2.971 | 2.297 | 1.843 | 1.639 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 27.934 | 27.946 | 27.956 | 27.966 | 27.975 | 27.983 | 27.99 | 28.017 | 28.03 | 28.035 | 28.037 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Falling Short | 20.024 | 19.083 | 18.889 | 18.651 | 18.359 | 18.034 | 17.717 | 16.438 | 15.647 | 15.082 | 14.662 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Falling Short | 8.139 | 7.439 | 7.513 | 7.535 | 7.497 | 7.397 | 7.24 | 5.924 | 4.001 | 2.608 | 2.192 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Falling Short | 2.952 | 2.727 | 2.567 | 2.401 | 2.229 | 2.052 | 1.871 | 0.993 | 0.09 | -0.872 | -1.861 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Falling Short | 13.94 | 13.786 | 13.59 | 13.36 | 13.072 | 12.749 | 12.435 | 11.202 | 10.594 | 10.227 | 9.993 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Falling Short | 2.324 | 2.079 | 1.789 | 1.449 | 1.04 | 0.586 | 0.129 | -2.051 | -3.929 | -5.353 | -6.33 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Falling Short | 7.826 | 6.981 | 6.791 | 6.559 | 6.267 | 5.942 | 5.627 | 4.325 | 3.451 | 2.868 | 2.484 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 23.572 | 23.13 | 22.848 | 22.502 | 22.079 | 21.606 | 21.138 | 19.094 | 17.619 | 16.567 | 15.865 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Falling Short | 11.311 | 11.223 | 11.074 | 10.866 | 10.582 | 10.25 | 9.922 | 8.554 | 7.567 | 6.909 | 6.559 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Falling Short | 11.224 | 11.048 | 10.825 | 10.557 | 10.224 | 9.852 | 9.491 | 7.936 | 6.84 | 6.074 | 5.529 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Falling Short | 12.712 | 12.475 | 12.54 | 12.59 | 12.623 | 12.646 | 12.663 | 12.687 | 12.639 | 12.581 | 12.532 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Falling Short | 6.008 | 5.655 | 5.257 | 4.819 | 4.308 | 3.75 | 3.202 | 0.805 | -0.943 | -2.332 | -3.467 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Falling Short | 8.487 | 6.903 | 6.854 | 6.773 | 6.648 | 6.491 | 6.325 | 5.557 | 4.945 | 4.546 | 4.403 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Falling Short | 7.81 | 7.143 | 6.923 | 6.654 | 6.327 | 5.963 | 5.603 | 4.135 | 3.28 | 2.686 | 2.273 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Falling Short | 31.089 | 31.093 | 31.097 | 31.101 | 31.104 | 31.106 | 31.108 | 31.116 | 31.12 | 31.12 | 31.12 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Falling Short | 10.249 | 10.252 | 10.241 | 10.216 | 25.574 | 25.523 | 25.471 | 25.256 | 25.102 | 24.977 | 24.882 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Falling Short | 7.652 | 6.067 | 20.831 | 20.545 | 20.174 | 19.753 | 19.341 | 17.755 | 16.811 | 16.253 | 15.97 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Falling Short | 8.95 | 8.746 | 8.509 | 8.231 | 7.904 | 7.541 | 7.174 | 5.333 | 3.56 | 2.146 | 1.119 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Falling Short | 11.706 | 11.633 | 11.539 | 11.427 | 11.288 | 11.132 | 10.983 | 10.421 | 10.183 | 10.062 | 9.995 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Falling Short | 19.882 | 19.357 | 19.309 | 19.24 | 19.142 | 19.026 | 18.909 | 18.447 | 18.216 | 18.069 | 17.986 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Falling Short | 10.745 | 10.54 | 10.278 | 9.977 | 9.581 | 9.123 | 8.671 | 6.683 | 5.266 | 4.391 | 3.995 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Falling Short | 11.953 | 11.635 | 11.464 | 11.25 | 10.991 | 10.703 | 10.419 | 9.305 | 8.749 | 8.378 | 8.136 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Falling Short | 10.97 | 10.49 | 10.305 | 10.07 | 9.766 | 9.42 | 9.086 | 7.775 | 7.102 | 6.732 | 6.529 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 13.894 | 13.897 | 13.893 | 13.88 | 13.857 | 13.827 | 13.796 | 13.635 | 13.478 | 13.37 | 13.316 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 14.081 | 14.084 | 14.078 | 14.06 | 14.029 | 13.99 | 13.946 | 13.674 | 13.338 | 13.103 | 13.006 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 18.696 | 18.657 | 18.598 | 18.519 | 18.412 | 18.287 | 18.167 | 17.644 | 17.26 | 17.023 | 16.898 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 18.901 | 18.868 | 18.817 | 18.746 | 18.652 | 18.544 | 18.44 | 17.984 | 17.632 | 17.408 | 17.272 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Falling Short | 12.151 | 11.972 | 11.754 | 11.497 | 11.188 | 10.847 | 10.515 | 9.209 | 8.477 | 7.956 | 7.544 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 22.245 | 22.069 | 21.856 | 21.62 | 21.319 | 20.976 | 20.642 | 19.167 | 18.077 | 17.329 | 16.84 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Falling Short | 26.878 | 25.87 | 25.704 | 25.53 | 25.345 | 25.149 | 24.943 | 24.137 | 23.463 | 22.812 | 22.23 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Falling Short | 5.584 | 5.174 | 5.158 | 5.135 | 5.106 | 5.072 | 5.039 | 4.901 | 4.797 | 4.723 | 4.669 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Falling Short | 11.079 | 11.087 | 11.081 | 11.059 | 11.019 | 10.969 | 10.916 | 10.688 | 10.531 | 10.403 | 10.313 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Leading the Way | 5.382 | 4.87 | 4.081 | 3.204 | 2.701 | 2.397 | 1.777 | -4.906 | -9.838 | -13.068 | -12.374 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Leading the Way | 10.834 | 9.594 | 7.069 | 5.616 | 4.605 | 3.833 | 2.686 | -9.89 | -18.476 | -24.439 | -23.358 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 7.951 | 7.48 | 8.764 | 7.967 | 7.455 | 7.055 | 6.368 | -0.156 | -4.883 | -8.065 | -7.757 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Leading the Way | 5.704 | 5.339 | 4.723 | 4.011 | 3.586 | 3.284 | 2.667 | -3.908 | -8.829 | -12.245 | -11.666 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Leading the Way | 22.754 | 22.794 | 22.832 | 22.867 | 22.901 | 22.932 | 22.962 | 23.01 | 23.012 | 23.014 | 23.017 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Leading the Way | 2.038 | 1.954 | 1.784 | 1.583 | 1.485 | 1.423 | 1.258 | -1.029 | -2.758 | -3.915 | -3.616 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Leading the Way | 3.659 | 3.618 | 3.562 | 3.507 | 3.457 | 3.406 | 3.336 | 2.855 | 2.527 | 2.299 | 2.253 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Leading the Way | 2.608 | 2.373 | 2.041 | 1.668 | 1.377 | 1.122 | 0.753 | -2.93 | -5.88 | -8.039 | -8.344 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Leading the Way | 7.196 | 6.987 | 6.657 | 6.297 | 6.097 | 5.98 | 5.713 | 1.984 | -0.911 | -2.994 | -2.727 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Leading the Way | 11.86 | 11.491 | 10.911 | 10.303 | 9.87 | 9.497 | 8.877 | 4.044 | 0.827 | -0.987 | -0.46 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Leading the Way | 4.734 | 4.022 | 3.374 | 2.683 | 2.197 | 1.789 | 1.049 | -6.74 | -12.589 | -16.929 | -16.689 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Leading the Way | 11.006 | 10.36 | 9.905 | 9.379 | 9.074 | 8.854 | 8.345 | 2.443 | -1.972 | -5.084 | -4.572 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Leading the Way | 7.44 | 6.956 | 6.287 | 5.558 | 5.049 | 4.603 | 3.912 | -1.859 | -6.07 | -8.751 | -8.901 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Leading the Way | 3.513 | 2.751 | 2.174 | 1.527 | 1.141 | 0.834 | 0.215 | -5.852 | -10.313 | -13.327 | -12.955 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 13.287 | 13.065 | 12.692 | 12.249 | 11.879 | 11.493 | 10.302 | 4.197 | 1.431 | 0.016 | 0.206 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 16.5 | 16.401 | 16.265 | 16.115 | 15.983 | 15.86 | 15.713 | 14.423 | 13.566 | 13.285 | 13.605 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Leading the Way | 9.523 | 8.57 | 8.323 | 8.019 | 7.791 | 7.567 | 7.102 | 1.99 | -1.798 | -4.395 | -3.947 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Leading the Way | 10.16 | 9.45 | 8.946 | 8.387 | 7.972 | 7.611 | 6.948 | 0.457 | -4.364 | -7.83 | -7.462 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Leading the Way | 15.534 | 15.217 | 14.749 | 14.248 | 13.911 | 13.64 | 13.096 | 8.087 | 4.618 | 2.191 | 2.538 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Leading the Way | 7.094 | 6.909 | 6.62 | 6.25 | 5.895 | 5.496 | 4.92 | -0.109 | -3.678 | -5.542 | -5.552 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Leading the Way | 20.204 | 19.822 | 19.299 | 18.738 | 18.27 | 17.83 | 17.168 | 10.971 | 6.201 | 2.821 | 2.599 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 17.758 | 17.582 | 17.329 | 17.048 | 16.828 | 16.622 | 16.289 | 13.003 | 10.332 | 8.232 | 7.984 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Leading the Way | 11.736 | 10.82 | 9.876 | 8.839 | 8.167 | 7.646 | 6.745 | -1.676 | -7.759 | -11.865 | -11.404 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Leading the Way | 7.842 | 7.274 | 7.094 | 6.897 | 6.796 | 6.746 | 6.602 | 4.141 | 2.302 | 1.012 | 1.393 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Leading the Way | 8.698 | 8.161 | 7.31 | 6.346 | 5.726 | 5.28 | 4.497 | -3.536 | -9.364 | -12.938 | -12.36 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Leading the Way | 6.892 | 6.147 | 5.404 | 4.68 | 4.145 | 3.722 | 3.091 | -2.477 | -6.203 | -8.599 | -8.094 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Leading the Way | 8.036 | 7.632 | 7.045 | 6.417 | 5.999 | 5.688 | 5.112 | -0.792 | -5.006 | -7.75 | -7.152 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Leading the Way | 8.036 | 7.761 | 7.322 | 6.82 | 6.436 | 6.098 | 5.511 | -0.266 | -4.526 | -7.628 | -7.323 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Leading the Way | 3.996 | 3.632 | 3.02 | 2.299 | 1.84 | 1.466 | 0.721 | -6.757 | -12.247 | -15.992 | -15.419 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Leading the Way | 7.772 | 7.335 | 6.732 | 6.074 | 5.566 | 5.124 | 4.47 | -1.644 | -6.44 | -10.111 | -10.49 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Leading the Way | 8.421 | 8.222 | 8.281 | 8.311 | 8.386 | 8.469 | 8.465 | 6.454 | 4.928 | 3.867 | 4.565 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Leading the Way | 5.553 | 4.558 | 4.186 | 3.809 | 3.523 | 3.266 | 2.826 | -1.169 | -3.922 | -5.872 | -5.702 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Leading the Way | 14.555 | 13.007 | 11.967 | 10.832 | 10.064 | 9.45 | 8.461 | -0.88 | -7.605 | -11.9 | -11.337 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Leading the Way | 12.828 | 12.777 | 12.661 | 12.525 | 12.464 | 12.435 | 12.332 | 10.607 | 9.361 | 8.518 | 8.833 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Leading the Way | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | 7.498 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 12.63 | 12.592 | 12.493 | 12.364 | 12.298 | 12.255 | 12.119 | 9.926 | 8.3 | 7.218 | 7.567 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 14.65 | 14.537 | 14.345 | 14.108 | 13.96 | 13.842 | 13.598 | 10.595 | 8.394 | 7.056 | 7.332 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Leading the Way | 4.478 | 4.406 | 4.3 | 4.19 | 4.142 | 4.128 | 4.066 | 2.896 | 1.932 | 1.209 | 1.286 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Leading the Way | 8.944 | 8.749 | 8.461 | 8.155 | 7.974 | 7.838 | 7.575 | 4.895 | 2.934 | 1.628 | 1.865 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Leading the Way | 8.32 | 8.041 | 7.586 | 7.084 | 6.757 | 6.488 | 5.952 | -0.08 | -4.518 | -7.603 | -6.95 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 23.137 | 22.85 | 22.797 | 22.732 | 22.701 | 22.679 | 22.567 | 21.085 | 20.003 | 19.254 | 19.587 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Leading the Way | 6.789 | 6.638 | 6.352 | 6.021 | 5.792 | 5.575 | 5.151 | 0.488 | -2.861 | -4.857 | -4.243 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Leading the Way | 5.042 | 4.099 | 3.258 | 2.302 | 1.623 | 1.044 | 0.123 | -7.874 | -13.361 | -16.548 | -15.894 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Leading the Way | 9.902 | 8.519 | 7.924 | 7.258 | 6.818 | 6.458 | 5.789 | -2.104 | -7.841 | -11.839 | -11.054 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 8.631 | 8.463 | 8.171 | 7.862 | 7.607 | 7.355 | 6.892 | 2.731 | -0.059 | -1.923 | -1.539 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 13.363 | 13.018 | 12.477 | 11.903 | 11.515 | 11.191 | 10.513 | 3.625 | -1.468 | -5.121 | -4.562 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Leading the Way | 4.237 | 3.728 | 3.542 | 3.344 | 3.218 | 3.129 | 2.967 | 0.114 | -2.097 | -3.836 | -3.658 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Leading the Way | 8.025 | 7.572 | 6.842 | 6.001 | 5.388 | 4.859 | 3.875 | -6.591 | -14.39 | -19.827 | -19.057 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Leading the Way | 18.017 | 17.993 | 17.936 | 17.864 | 17.831 | 17.811 | 17.728 | 16.369 | 15.288 | 14.462 | 14.602 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Leading the Way | 6.577 | 6.333 | 5.94 | 5.533 | 5.275 | 5.088 | 4.721 | 0.908 | -1.708 | -3.364 | -2.939 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Leading the Way | 8.988 | 8.962 | 8.897 | 8.816 | 8.744 | 8.67 | 8.541 | 7.177 | 6.196 | 5.586 | 5.624 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Leading the Way | 0.464 | 0.171 | -0.334 | -0.933 | -1.277 | -1.495 | -1.992 | 9.047 | 4.524 | 1.361 | 2.065 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Leading the Way | 5.341 | 4.543 | 3.468 | 2.515 | 1.772 | 1.085 | 0.032 | -7.888 | -13.294 | -16.644 | -16.132 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Leading the Way | 10.06 | 9.437 | 7.803 | 6.823 | 6.182 | 5.714 | 4.951 | -2.81 | -8.549 | -12.38 | -12.039 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Leading the Way | 14.363 | 14.018 | 13.93 | 13.809 | 13.699 | 13.578 | 13.374 | 11.353 | 9.898 | 8.971 | 9.031 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Leading the Way | 7.269 | 5.702 | 5.14 | 4.503 | 4.112 | 3.825 | 3.205 | -5.756 | -12.391 | -17.084 | -15.962 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Leading the Way | 7.235 | 6.694 | 5.865 | 4.951 | 4.329 | 3.827 | 2.954 | -5.078 | -10.803 | -14.622 | -14.2 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Leading the Way | 28.899 | 28.302 | 27.447 | 26.643 | 26.055 | 25.546 | 24.746 | 18.208 | 13.96 | 11.406 | 11.897 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Leading the Way | 5.122 | 4.773 | 4.233 | 3.623 | 3.232 | 2.943 | 2.41 | -3.125 | -7.299 | -10.203 | -9.945 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Leading the Way | 11.665 | 11.359 | 10.898 | 10.406 | 10.133 | 9.968 | 9.627 | 6.095 | 3.544 | 1.83 | 2.164 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Leading the Way | 18.263 | 18.11 | 17.839 | 17.52 | 17.308 | 17.133 | 16.764 | 12.414 | 9.122 | 6.815 | 7.225 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Leading the Way | 8.616 | 8.577 | 7.019 | 6.843 | 6.752 | 6.688 | 6.509 | 3.955 | 2.199 | 1.133 | 1.527 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Leading the Way | 25.852 | 25.887 | 25.887 | 25.848 | 25.779 | 25.668 | 25.5 | 23.778 | 22.593 | 22.081 | 22.266 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Leading the Way | 14.539 | 14.022 | 13.932 | 13.821 | 13.82 | 13.88 | 13.856 | 12.482 | 11.459 | 10.797 | 11.208 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Leading the Way | 4.849 | 4.588 | 4.117 | 3.521 | 2.859 | 2.075 | 1.035 | -5.145 | -8.858 | -10.212 | -10.237 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Leading the Way | 15.811 | 15.933 | 16.036 | 16.126 | 16.219 | 16.314 | 16.394 | 16.218 | 16.022 | 15.854 | 16.111 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 7.47 | 6.853 | 6.237 | 5.579 | 5.091 | 4.67 | 4.013 | 14.259 | 10.192 | 7.473 | 7.821 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Leading the Way | 2.429 | 2.2 | 1.809 | 1.361 | 1.175 | 1.11 | 0.839 | -3.152 | -6.204 | -8.263 | -7.687 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Leading the Way | 14.297 | 13.919 | 13.361 | 12.771 | 12.322 | 11.911 | 11.309 | 6.126 | 2.573 | 0.324 | 0.487 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Leading the Way | 14.991 | 12.57 | 12.524 | 12.435 | 12.4 | 12.362 | 12.159 | 9.587 | 7.895 | 6.818 | 7.295 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Leading the Way | 8.646 | 7.759 | 6.926 | 6.088 | 5.53 | 5.09 | 4.324 | -3.899 | -10.073 | -14.412 | -13.978 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Leading the Way | 18.444 | 18.307 | 18.101 | 17.901 | 17.78 | 17.701 | 17.548 | 15.473 | 13.85 | 12.667 | 12.816 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Leading the Way | 10.919 | 10.179 | 9.106 | 7.966 | 7.241 | 6.73 | 5.867 | -2.675 | -8.79 | -12.828 | -12.324 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Leading the Way | 3.501 | 2.549 | 1.662 | 0.682 | -0.04 | -0.669 | -1.644 | -9.925 | -15.491 | -19.063 | -18.477 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Leading the Way | 2.628 | 2.102 | 1.391 | 0.707 | 0.243 | -0.092 | -0.632 | -5.422 | -8.663 | -10.754 | -10.398 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Leading the Way | 8.501 | 8.441 | 8.342 | 8.224 | 8.132 | 8.048 | 7.916 | 6.633 | 5.721 | 5.266 | 5.348 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Leading the Way | 21.015 | 20.717 | 20.668 | 20.609 | 20.578 | 20.563 | 20.529 | 19.57 | 18.845 | 18.297 | 18.453 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Leading the Way | 19.146 | 18.863 | 18.436 | 17.972 | 17.693 | 17.523 | 17.185 | 13.333 | 10.449 | 8.572 | 8.969 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Leading the Way | 14.59 | 14.735 | 14.872 | 15.001 | 15.125 | 15.243 | 15.354 | 15.76 | 16.088 | 16.365 | 16.676 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Leading the Way | 14.652 | 14.714 | 14.708 | 14.685 | 14.712 | 14.753 | 14.717 | 13.367 | 12.463 | 11.995 | 12.556 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Leading the Way | 1.111 | 1.046 | 0.838 | 0.512 | 20.151 | 19.85 | 19.264 | 12.943 | 8.306 | 5.638 | 6.1 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Leading the Way | 7.535 | 7.107 | 6.477 | 5.803 | 5.365 | 5.019 | 4.437 | -1.107 | -5.146 | -7.95 | -7.699 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Leading the Way | 6.849 | 6.374 | 5.674 | 4.927 | 4.402 | 3.957 | 3.277 | -2.556 | -6.532 | -8.893 | -8.338 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Leading the Way | 16.224 | 16.122 | 15.962 | 15.784 | 15.62 | 15.452 | 15.172 | 12.582 | 10.623 | 9.19 | 9.191 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Leading the Way | 6.698 | 6.53 | 6.263 | 5.985 | 5.793 | 5.636 | 5.366 | 2.237 | -0.018 | -1.579 | -1.213 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 1.698 | 1.13 | 0.35 | -0.43 | -1.055 | -1.633 | -2.465 | -9.54 | -14.646 | -18.21 | -18.305 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Leading the Way | 18.423 | 18.394 | 18.327 | 18.245 | 18.196 | 18.157 | 18.063 | 16.965 | 16.158 | 15.634 | 15.768 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Leading the Way | 6.537 | 6.184 | 5.655 | 5.11 | 4.768 | 4.518 | 4.054 | -0.189 | -3.092 | -4.989 | -4.564 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Leading the Way | 2.77 | 2.747 | 2.712 | 2.678 | 2.652 | 2.628 | 2.591 | 2.183 | 1.907 | 1.728 | 1.769 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Leading the Way | 9.14 | 8.766 | 8.57 | 8.339 | 8.193 | 8.076 | 7.826 | 4.883 | 2.612 | 1.044 | 1.216 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Leading the Way | 14.269 | 14.045 | 13.705 | 13.344 | 13.087 | 12.871 | 12.524 | 9.18 | 6.817 | 5.212 | 5.416 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Leading the Way | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Leading the Way | 20.785 | 20.574 | 20.264 | 19.949 | 19.738 | 19.575 | 19.284 | 16.049 | 13.63 | 11.947 | 12.188 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Leading the Way | 8.274 | 7.875 | 7.278 | 6.651 | 6.315 | 6.121 | 5.688 | 0.854 | -2.686 | -5.005 | -4.493 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Leading the Way | 14.225 | 13.91 | 13.439 | 12.925 | 12.615 | 12.389 | 11.981 | 7.819 | 4.765 | 2.782 | 3.073 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Leading the Way | 33.151 | 32.746 | 32.678 | 32.606 | 32.568 | 32.55 | 32.5 | 31.665 | 31.087 | 30.68 | 30.822 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Leading the Way | 4.286 | 3.316 | 2.409 | 1.441 | 0.795 | 0.331 | -0.427 | -7.178 | -11.902 | -14.869 | -14.329 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Leading the Way | 14.514 | 13.668 | 13.216 | 12.708 | 12.305 | 11.944 | 11.447 | 13.788 | 9.194 | 5.72 | 5.353 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Leading the Way | 9.505 | 9.34 | 9.067 | 8.762 | 8.499 | 8.244 | 7.778 | 2.173 | -2.175 | -5.404 | -5.051 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Leading the Way | 15.376 | 15.3 | 15.178 | 15.036 | 14.952 | 14.891 | 14.762 | 12.972 | 11.555 | 10.533 | 10.621 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 24.31 | 22.441 | 21.943 | 21.414 | 21.038 | 20.713 | 20.176 | 15.964 | 13.203 | 11.369 | 11.618 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Leading the Way | 5.245 | 4.672 | 4.194 | 3.659 | 3.264 | 2.912 | 2.327 | -3.405 | -7.944 | -11.441 | -11.612 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Leading the Way | 1.414 | 0.494 | -0.297 | -1.104 | -1.642 | -2.04 | -2.77 | -10.248 | -15.896 | -20.021 | -19.839 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Leading the Way | 3.133 | 3.085 | 1.689 | 1.587 | 1.5 | 1.414 | 1.29 | 0.545 | 0.106 | -0.134 | -0.138 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Leading the Way | 7.501 | 6.962 | 8.487 | 7.994 | 7.654 | 7.356 | 6.782 | 0.317 | -4.434 | -7.788 | -7.165 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Leading the Way | 5.589 | 5.326 | 4.873 | 4.336 | 4.13 | 4.072 | 3.728 | -2.165 | -6.728 | -9.958 | -9.213 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Leading the Way | 32.12 | 30.728 | 30.619 | 30.488 | 30.375 | 30.261 | 30.008 | 27.43 | 25.584 | 24.193 | 24.302 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Leading the Way | 12.221 | 12.06 | 11.778 | 11.449 | 11.224 | 11.029 | 10.605 | 5.941 | 2.401 | -0.195 | 0.234 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Leading the Way | 8.802 | 8.011 | 7.587 | 7.202 | 6.938 | 6.717 | 6.332 | 3.031 | 0.931 | -0.489 | -0.126 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Leading the Way | 6.515 | 6.556 | 6.542 | 6.501 | 6.533 | 6.592 | 6.579 | 5.405 | 4.52 | 3.954 | 4.341 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Leading the Way | 13.497 | 13.427 | 13.283 | 13.101 | 12.967 | 12.845 | 12.586 | 9.017 | 6.315 | 4.339 | 4.759 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 14.658 | 14.591 | 14.442 | 14.216 | 13.945 | 13.599 | 13.127 | 8.779 | 5.665 | 3.944 | 3.857 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 12.98 | 12.783 | 12.489 | 12.147 | 11.961 | 11.834 | 11.577 | 7.754 | 4.585 | 2.056 | 1.961 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Leading the Way | 4.588 | 3.437 | 2.952 | 2.418 | 2.032 | 1.704 | 1.234 | -3.708 | -7.541 | -10.474 | -10.73 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Leading the Way | 4.695 | 2.712 | 1.016 | -0.785 | -2.092 | -3.114 | -4.585 | -15.624 | -23.306 | -28.276 | -28.159 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Leading the Way | 11.51 | 10.508 | 9.827 | 9.219 | 8.788 | 8.453 | 7.937 | 3.429 | 0.231 | -1.895 | -1.695 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Leading the Way | 15.775 | 14.864 | 14.281 | 13.625 | 13.205 | 12.869 | 12.212 | 6.006 | 1.606 | -1.339 | -0.748 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Leading the Way | 8.113 | 7.887 | 7.485 | 7.013 | 6.697 | 6.436 | 5.9 | 0.547 | -3.27 | -5.832 | -5.217 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Leading the Way | 12.772 | 12.811 | 12.844 | 12.873 | 12.899 | 12.921 | 12.939 | 12.874 | 12.808 | 12.74 | 12.771 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Leading the Way | 21.689 | 21.568 | 21.373 | 21.147 | 21.012 | 20.914 | 20.728 | 18.877 | 17.493 | 16.565 | 16.708 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Leading the Way | 15.073 | 15.214 | 15.33 | 15.432 | 15.543 | 15.654 | 15.732 | 15.079 | 14.563 | 14.191 | 14.689 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 10.67 | 10.162 | 9.438 | 8.668 | 8.15 | 7.747 | 7.094 | 0.927 | -3.597 | -6.685 | -6.399 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 21.902 | 21.857 | 21.78 | 21.7 | 21.656 | 21.631 | 21.571 | 20.81 | 20.247 | 19.846 | 19.904 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Leading the Way | 2.561 | 2.218 | 1.668 | 1.056 | 0.689 | 0.435 | -0.097 | -5.885 | -10.098 | -12.932 | -12.153 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Leading the Way | 6.6 | 6.582 | 6.551 | 6.516 | 6.497 | 6.482 | 6.45 | 6.019 | 5.704 | 5.487 | 5.545 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Leading the Way | 6.04 | 5.167 | 4.744 | 4.327 | 4.073 | 3.927 | 3.65 | 0.53 | -1.667 | -3.067 | -2.662 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Leading the Way | 11.962 | 11.2 | 10.092 | 8.862 | 7.919 | 7.089 | 5.699 | -7.193 | -16.619 | -23.077 | -22.597 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Leading the Way | 10.472 | 8.891 | 7.835 | 7.122 | 6.636 | 6.231 | 5.488 | -1.954 | -7.297 | -10.861 | -10.259 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Leading the Way | 15.158 | 14.969 | 14.708 | 14.419 | 14.166 | 13.91 | 13.532 | 10.149 | 7.496 | 5.533 | 5.299 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Leading the Way | 15.945 | 15.883 | 15.808 | 15.728 | 15.652 | 15.575 | 15.48 | 14.867 | 14.366 | 13.936 | 13.692 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Leading the Way | 2.041 | 1.555 | 22.476 | 22.039 | 21.733 | 21.48 | 21.048 | 16.277 | 12.737 | 10.549 | 10.693 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Leading the Way | 13.662 | 13.069 | 12.568 | 12.051 | 11.647 | 11.286 | 10.775 | 7.419 | 5.375 | 4.29 | 4.568 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Leading the Way | 3.261 | 3.035 | 2.712 | 2.368 | 2.126 | 1.916 | 1.597 | -0.781 | -2.46 | -3.576 | -3.545 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Leading the Way | 2.819 | 2.661 | 2.44 | 2.208 | 2.009 | 1.813 | 1.537 | -0.623 | -2.18 | -3.242 | -3.339 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 12.373 | 11.626 | 11.051 | 10.404 | 9.956 | 9.594 | 8.914 | 1.188 | -4.448 | -8.43 | -7.766 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Leading the Way | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Leading the Way | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Leading the Way | 17.632 | 17.056 | 16.751 | 16.408 | 16.204 | 16.051 | 15.719 | 11.951 | 9.172 | 7.21 | 7.609 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Leading the Way | 11.191 | 10.107 | 9.959 | 9.783 | 9.615 | 9.433 | 9.158 | 6.949 | 5.432 | 4.371 | 4.264 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Leading the Way | 10.433 | 10.114 | 9.632 | 9.126 | 8.81 | 8.581 | 8.165 | 3.87 | 0.782 | -1.184 | -0.818 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Leading the Way | 12.964 | 12.634 | 12.18 | 11.732 | 11.382 | 11.066 | 10.592 | 6.528 | 3.642 | 1.663 | 1.68 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Leading the Way | 10.497 | 9.664 | 9.37 | 9.019 | 8.772 | 8.556 | 8.158 | 4.166 | 1.164 | -1.029 | -0.869 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Leading the Way | 10.302 | 10.064 | 9.676 | 9.232 | 8.979 | 8.807 | 8.419 | 4.14 | 1.009 | -1.079 | -0.745 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Leading the Way | 16.826 | 16.006 | 15.914 | 15.794 | 15.747 | 15.737 | 15.614 | 12.979 | 11.06 | 9.708 | 10.186 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Leading the Way | 15.728 | 15.303 | 14.661 | 13.96 | 13.474 | 13.051 | 12.353 | 5.916 | 1.361 | -1.448 | -1.143 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | 5.547 | 5.391 | 5.147 | 4.891 | 4.683 | 4.484 | 4.178 | 1.894 | 0.392 | -0.541 | -0.412 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Leading the Way | 12.428 | 11.779 | 9.581 | 8.732 | 8.212 | 7.82 | 7.111 | -0.374 | -5.554 | -8.752 | -7.826 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Leading the Way | 23.191 | 13.52 | 2.201 | 1.289 | 0.662 | 0.165 | -0.647 | -7.869 | -12.57 | -15.671 | -15.367 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Leading the Way | 0.644 | -0.296 | -1.224 | -3.921 | -4.585 | -5.116 | -6.014 | -13.661 | -18.973 | -22.56 | -22.222 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Leading the Way | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Leading the Way | 3.257 | 3.058 | 2.783 | 2.471 | 2.253 | 2.064 | 1.752 | -1.789 | -4.563 | -6.587 | -6.643 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Leading the Way | 12.022 | 11.023 | 10.447 | 9.813 | 9.384 | 9.048 | 8.527 | 3.48 | -0.141 | -2.464 | -2.063 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 5.855 | 4.11 | 3.801 | 3.42 | 3.234 | 3.125 | 2.814 | -1.721 | -4.842 | -6.924 | -6.291 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 27.96 | 27.983 | 28.006 | 28.028 | 28.048 | 28.068 | 28.087 | 28.168 | 28.232 | 28.286 | 28.335 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Leading the Way | 19.969 | 18.838 | 18.31 | 17.723 | 17.344 | 17.049 | 16.534 | 11.773 | 8.361 | 6.007 | 6.24 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Leading the Way | 8.415 | 7.8 | 7.908 | 7.93 | 7.903 | 7.793 | 7.54 | 4.454 | 2.554 | 1.885 | 2.572 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Leading the Way | 3.183 | 3.097 | 3.077 | 3.051 | 3.021 | 2.986 | 2.947 | 2.633 | 2.279 | 1.893 | 1.582 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Leading the Way | 13.776 | 13.312 | 12.627 | 11.901 | 11.469 | 11.175 | 10.548 | 3.969 | -1.047 | -4.62 | -4.235 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Leading the Way | 2.326 | 1.963 | 1.446 | 0.889 | 0.412 | -0.051 | -0.722 | -6.359 | -10.493 | -13.396 | -13.581 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Leading the Way | 7.781 | 6.77 | 6.316 | 5.851 | 5.475 | 5.156 | 4.727 | 1.468 | -0.61 | -1.905 | -1.754 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 23.523 | 22.868 | 22.207 | 21.467 | 20.936 | 20.479 | 19.682 | 11.828 | 6.067 | 2.019 | 2.406 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Leading the Way | 11.164 | 10.682 | 9.939 | 9.114 | 8.626 | 8.298 | 7.658 | 1.164 | -3.459 | -6.42 | -5.768 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Leading the Way | 11.112 | 10.661 | 9.999 | 9.289 | 8.819 | 8.448 | 7.78 | 1.034 | -3.988 | -7.553 | -7.313 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Leading the Way | 12.9 | 12.704 | 12.781 | 12.836 | 12.936 | 13.053 | 13.113 | 12.263 | 11.626 | 11.21 | 11.745 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Leading the Way | 5.98 | 5.463 | 4.753 | 4.027 | 3.479 | 2.986 | 2.196 | -5.125 | -10.817 | -15.15 | -15.303 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Leading the Way | 8.559 | 6.955 | 6.81 | 6.619 | 6.489 | 6.361 | 6.057 | 2.988 | 0.867 | -0.503 | -0.11 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Leading the Way | 7.802 | 7.013 | 6.54 | 6.004 | 5.628 | 5.308 | 4.717 | -1.14 | -5.502 | -8.71 | -8.459 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Leading the Way | 31.099 | 31.106 | 31.111 | 31.116 | 31.123 | 31.131 | 31.136 | 31.136 | 31.137 | 31.142 | 31.166 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Leading the Way | 10.282 | 10.228 | 10.108 | 9.964 | 25.305 | 25.29 | 25.182 | 23.365 | 21.916 | 20.883 | 21.164 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Leading the Way | 7.591 | 5.802 | 20.179 | 19.527 | 19.055 | 18.635 | 17.885 | 10.573 | 5.572 | 2.007 | 2.503 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Leading the Way | 8.969 | 8.662 | 8.248 | 7.801 | 7.409 | 7.033 | 6.507 | 1.829 | -1.735 | -4.36 | -4.725 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Leading the Way | 11.67 | 11.54 | 11.345 | 11.146 | 10.986 | 10.84 | 10.6 | 8.891 | 7.693 | 6.883 | 7.01 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Leading the Way | 19.93 | 19.373 | 19.222 | 19.036 | 18.943 | 18.876 | 18.636 | 15.533 | 13.179 | 11.456 | 11.876 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Leading the Way | 10.568 | 10.027 | 9.244 | 8.487 | 7.931 | 7.456 | 6.68 | -0.049 | -4.769 | -7.747 | -7.258 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Leading the Way | 11.904 | 11.429 | 10.985 | 10.485 | 10.161 | 9.916 | 9.421 | 4.025 | -0.061 | -3.073 | -2.7 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Leading the Way | 10.903 | 10.262 | 9.784 | 9.256 | 8.867 | 8.529 | 7.926 | 2.668 | -1.107 | -3.755 | -3.477 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 13.915 | 13.886 | 13.819 | 13.734 | 13.703 | 13.689 | 13.62 | 12.383 | 11.457 | 10.835 | 11.061 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 14.103 | 14.071 | 14.005 | 13.92 | 13.867 | 13.826 | 13.741 | 12.321 | 11.239 | 10.527 | 10.727 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 18.65 | 18.504 | 18.284 | 18.046 | 17.878 | 17.743 | 17.527 | 15.562 | 14.232 | 13.404 | 13.558 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 18.855 | 18.703 | 18.477 | 18.232 | 18.072 | 17.955 | 17.756 | 15.459 | 13.792 | 12.664 | 12.865 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Leading the Way | 12.127 | 11.851 | 11.436 | 10.976 | 10.635 | 10.332 | 9.74 | 4.114 | -0.2 | -3.564 | -3.507 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 22.091 | 21.611 | 20.952 | 20.33 | 19.906 | 19.573 | 19.034 | 14.23 | 10.838 | 8.649 | 8.874 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Leading the Way | 26.991 | 26.076 | 25.998 | 25.91 | 25.821 | 25.721 | 25.597 | 24.925 | 24.509 | 24.192 | 24.017 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Leading the Way | 5.587 | 5.157 | 5.104 | 5.049 | 5.012 | 4.984 | 4.931 | 4.27 | 3.804 | 3.463 | 3.528 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Leading the Way | 11.169 | 11.176 | 11.132 | 11.069 | 11.055 | 11.061 | 10.966 | 8.934 | 7.381 | 6.253 | 6.727 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - System Transformation | 5.409 | 5.224 | 4.937 | 4.617 | 4.264 | 3.884 | 3.432 | 1.211 | -2.045 | -6.628 | -13.743 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - System Transformation | 10.829 | 10.016 | 8.137 | 7.415 | 6.619 | 5.78 | 4.826 | 0.874 | -6.286 | -13.527 | -22.8 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 7.892 | 7.607 | 9.221 | 8.812 | 8.365 | 7.889 | 7.362 | 4.609 | 0.777 | -3.595 | -9.838 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - System Transformation | 5.665 | 5.468 | 5.166 | 4.833 | 4.467 | 4.082 | 3.664 | 1.515 | -2.157 | -6.548 | -13.189 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - System Transformation | 22.753 | 22.781 | 22.806 | 22.828 | 22.847 | 22.864 | 22.878 | 22.9 | 22.9 | 22.9 | 22.9 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - System Transformation | 1.952 | 1.909 | 1.833 | 1.744 | 1.635 | 1.506 | 1.349 | 0.396 | -1.323 | -3.267 | -5.881 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - System Transformation | 3.647 | 3.601 | 3.546 | 3.494 | 3.439 | 3.381 | 3.321 | 3.016 | 2.661 | 2.371 | 2.037 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - System Transformation | 2.497 | 2.305 | 2.068 | 1.806 | 1.513 | 1.19 | 0.813 | -1.284 | -4.433 | -7.605 | -11.357 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - System Transformation | 7.087 | 6.981 | 6.832 | 6.677 | 6.492 | 6.279 | 6.007 | 4.505 | 1.858 | -1.316 | -5.61 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - System Transformation | 11.802 | 11.54 | 11.179 | 10.827 | 10.435 | 10.012 | 9.539 | 7.128 | 4.345 | 1.526 | -2.42 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - System Transformation | 4.668 | 4.067 | 3.66 | 3.26 | 2.82 | 2.351 | 1.842 | -0.778 | -5.579 | -10.699 | -17.82 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - System Transformation | 10.954 | 10.435 | 10.225 | 9.996 | 9.734 | 9.444 | 9.126 | 7.217 | 3.968 | -0.027 | -6.101 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - System Transformation | 7.354 | 7.013 | 6.605 | 6.187 | 5.727 | 5.227 | 4.68 | 1.504 | -2.447 | -6.56 | -11.952 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - System Transformation | 3.415 | 2.758 | 2.428 | 2.093 | 1.724 | 1.328 | 0.901 | -1.532 | -5.335 | -9.611 | -15.847 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 13.228 | 13.071 | 12.849 | 12.598 | 12.29 | 11.927 | 10.914 | 6.768 | 4.097 | 1.884 | -0.719 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 16.456 | 16.451 | 16.426 | 16.389 | 16.334 | 16.231 | 16.011 | 14.725 | 14.409 | 13.487 | 12.429 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - System Transformation | 9.468 | 8.534 | 8.376 | 8.201 | 7.988 | 7.743 | 7.474 | 5.736 | 2.532 | -0.65 | -5.06 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - System Transformation | 10.123 | 9.486 | 9.147 | 8.791 | 8.403 | 7.991 | 7.57 | 5.214 | 1.887 | -2.202 | -8.369 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - System Transformation | 15.508 | 15.292 | 15.02 | 14.76 | 14.475 | 14.168 | 13.833 | 12.127 | 9.703 | 6.782 | 2.318 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - System Transformation | 7.088 | 6.997 | 6.862 | 6.687 | 6.451 | 6.147 | 5.761 | 2.971 | -0.784 | -3.437 | -6.093 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - System Transformation | 20.175 | 19.881 | 19.529 | 19.168 | 18.764 | 18.322 | 17.831 | 15.007 | 10.827 | 6.741 | 1.523 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 17.658 | 17.463 | 17.233 | 16.994 | 16.737 | 16.465 | 16.178 | 14.569 | 11.889 | 9.137 | 5.589 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - System Transformation | 11.699 | 11.04 | 10.536 | 10.012 | 9.45 | 8.854 | 8.191 | 4.751 | 0.31 | -5.168 | -13.245 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - System Transformation | 7.812 | 7.314 | 7.259 | 7.2 | 7.126 | 7.041 | 6.927 | 6.343 | 4.71 | 2.996 | 0.67 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - System Transformation | 8.721 | 8.519 | 8.194 | 7.818 | 7.382 | 6.894 | 6.306 | 3.151 | -1.442 | -6.518 | -13.65 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - System Transformation | 6.828 | 6.249 | 5.785 | 5.359 | 4.9 | 4.416 | 3.885 | 1.415 | -1.522 | -4.864 | -9.413 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - System Transformation | 8.005 | 7.808 | 7.537 | 7.266 | 6.962 | 6.62 | 6.19 | 3.832 | 0.643 | -3.151 | -8.671 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - System Transformation | 7.959 | 7.725 | 7.401 | 7.052 | 6.672 | 6.272 | 5.853 | 3.634 | 0.159 | -3.541 | -8.766 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - System Transformation | 3.958 | 3.746 | 3.43 | 3.082 | 2.691 | 2.268 | 1.802 | -0.787 | -4.974 | -9.683 | -16.689 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - System Transformation | 7.678 | 7.315 | 6.871 | 6.406 | 5.909 | 5.387 | 4.82 | 1.908 | -2.417 | -7.022 | -12.969 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - System Transformation | 8.296 | 8.079 | 8.153 | 8.207 | 8.235 | 8.24 | 8.211 | 7.828 | 6.006 | 4.295 | 2.146 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - System Transformation | 5.463 | 4.477 | 4.191 | 3.925 | 3.628 | 3.311 | 2.966 | 1.315 | -1.239 | -3.716 | -6.953 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - System Transformation | 14.486 | 13.251 | 12.734 | 12.194 | 11.595 | 10.924 | 10.093 | 5.737 | 0.52 | -5.619 | -14.04 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - System Transformation | 12.787 | 12.782 | 12.749 | 12.706 | 12.649 | 12.581 | 12.49 | 11.979 | 10.801 | 9.554 | 7.832 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - System Transformation | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 12.589 | 12.598 | 12.582 | 12.551 | 12.5 | 12.431 | 12.335 | 11.656 | 10.165 | 8.622 | 6.553 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 14.637 | 14.625 | 14.585 | 14.524 | 14.436 | 14.319 | 14.158 | 12.984 | 11.013 | 9.072 | 6.507 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - System Transformation | 4.473 | 4.452 | 4.426 | 4.404 | 4.377 | 4.346 | 4.302 | 4.048 | 3.262 | 2.321 | 0.955 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - System Transformation | 8.938 | 8.822 | 8.678 | 8.542 | 8.396 | 8.243 | 8.077 | 7.193 | 5.719 | 4.024 | 1.488 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - System Transformation | 8.256 | 8.061 | 7.793 | 7.521 | 7.217 | 6.892 | 6.541 | 4.597 | 0.964 | -2.92 | -8.466 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 23.088 | 22.789 | 22.747 | 22.705 | 22.652 | 22.593 | 22.53 | 22.124 | 21.185 | 20.107 | 18.484 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - System Transformation | 6.715 | 6.625 | 6.481 | 6.329 | 6.134 | 5.9 | 5.617 | 3.764 | 0.572 | -2.36 | -6.119 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - System Transformation | 5.021 | 4.323 | 3.9 | 3.428 | 2.892 | 2.302 | 1.626 | -1.901 | -6.633 | -11.192 | -17.173 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - System Transformation | 9.822 | 8.575 | 8.253 | 7.917 | 7.537 | 7.123 | 6.653 | 4.142 | -0.788 | -5.705 | -12.352 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 8.561 | 8.382 | 8.136 | 7.896 | 7.622 | 7.324 | 7.006 | 5.324 | 2.889 | 0.562 | -2.636 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 13.297 | 13.021 | 12.666 | 12.327 | 11.954 | 11.561 | 11.15 | 8.904 | 5.105 | 0.706 | -5.982 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - System Transformation | 4.14 | 3.657 | 3.539 | 3.414 | 3.267 | 3.103 | 2.904 | 1.917 | -0.409 | -2.745 | -5.538 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - System Transformation | 7.974 | 7.681 | 7.257 | 6.787 | 6.26 | 5.686 | 5.047 | 1.447 | -4.899 | -11.452 | -20.696 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - System Transformation | 17.969 | 17.947 | 17.911 | 17.869 | 17.819 | 17.763 | 17.699 | 17.277 | 16.238 | 15.082 | 13.479 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - System Transformation | 6.529 | 6.381 | 6.173 | 5.975 | 5.749 | 5.5 | 5.208 | 3.697 | 1.425 | -0.94 | -4.287 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - System Transformation | 8.932 | 8.901 | 8.85 | 8.787 | 8.704 | 8.601 | 8.474 | 7.666 | 6.512 | 5.48 | 4.321 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - System Transformation | 0.397 | 0.28 | 0.07 | -0.182 | -0.471 | -0.788 | -1.142 | 14.006 | 10.739 | 6.479 | 0.043 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - System Transformation | 5.191 | 4.438 | 3.603 | 2.937 | 2.22 | 1.467 | 0.685 | -3.251 | -7.618 | -12.164 | -18.5 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - System Transformation | 10.074 | 9.767 | 8.62 | 8.195 | 7.725 | 7.213 | 6.601 | 3.589 | -0.92 | -6.087 | -13.208 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - System Transformation | 14.276 | 13.913 | 13.831 | 13.728 | 13.595 | 13.435 | 13.242 | 12.089 | 10.441 | 9.099 | 7.733 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - System Transformation | 7.171 | 5.777 | 5.533 | 5.265 | 4.941 | 4.575 | 4.13 | 1.656 | -4.197 | -10.081 | -17.897 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - System Transformation | 7.21 | 6.858 | 6.386 | 5.896 | 5.362 | 4.798 | 4.195 | 1.032 | -3.3 | -8.115 | -15.205 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - System Transformation | 28.816 | 28.342 | 27.765 | 27.275 | 26.736 | 26.162 | 25.525 | 22.387 | 18.562 | 15.051 | 10.379 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - System Transformation | 5.069 | 4.872 | 4.593 | 4.283 | 3.939 | 3.57 | 3.157 | 0.966 | -2.459 | -6.46 | -12.159 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - System Transformation | 11.65 | 11.501 | 11.303 | 11.108 | 10.897 | 10.675 | 10.428 | 9.237 | 7.495 | 5.037 | 1.174 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - System Transformation | 18.223 | 18.133 | 17.992 | 17.833 | 17.648 | 17.441 | 17.203 | 15.789 | 13.114 | 10.238 | 6.131 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - System Transformation | 8.575 | 8.604 | 7.162 | 7.134 | 7.077 | 6.991 | 6.856 | 5.99 | 4.277 | 2.645 | 0.563 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - System Transformation | 25.817 | 25.847 | 25.855 | 25.836 | 25.786 | 25.703 | 25.585 | 24.588 | 23.065 | 22.172 | 21.51 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - System Transformation | 14.47 | 14.012 | 14.034 | 14.046 | 14.04 | 14.02 | 13.974 | 13.63 | 12.704 | 11.356 | 9.277 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - System Transformation | 4.788 | 4.53 | 4.13 | 3.651 | 3.069 | 2.387 | 1.601 | -3.1 | -7.487 | -9.755 | -11.119 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - System Transformation | 15.695 | 15.768 | 15.824 | 15.863 | 15.888 | 15.9 | 15.896 | 15.75 | 15.074 | 14.383 | 13.653 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 7.391 | 6.885 | 6.482 | 6.073 | 5.632 | 5.159 | 4.624 | 17.921 | 14.755 | 11.119 | 6.07 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - System Transformation | 2.41 | 2.379 | 2.301 | 2.21 | 2.098 | 1.969 | 1.796 | 0.787 | -1.417 | -4.457 | -9.249 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - System Transformation | 14.24 | 13.944 | 13.567 | 13.19 | 12.775 | 12.331 | 11.843 | 9.321 | 5.897 | 2.847 | -0.89 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - System Transformation | 14.901 | 12.46 | 12.443 | 12.41 | 12.341 | 12.241 | 12.114 | 11.244 | 9.553 | 7.913 | 5.658 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - System Transformation | 8.524 | 7.812 | 7.326 | 6.887 | 6.397 | 5.869 | 5.259 | 2.101 | -3.468 | -9.193 | -16.84 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - System Transformation | 18.387 | 18.295 | 18.181 | 18.08 | 17.964 | 17.838 | 17.685 | 16.921 | 15.33 | 13.65 | 11.474 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - System Transformation | 10.933 | 10.556 | 10.051 | 9.537 | 8.975 | 8.381 | 7.71 | 4.448 | -0.226 | -5.705 | -13.637 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - System Transformation | 3.403 | 2.648 | 2.119 | 1.559 | 0.942 | 0.264 | -0.51 | -4.332 | -8.547 | -13.361 | -19.887 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - System Transformation | 2.594 | 2.263 | 1.868 | 1.522 | 1.149 | 0.755 | 0.33 | -1.668 | -3.954 | -6.81 | -10.95 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - System Transformation | 8.507 | 8.495 | 8.469 | 8.432 | 8.38 | 8.311 | 8.215 | 7.582 | 6.716 | 5.985 | 5.146 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - System Transformation | 21.008 | 20.735 | 20.727 | 20.713 | 20.695 | 20.673 | 20.64 | 20.508 | 19.874 | 19.237 | 18.463 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - System Transformation | 19.154 | 19.06 | 18.914 | 18.756 | 18.576 | 18.372 | 18.103 | 16.747 | 14.702 | 12.019 | 8.04 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - System Transformation | 14.515 | 14.619 | 14.713 | 14.797 | 14.872 | 14.939 | 14.996 | 15.178 | 15.17 | 15.141 | 15.111 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - System Transformation | 14.558 | 14.623 | 14.657 | 14.683 | 14.683 | 14.661 | 14.611 | 14.176 | 13.189 | 12.308 | 11.277 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - System Transformation | 1.053 | 1.053 | 0.998 | 0.888 | 20.607 | 20.352 | 20.022 | 17.246 | 12.701 | 8.957 | 4.346 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - System Transformation | 7.46 | 7.163 | 6.789 | 6.418 | 6.017 | 5.6 | 5.157 | 2.93 | -0.302 | -3.973 | -9.206 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - System Transformation | 6.799 | 6.506 | 6.114 | 5.719 | 5.283 | 4.811 | 4.26 | 1.512 | -1.749 | -5.226 | -9.879 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - System Transformation | 16.187 | 16.079 | 15.935 | 15.78 | 15.608 | 15.422 | 15.224 | 14.085 | 12.336 | 10.647 | 8.39 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - System Transformation | 6.592 | 6.456 | 6.28 | 6.11 | 5.916 | 5.704 | 5.472 | 4.255 | 2.152 | -0.023 | -2.824 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 1.615 | 1.127 | 0.549 | 0.01 | -0.574 | -1.188 | -1.85 | -5.198 | -9.833 | -14.122 | -19.484 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - System Transformation | 18.405 | 18.393 | 18.365 | 18.329 | 18.284 | 18.23 | 18.164 | 17.748 | 17.044 | 16.294 | 15.23 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - System Transformation | 6.495 | 6.272 | 5.984 | 5.716 | 5.422 | 5.106 | 4.756 | 3.087 | 1.063 | -1.644 | -5.792 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - System Transformation | 2.764 | 2.747 | 2.724 | 2.703 | 2.679 | 2.653 | 2.621 | 2.46 | 2.183 | 1.96 | 1.701 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - System Transformation | 9.072 | 8.734 | 8.627 | 8.508 | 8.365 | 8.202 | 8.009 | 6.821 | 4.668 | 2.391 | -0.68 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - System Transformation | 14.227 | 14.058 | 13.835 | 13.613 | 13.37 | 13.113 | 12.833 | 11.428 | 9.401 | 7.328 | 4.543 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - System Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - System Transformation | 20.768 | 20.631 | 20.461 | 20.306 | 20.133 | 19.949 | 19.743 | 18.684 | 16.724 | 14.676 | 11.834 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - System Transformation | 8.245 | 8.057 | 7.813 | 7.582 | 7.327 | 7.055 | 6.739 | 5.111 | 2.482 | -0.962 | -6.226 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - System Transformation | 14.21 | 14.043 | 13.825 | 13.601 | 13.353 | 13.089 | 12.789 | 11.218 | 8.76 | 5.957 | 1.977 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - System Transformation | 33.135 | 32.752 | 32.726 | 32.701 | 32.668 | 32.631 | 32.583 | 32.388 | 31.861 | 31.31 | 30.596 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - System Transformation | 4.299 | 3.616 | 3.17 | 2.707 | 2.202 | 1.671 | 1.061 | -1.69 | -5.223 | -9.378 | -15.386 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - System Transformation | 14.467 | 13.754 | 13.495 | 13.2 | 12.867 | 12.484 | 12.015 | 17.37 | 13.096 | 8.589 | 3.147 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - System Transformation | 9.389 | 9.219 | 8.989 | 8.741 | 8.452 | 8.135 | 7.789 | 5.704 | 1.87 | -2.071 | -7.267 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - System Transformation | 15.338 | 15.297 | 15.24 | 15.175 | 15.097 | 15.008 | 14.899 | 14.226 | 12.898 | 11.469 | 9.581 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 24.288 | 22.484 | 22.157 | 21.836 | 21.494 | 21.137 | 20.758 | 19.05 | 16.936 | 14.673 | 11.387 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - System Transformation | 5.141 | 4.589 | 4.221 | 3.841 | 3.431 | 3 | 2.552 | 0.142 | -3.762 | -8.084 | -13.98 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - System Transformation | 1.38 | 0.662 | 0.221 | -0.203 | -0.662 | -1.145 | -1.68 | -4.368 | -8.744 | -13.867 | -21.371 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - System Transformation | 3.099 | 3.046 | 1.658 | 1.57 | 1.471 | 1.363 | 1.245 | 0.68 | 0.138 | -0.33 | -0.851 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - System Transformation | 7.396 | 6.892 | 8.564 | 8.264 | 7.923 | 7.556 | 7.161 | 4.962 | 0.908 | -3.178 | -8.832 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - System Transformation | 5.57 | 5.558 | 5.498 | 5.415 | 5.306 | 5.174 | 4.981 | 3.686 | 0.218 | -4.146 | -10.885 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - System Transformation | 32.093 | 30.698 | 30.607 | 30.505 | 30.386 | 30.253 | 30.116 | 29.266 | 27.999 | 26.458 | 24.118 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - System Transformation | 12.169 | 12.028 | 11.831 | 11.622 | 11.391 | 11.149 | 10.902 | 9.491 | 6.739 | 3.669 | -0.925 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - System Transformation | 8.724 | 7.951 | 7.635 | 7.384 | 7.111 | 6.827 | 6.539 | 5.278 | 3.645 | 1.687 | -1.176 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - System Transformation | 6.45 | 6.517 | 6.563 | 6.594 | 6.608 | 6.605 | 6.578 | 6.252 | 5.319 | 4.155 | 2.483 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - System Transformation | 13.458 | 13.405 | 13.313 | 13.199 | 13.065 | 12.917 | 12.752 | 11.78 | 9.358 | 7.04 | 3.954 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 14.554 | 14.476 | 14.348 | 14.166 | 13.919 | 13.602 | 13.203 | 10.417 | 6.466 | 3.778 | 1.501 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 12.874 | 12.733 | 12.564 | 12.376 | 12.167 | 11.942 | 11.692 | 10.211 | 7.166 | 3.702 | -0.874 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - System Transformation | 4.471 | 3.409 | 3.088 | 2.743 | 2.366 | 1.959 | 1.49 | -0.942 | -4.634 | -8.679 | -13.666 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - System Transformation | 4.628 | 3.117 | 2.135 | 1.107 | 0.02 | -1.142 | -2.472 | -8.674 | -14.181 | -21.88 | -32.813 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - System Transformation | 11.47 | 10.599 | 10.177 | 9.846 | 9.487 | 9.112 | 8.682 | 6.763 | 4.081 | 1.265 | -2.527 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - System Transformation | 15.733 | 14.949 | 14.623 | 14.285 | 13.913 | 13.519 | 13.095 | 10.898 | 7.482 | 3.614 | -2.173 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - System Transformation | 8.059 | 7.903 | 7.659 | 7.389 | 7.088 | 6.766 | 6.417 | 4.5 | 1.477 | -1.892 | -6.923 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - System Transformation | 12.723 | 12.735 | 12.74 | 12.74 | 12.734 | 12.724 | 12.707 | 12.566 | 12.265 | 11.977 | 11.694 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - System Transformation | 21.642 | 21.577 | 21.479 | 21.369 | 21.247 | 21.109 | 20.935 | 19.991 | 18.919 | 17.425 | 15.256 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - System Transformation | 14.974 | 15.079 | 15.168 | 15.244 | 15.305 | 15.354 | 15.384 | 15.402 | 14.541 | 13.758 | 12.827 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 10.632 | 10.317 | 9.918 | 9.521 | 9.091 | 8.637 | 8.135 | 5.61 | 2.165 | -1.927 | -7.755 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 21.862 | 21.827 | 21.78 | 21.733 | 21.679 | 21.618 | 21.546 | 21.167 | 20.569 | 19.87 | 18.946 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - System Transformation | 2.505 | 2.325 | 2.06 | 1.78 | 1.468 | 1.132 | 0.76 | -1.198 | -4.235 | -8.208 | -14.245 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - System Transformation | 6.594 | 6.583 | 6.568 | 6.553 | 6.534 | 6.515 | 6.493 | 6.367 | 6.086 | 5.804 | 5.414 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - System Transformation | 5.994 | 5.258 | 5.073 | 4.905 | 4.713 | 4.503 | 4.253 | 3.116 | 1.53 | -0.616 | -3.735 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - System Transformation | 11.904 | 11.389 | 10.702 | 9.969 | 9.158 | 8.283 | 7.324 | 1.974 | -5.51 | -13.512 | -24.782 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - System Transformation | 10.424 | 8.98 | 8.203 | 7.839 | 7.424 | 6.971 | 6.471 | 3.78 | -0.564 | -5.119 | -11.508 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - System Transformation | 15.093 | 14.896 | 14.663 | 14.424 | 14.161 | 13.881 | 13.582 | 11.876 | 9.264 | 6.797 | 3.769 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - System Transformation | 15.882 | 15.787 | 15.682 | 15.574 | 15.459 | 15.338 | 15.21 | 14.566 | 13.833 | 13.115 | 12.37 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - System Transformation | 2.003 | 1.663 | 22.821 | 22.65 | 22.432 | 22.168 | 21.821 | 19.656 | 16.143 | 12.91 | 8.973 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - System Transformation | 13.621 | 13.095 | 12.739 | 12.389 | 12.011 | 11.618 | 11.199 | 9.293 | 7.531 | 5.848 | 3.645 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - System Transformation | 3.222 | 3.036 | 2.806 | 2.578 | 2.34 | 2.095 | 1.843 | 0.608 | -0.77 | -2.342 | -4.549 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - System Transformation | 2.781 | 2.628 | 2.443 | 2.26 | 2.06 | 1.848 | 1.622 | 0.416 | -1.122 | -2.507 | -4.165 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 12.326 | 11.721 | 11.406 | 11.061 | 10.673 | 10.253 | 9.766 | 7.215 | 2.539 | -2.255 | -8.928 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - System Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - System Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - System Transformation | 17.574 | 17.057 | 16.887 | 16.713 | 16.518 | 16.308 | 16.077 | 14.845 | 12.559 | 9.953 | 6.183 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - System Transformation | 11.117 | 10.005 | 9.851 | 9.682 | 9.487 | 9.269 | 9.027 | 7.769 | 6.193 | 4.873 | 3.483 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - System Transformation | 10.407 | 10.235 | 10.01 | 9.794 | 9.55 | 9.282 | 8.972 | 7.325 | 4.856 | 2.074 | -1.894 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - System Transformation | 12.895 | 12.611 | 12.273 | 11.964 | 11.626 | 11.269 | 10.888 | 8.905 | 6.236 | 3.701 | 0.46 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - System Transformation | 10.428 | 9.621 | 9.413 | 9.182 | 8.927 | 8.653 | 8.361 | 6.757 | 4.284 | 1.483 | -2.489 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - System Transformation | 10.284 | 10.193 | 10.051 | 9.895 | 9.71 | 9.5 | 9.251 | 7.804 | 5.391 | 2.589 | -1.591 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - System Transformation | 16.763 | 15.988 | 15.984 | 15.964 | 15.921 | 15.858 | 15.762 | 15.094 | 13.273 | 11.398 | 8.866 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - System Transformation | 15.671 | 15.399 | 15.045 | 14.686 | 14.275 | 13.819 | 13.298 | 10.359 | 6.227 | 2.203 | -3.056 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | 5.515 | 5.369 | 5.176 | 4.986 | 4.778 | 4.56 | 4.328 | 3.171 | 1.839 | 0.647 | -0.946 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - System Transformation | 12.362 | 11.991 | 10.229 | 9.905 | 9.528 | 9.085 | 8.511 | 5.422 | 1.409 | -3.444 | -10.194 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - System Transformation | 23.15 | 13.658 | 2.812 | 2.367 | 1.857 | 1.291 | 0.622 | -2.389 | -6.464 | -10.817 | -16.535 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - System Transformation | 0.555 | -0.221 | -0.81 | -3.12 | -3.719 | -4.346 | -5.028 | -8.256 | -12.714 | -17.467 | -24.204 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - System Transformation | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - System Transformation | 3.203 | 3.064 | 2.898 | 2.718 | 2.515 | 2.293 | 2.043 | 0.52 | -2.095 | -4.802 | -8.255 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - System Transformation | 11.949 | 11.155 | 10.886 | 10.595 | 10.273 | 9.897 | 9.393 | 6.76 | 4.067 | 0.455 | -4.435 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 5.804 | 4.195 | 4.133 | 4.04 | 3.91 | 3.75 | 3.528 | 2.327 | -0.479 | -3.311 | -7.114 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 27.947 | 27.964 | 27.98 | 27.994 | 28.006 | 28.018 | 28.027 | 28.06 | 28.07 | 28.073 | 28.077 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - System Transformation | 19.937 | 18.929 | 18.632 | 18.32 | 17.983 | 17.631 | 17.254 | 15.395 | 12.785 | 9.688 | 5.148 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - System Transformation | 8.273 | 7.619 | 7.719 | 7.756 | 7.716 | 7.596 | 7.387 | 5.554 | 2.708 | 0.963 | -0.417 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - System Transformation | 3.069 | 2.909 | 2.809 | 2.699 | 2.58 | 2.451 | 2.312 | 1.579 | 0.667 | -0.288 | -1.251 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - System Transformation | 13.774 | 13.504 | 13.165 | 12.844 | 12.499 | 12.142 | 11.764 | 9.744 | 6.355 | 1.978 | -4.971 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - System Transformation | 2.25 | 1.912 | 1.494 | 1.065 | 0.596 | 0.099 | -0.436 | -3.295 | -7.183 | -10.771 | -15.187 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - System Transformation | 7.735 | 6.803 | 6.489 | 6.171 | 5.826 | 5.462 | 5.062 | 3.274 | 1.541 | -0.258 | -2.489 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 23.467 | 22.927 | 22.502 | 22.051 | 21.56 | 21.04 | 20.484 | 17.491 | 12.794 | 7.754 | 0.676 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - System Transformation | 11.164 | 10.98 | 10.696 | 10.388 | 10.043 | 9.662 | 9.199 | 6.864 | 3.454 | -0.75 | -7.039 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - System Transformation | 11.091 | 10.801 | 10.432 | 10.064 | 9.667 | 9.246 | 8.777 | 6.324 | 2.346 | -2.027 | -8.349 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - System Transformation | 12.799 | 12.594 | 12.683 | 12.758 | 12.815 | 12.857 | 12.875 | 12.798 | 11.901 | 10.929 | 9.605 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - System Transformation | 5.864 | 5.376 | 4.816 | 4.291 | 3.731 | 3.152 | 2.56 | -0.56 | -5.244 | -10.422 | -17.599 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - System Transformation | 8.49 | 6.878 | 6.776 | 6.658 | 6.509 | 6.336 | 6.143 | 4.944 | 3.021 | 1.126 | -1.568 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - System Transformation | 7.743 | 7.006 | 6.683 | 6.339 | 5.967 | 5.577 | 5.179 | 3.045 | -0.222 | -4.034 | -9.688 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - System Transformation | 31.094 | 31.1 | 31.106 | 31.111 | 31.116 | 31.12 | 31.123 | 31.129 | 31.116 | 31.092 | 31.052 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - System Transformation | 10.261 | 10.262 | 10.241 | 10.21 | 25.57 | 25.519 | 25.45 | 25.029 | 23.971 | 22.54 | 20.314 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - System Transformation | 7.518 | 5.782 | 20.348 | 19.942 | 19.491 | 19.013 | 18.502 | 16.053 | 11.972 | 7.91 | 2.283 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - System Transformation | 8.919 | 8.661 | 8.344 | 8.009 | 7.642 | 7.247 | 6.802 | 4.409 | 0.981 | -2.198 | -6.004 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - System Transformation | 11.646 | 11.516 | 11.351 | 11.192 | 11.026 | 10.856 | 10.689 | 9.898 | 9.064 | 8.04 | 6.455 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - System Transformation | 19.87 | 19.32 | 19.232 | 19.141 | 19.032 | 18.912 | 18.787 | 17.969 | 16.128 | 13.957 | 10.601 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - System Transformation | 10.494 | 10.075 | 9.568 | 9.128 | 8.64 | 8.116 | 7.533 | 4.561 | 0.703 | -3.258 | -8.742 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - System Transformation | 11.874 | 11.5 | 11.248 | 10.977 | 10.684 | 10.377 | 10.061 | 8.355 | 5.621 | 2.018 | -3.539 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - System Transformation | 10.868 | 10.28 | 9.946 | 9.6 | 9.225 | 8.836 | 8.432 | 6.418 | 3.548 | 0.403 | -4.323 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 13.893 | 13.895 | 13.885 | 13.869 | 13.845 | 13.814 | 13.772 | 13.472 | 12.611 | 11.722 | 10.494 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 14.088 | 14.089 | 14.078 | 14.056 | 14.022 | 13.978 | 13.915 | 13.501 | 12.454 | 11.502 | 10.354 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 18.643 | 18.56 | 18.441 | 18.317 | 18.18 | 18.031 | 17.858 | 17.002 | 15.875 | 14.744 | 13.208 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 18.855 | 18.786 | 18.687 | 18.581 | 18.464 | 18.336 | 18.179 | 17.403 | 16.047 | 14.609 | 12.642 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - System Transformation | 12.082 | 11.827 | 11.503 | 11.172 | 10.821 | 10.459 | 10.1 | 8.183 | 5.007 | 1.283 | -4.436 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 22.041 | 21.705 | 21.314 | 20.986 | 20.627 | 20.245 | 19.812 | 17.666 | 14.706 | 11.62 | 7.404 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - System Transformation | 26.933 | 25.969 | 25.845 | 25.713 | 25.566 | 25.404 | 25.225 | 24.475 | 23.777 | 23.138 | 22.519 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - System Transformation | 5.578 | 5.16 | 5.13 | 5.102 | 5.068 | 5.031 | 4.986 | 4.771 | 4.365 | 3.94 | 3.381 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - System Transformation | 11.105 | 11.115 | 11.105 | 11.087 | 11.056 | 11.013 | 10.958 | 10.539 | 9.188 | 7.614 | 5.344 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NPg Best View | 5.51 | 5.197 | 4.632 | 3.984 | 3.564 | 3.259 | 2.906 | 1.4 | -3.973 | -8.153 | -12.558 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NPg Best View | 11.026 | 10.115 | 7.989 | 6.903 | 6.114 | 5.453 | 4.683 | 1.443 | -7.304 | -13.903 | -20.449 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 8.045 | 7.734 | 9.197 | 8.59 | 8.145 | 7.758 | 7.306 | 5.22 | 0.19 | -3.669 | -7.587 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NPg Best View | 5.805 | 5.594 | 5.161 | 4.65 | 4.306 | 4.029 | 3.694 | 2.216 | -2.97 | -7.101 | -11.272 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NPg Best View | 22.754 | 22.804 | 22.85 | 22.893 | 22.932 | 22.967 | 22.997 | 23.055 | 23.057 | 23.06 | 23.062 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NPg Best View | 2.119 | 2.125 | 2.047 | 1.935 | 1.873 | 1.823 | 1.741 | 1.282 | -0.598 | -2.049 | -3.518 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NPg Best View | 3.674 | 3.644 | 3.604 | 3.565 | 3.528 | 3.49 | 3.444 | 3.2 | 2.883 | 2.641 | 2.417 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NPg Best View | 2.697 | 2.572 | 2.348 | 2.076 | 1.831 | 1.593 | 1.31 | -0.219 | -3.248 | -5.621 | -7.988 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NPg Best View | 7.3 | 7.245 | 7.051 | 6.821 | 6.646 | 6.514 | 6.352 | 5.601 | 2.493 | -0.007 | -2.6 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NPg Best View | 12.044 | 11.846 | 11.492 | 11.088 | 10.823 | 10.57 | 10.228 | 8.467 | 5.125 | 2.851 | 0.705 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NPg Best View | 4.834 | 4.277 | 3.802 | 3.288 | 2.865 | 2.474 | 2.017 | -0.055 | -6.084 | -11.036 | -15.833 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NPg Best View | 11.088 | 10.575 | 10.265 | 9.897 | 9.638 | 9.417 | 9.146 | 7.806 | 3.096 | -0.714 | -4.506 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NPg Best View | 7.54 | 7.196 | 6.683 | 6.115 | 5.67 | 5.24 | 4.732 | 2.104 | -2.337 | -5.557 | -8.731 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NPg Best View | 3.6 | 2.969 | 2.548 | 2.075 | 1.74 | 1.439 | 1.077 | -0.649 | -5.48 | -9.304 | -13.05 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 13.317 | 13.171 | 12.875 | 12.523 | 12.169 | 11.777 | 10.692 | 6.513 | 3.624 | 1.905 | 0.4 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 16.539 | 16.574 | 16.537 | 16.437 | 16.318 | 16.193 | 16.049 | 15.329 | 14.256 | 13.757 | 13.353 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NPg Best View | 9.565 | 8.691 | 8.526 | 8.318 | 8.112 | 7.893 | 7.62 | 6.156 | 2.149 | -0.97 | -3.813 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NPg Best View | 10.219 | 9.617 | 9.232 | 8.805 | 8.437 | 8.09 | 7.691 | 5.824 | 0.739 | -3.408 | -7.326 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NPg Best View | 15.6 | 15.406 | 15.081 | 14.723 | 14.454 | 14.211 | 13.92 | 12.657 | 9.095 | 6.216 | 3.462 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NPg Best View | 7.142 | 7.02 | 6.798 | 6.488 | 6.157 | 5.761 | 5.262 | 2.11 | -1.561 | -3.67 | -5.459 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NPg Best View | 20.281 | 20.013 | 19.612 | 19.172 | 18.75 | 18.324 | 17.827 | 15.193 | 10.314 | 6.548 | 2.95 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 17.817 | 17.71 | 17.53 | 17.325 | 17.138 | 16.951 | 16.729 | 15.611 | 12.86 | 10.506 | 8.238 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NPg Best View | 11.858 | 11.154 | 10.46 | 9.671 | 9.112 | 8.63 | 8.076 | 5.52 | -0.976 | -6.044 | -11.108 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NPg Best View | 7.9 | 7.404 | 7.301 | 7.174 | 7.098 | 7.05 | 6.981 | 6.645 | 4.675 | 3.124 | 1.555 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NPg Best View | 8.847 | 8.521 | 7.904 | 7.181 | 6.65 | 6.204 | 5.661 | 2.902 | -3.239 | -7.589 | -12.112 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NPg Best View | 7.044 | 6.482 | 5.957 | 5.427 | 5.022 | 4.675 | 4.257 | 2.372 | -1.558 | -4.439 | -7.287 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NPg Best View | 8.134 | 7.911 | 7.511 | 7.052 | 6.7 | 6.405 | 6.054 | 4.373 | -0.209 | -3.678 | -7.094 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NPg Best View | 8.079 | 7.909 | 7.575 | 7.198 | 6.843 | 6.515 | 6.135 | 4.432 | -0.056 | -3.697 | -7.145 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NPg Best View | 4.063 | 3.841 | 3.392 | 2.858 | 2.454 | 2.09 | 1.657 | -0.372 | -6.212 | -10.81 | -15.262 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NPg Best View | 7.87 | 7.567 | 7.113 | 6.601 | 6.168 | 5.766 | 5.304 | 3.073 | -1.83 | -5.888 | -9.925 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NPg Best View | 8.516 | 8.41 | 8.552 | 8.653 | 8.754 | 8.846 | 8.9 | 9.015 | 7.357 | 6.071 | 4.826 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NPg Best View | 5.625 | 4.728 | 4.468 | 4.2 | 3.967 | 3.74 | 3.455 | 2.21 | -0.599 | -2.795 | -4.887 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NPg Best View | 14.741 | 13.495 | 12.788 | 11.939 | 11.313 | 10.753 | 10.087 | 6.864 | -0.301 | -5.529 | -10.738 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NPg Best View | 12.882 | 12.895 | 12.843 | 12.767 | 12.731 | 12.71 | 12.666 | 12.427 | 11.089 | 10.061 | 8.991 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NPg Best View | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 12.679 | 12.709 | 12.678 | 12.61 | 12.567 | 12.528 | 12.463 | 12.03 | 10.278 | 8.954 | 7.667 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 14.7 | 14.662 | 14.546 | 14.38 | 14.255 | 14.132 | 13.969 | 12.919 | 10.561 | 8.909 | 7.291 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NPg Best View | 4.505 | 4.467 | 4.395 | 4.317 | 4.273 | 4.25 | 4.224 | 4.082 | 3.049 | 2.178 | 1.242 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NPg Best View | 8.985 | 8.848 | 8.634 | 8.402 | 8.255 | 8.131 | 7.986 | 7.3 | 5.229 | 3.616 | 2.019 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NPg Best View | 8.401 | 8.247 | 7.93 | 7.574 | 7.3 | 7.052 | 6.752 | 5.312 | 0.551 | -3.234 | -6.826 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 23.172 | 22.924 | 22.911 | 22.89 | 22.876 | 22.863 | 22.834 | 22.704 | 21.498 | 20.497 | 19.585 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NPg Best View | 6.878 | 6.833 | 6.657 | 6.432 | 6.244 | 6.042 | 5.767 | 4.187 | 0.585 | -1.919 | -4.199 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NPg Best View | 5.159 | 4.4 | 3.771 | 3.037 | 2.446 | 1.894 | 1.226 | -1.971 | -7.751 | -11.647 | -15.388 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NPg Best View | 9.993 | 8.771 | 8.355 | 7.867 | 7.487 | 7.145 | 6.736 | 4.776 | -1.289 | -6.002 | -10.526 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 8.711 | 8.639 | 8.459 | 8.26 | 8.079 | 7.886 | 7.629 | 6.332 | 3.427 | 1.196 | -0.807 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 13.465 | 13.259 | 12.882 | 12.479 | 12.175 | 11.899 | 11.56 | 9.963 | 4.602 | 0.185 | -4.008 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NPg Best View | 4.323 | 3.915 | 3.831 | 3.715 | 3.632 | 3.563 | 3.462 | 2.952 | 0.661 | -1.237 | -3.155 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NPg Best View | 8.144 | 7.885 | 7.37 | 6.75 | 6.227 | 5.732 | 5.139 | 2.177 | -6.037 | -12.5 | -18.59 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NPg Best View | 18.041 | 18.051 | 18.025 | 17.985 | 17.959 | 17.939 | 17.909 | 17.736 | 16.556 | 15.538 | 14.544 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NPg Best View | 6.704 | 6.588 | 6.346 | 6.08 | 5.91 | 5.772 | 5.579 | 4.527 | 1.776 | -0.258 | -2.33 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NPg Best View | 9.03 | 9.048 | 9.024 | 8.978 | 8.925 | 8.858 | 8.758 | 8.136 | 7.121 | 6.429 | 5.782 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NPg Best View | 0.566 | 0.447 | 0.125 | -0.28 | -0.553 | -0.759 | -1.015 | 14.919 | 10.039 | 6.119 | 2.139 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NPg Best View | 5.645 | 5.108 | 4.377 | 3.716 | 3.216 | 2.717 | 2.09 | -0.968 | -6.395 | -10.281 | -13.842 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NPg Best View | 10.209 | 9.796 | 8.394 | 7.642 | 7.093 | 6.634 | 6.104 | 3.649 | -2.391 | -6.949 | -11.659 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NPg Best View | 14.428 | 14.155 | 14.131 | 14.072 | 13.988 | 13.88 | 13.724 | 12.843 | 11.34 | 10.295 | 9.348 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NPg Best View | 7.425 | 6.068 | 5.732 | 5.3 | 4.991 | 4.726 | 4.382 | 2.605 | -4.434 | -9.96 | -15.318 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NPg Best View | 7.371 | 7.009 | 6.415 | 5.741 | 5.261 | 4.836 | 4.321 | 1.759 | -4.144 | -8.663 | -13.163 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NPg Best View | 29.132 | 28.763 | 28.194 | 27.644 | 27.249 | 26.883 | 26.409 | 23.958 | 19.659 | 16.686 | 13.789 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NPg Best View | 5.222 | 5.018 | 4.635 | 4.189 | 3.858 | 3.577 | 3.243 | 1.676 | -2.755 | -6.265 | -9.818 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NPg Best View | 11.724 | 11.526 | 11.183 | 10.819 | 10.581 | 10.406 | 10.205 | 9.423 | 6.672 | 4.504 | 2.185 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NPg Best View | 18.307 | 18.241 | 18.055 | 17.83 | 17.636 | 17.459 | 17.249 | 16.189 | 12.666 | 9.867 | 7.204 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NPg Best View | 8.667 | 8.705 | 7.219 | 7.116 | 7.042 | 6.972 | 6.862 | 6.216 | 4.333 | 3.02 | 1.737 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NPg Best View | 25.882 | 25.946 | 25.97 | 25.95 | 25.89 | 25.784 | 25.628 | 24.531 | 23.318 | 22.751 | 22.373 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NPg Best View | 14.614 | 14.181 | 14.174 | 14.142 | 14.167 | 14.221 | 14.254 | 14.368 | 13.228 | 12.32 | 11.252 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NPg Best View | 4.944 | 4.788 | 4.432 | 3.96 | 3.381 | 2.669 | 1.757 | -3.276 | -6.959 | -8.438 | -9.303 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NPg Best View | 15.891 | 16.079 | 16.236 | 16.37 | 16.493 | 16.604 | 16.691 | 17.034 | 16.811 | 16.608 | 16.373 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 7.544 | 7.08 | 6.627 | 6.121 | 5.699 | 5.31 | 4.861 | 18.842 | 14.5 | 11.212 | 8.054 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NPg Best View | 2.498 | 2.398 | 2.14 | 1.838 | 1.677 | 1.589 | 1.487 | 1.035 | -2.348 | -5.069 | -7.979 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NPg Best View | 14.392 | 14.129 | 13.715 | 13.264 | 12.9 | 12.547 | 12.119 | 9.912 | 6.228 | 3.618 | 1.116 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NPg Best View | 15.046 | 12.707 | 12.736 | 12.736 | 12.71 | 12.669 | 12.578 | 12.092 | 10.299 | 8.966 | 7.739 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NPg Best View | 8.828 | 8.166 | 7.579 | 6.968 | 6.505 | 6.1 | 5.608 | 3.282 | -3.158 | -8.174 | -13.173 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NPg Best View | 18.52 | 18.462 | 18.336 | 18.206 | 18.119 | 18.052 | 17.962 | 17.535 | 15.843 | 14.491 | 13.094 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NPg Best View | 11.098 | 10.603 | 9.823 | 8.971 | 8.388 | 7.924 | 7.376 | 4.812 | -1.587 | -6.42 | -11.514 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NPg Best View | 3.595 | 2.869 | 2.224 | 1.468 | 0.838 | 0.244 | -0.45 | -3.486 | -9.399 | -13.712 | -17.823 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NPg Best View | 2.775 | 2.428 | 1.925 | 1.427 | 1.076 | 0.791 | 0.445 | -1.077 | -4.403 | -6.855 | -9.405 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NPg Best View | 8.522 | 8.491 | 8.42 | 8.329 | 8.242 | 8.153 | 8.042 | 7.369 | 6.406 | 5.846 | 5.319 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NPg Best View | 21.03 | 20.757 | 20.734 | 20.695 | 20.671 | 20.656 | 20.638 | 20.57 | 19.808 | 19.194 | 18.601 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NPg Best View | 19.24 | 19.092 | 18.804 | 18.472 | 18.244 | 18.074 | 17.87 | 16.951 | 13.844 | 11.486 | 9.021 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NPg Best View | 14.645 | 14.829 | 14.997 | 15.151 | 15.294 | 15.424 | 15.537 | 16.015 | 16.332 | 16.6 | 16.839 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NPg Best View | 14.754 | 14.911 | 14.996 | 15.051 | 15.121 | 15.183 | 15.202 | 15.148 | 14.129 | 13.46 | 12.79 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NPg Best View | 1.172 | 1.197 | 1.076 | 0.848 | 20.502 | 20.187 | 19.76 | 16.912 | 12.026 | 8.804 | 5.955 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NPg Best View | 7.597 | 7.29 | 6.797 | 6.273 | 5.879 | 5.539 | 5.147 | 3.425 | -0.852 | -4.198 | -7.594 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NPg Best View | 6.959 | 6.659 | 6.164 | 5.602 | 5.181 | 4.795 | 4.334 | 2.163 | -2.113 | -5.084 | -7.946 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NPg Best View | 16.258 | 16.201 | 16.087 | 15.959 | 15.815 | 15.659 | 15.472 | 14.526 | 12.516 | 10.901 | 9.439 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NPg Best View | 6.745 | 6.661 | 6.475 | 6.278 | 6.104 | 5.946 | 5.751 | 4.896 | 2.492 | 0.662 | -1.115 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 1.815 | 1.392 | 0.79 | 0.178 | -0.344 | -0.85 | -1.446 | -4.379 | -9.496 | -13.374 | -17.13 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NPg Best View | 18.447 | 18.448 | 18.414 | 18.365 | 18.327 | 18.291 | 18.24 | 17.952 | 17.091 | 16.44 | 15.81 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NPg Best View | 6.616 | 6.395 | 6.004 | 5.605 | 5.309 | 5.063 | 4.776 | 3.629 | 0.498 | -1.918 | -4.371 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NPg Best View | 2.779 | 2.767 | 2.743 | 2.719 | 2.699 | 2.68 | 2.655 | 2.521 | 2.234 | 2.029 | 1.834 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NPg Best View | 9.184 | 8.883 | 8.747 | 8.589 | 8.44 | 8.304 | 8.141 | 7.315 | 4.869 | 2.945 | 1.072 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NPg Best View | 14.333 | 14.19 | 13.945 | 13.677 | 13.467 | 13.279 | 13.052 | 11.965 | 9.496 | 7.618 | 5.773 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NPg Best View | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NPg Best View | 20.844 | 20.707 | 20.483 | 20.249 | 20.074 | 19.922 | 19.741 | 18.88 | 16.37 | 14.423 | 12.5 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NPg Best View | 8.382 | 8.132 | 7.701 | 7.243 | 6.963 | 6.763 | 6.527 | 5.484 | 1.596 | -1.451 | -4.672 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NPg Best View | 14.295 | 14.082 | 13.729 | 13.336 | 13.068 | 12.845 | 12.584 | 11.342 | 8.039 | 5.531 | 2.979 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NPg Best View | 33.177 | 32.805 | 32.773 | 32.732 | 32.709 | 32.696 | 32.673 | 32.587 | 31.984 | 31.517 | 31.045 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NPg Best View | 4.452 | 3.696 | 3.043 | 2.324 | 1.807 | 1.393 | 0.901 | -1.2 | -6.143 | -9.752 | -13.501 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NPg Best View | 14.598 | 13.882 | 13.553 | 13.154 | 12.786 | 12.422 | 12.01 | 17.804 | 13.037 | 9.205 | 5.379 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NPg Best View | 9.592 | 9.558 | 9.4 | 9.211 | 8.976 | 8.731 | 8.434 | 6.901 | 2.345 | -1.346 | -4.741 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NPg Best View | 15.414 | 15.39 | 15.316 | 15.222 | 15.149 | 15.085 | 15.004 | 14.554 | 13.059 | 11.866 | 10.662 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 24.38 | 22.595 | 22.231 | 21.838 | 21.549 | 21.284 | 20.966 | 19.61 | 16.81 | 14.674 | 12.619 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NPg Best View | 5.32 | 4.857 | 4.504 | 4.106 | 3.763 | 3.434 | 3.056 | 1.29 | -3.383 | -7.33 | -11.162 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NPg Best View | 1.551 | 0.813 | 0.225 | -0.38 | -0.837 | -1.216 | -1.658 | -3.652 | -9.522 | -14.333 | -19.222 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NPg Best View | 3.163 | 3.141 | 1.776 | 1.711 | 1.654 | 1.591 | 1.504 | 1.083 | 0.637 | 0.363 | 0.114 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NPg Best View | 7.613 | 7.216 | 8.902 | 8.567 | 8.302 | 8.045 | 7.717 | 6.082 | 1.126 | -2.78 | -6.48 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NPg Best View | 5.672 | 5.562 | 5.269 | 4.901 | 4.724 | 4.632 | 4.516 | 3.849 | -1.189 | -5.342 | -9.712 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NPg Best View | 32.137 | 30.778 | 30.706 | 30.616 | 30.515 | 30.404 | 30.269 | 29.594 | 27.692 | 26.086 | 24.605 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NPg Best View | 12.267 | 12.182 | 11.987 | 11.757 | 11.568 | 11.389 | 11.175 | 10.181 | 6.413 | 3.26 | 0.315 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NPg Best View | 8.856 | 8.162 | 7.848 | 7.568 | 7.346 | 7.144 | 6.905 | 6.033 | 3.792 | 2.045 | 0.385 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NPg Best View | 6.582 | 6.696 | 6.756 | 6.781 | 6.847 | 6.916 | 6.96 | 7.052 | 6.061 | 5.287 | 4.456 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NPg Best View | 13.533 | 13.524 | 13.442 | 13.324 | 13.209 | 13.095 | 12.954 | 12.219 | 9.319 | 6.962 | 4.801 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 14.737 | 14.747 | 14.666 | 14.493 | 14.253 | 13.925 | 13.484 | 10.655 | 7.501 | 5.685 | 4.195 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 13.059 | 12.962 | 12.775 | 12.534 | 12.391 | 12.273 | 12.127 | 11.281 | 7.912 | 4.978 | 1.945 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NPg Best View | 4.659 | 3.646 | 3.294 | 2.882 | 2.531 | 2.206 | 1.845 | 0.123 | -3.915 | -7.239 | -10.569 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NPg Best View | 4.957 | 3.396 | 2.175 | 0.807 | -0.246 | -1.153 | -2.186 | -6.558 | -14.714 | -20.798 | -26.98 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NPg Best View | 11.673 | 10.831 | 10.346 | 9.901 | 9.578 | 9.304 | 8.974 | 7.514 | 4.285 | 1.882 | -0.558 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NPg Best View | 15.841 | 15.055 | 14.616 | 14.127 | 13.758 | 13.436 | 13.057 | 11.416 | 6.689 | 2.983 | -0.602 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NPg Best View | 8.178 | 8.064 | 7.783 | 7.449 | 7.185 | 6.949 | 6.66 | 5.305 | 1.175 | -2.092 | -5.19 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NPg Best View | 12.802 | 12.864 | 12.916 | 12.961 | 13 | 13.032 | 13.054 | 13.112 | 13.041 | 12.971 | 12.894 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NPg Best View | 21.738 | 21.696 | 21.581 | 21.428 | 21.325 | 21.24 | 21.134 | 20.658 | 19.146 | 17.969 | 16.772 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NPg Best View | 15.142 | 15.341 | 15.506 | 15.646 | 15.779 | 15.9 | 15.999 | 16.388 | 15.808 | 15.344 | 14.895 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 10.755 | 10.402 | 9.847 | 9.248 | 8.789 | 8.394 | 7.947 | 5.977 | 1.16 | -2.558 | -6.302 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 21.937 | 21.931 | 21.892 | 21.847 | 21.82 | 21.8 | 21.768 | 21.611 | 21.011 | 20.531 | 20.024 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NPg Best View | 2.646 | 2.461 | 2.077 | 1.638 | 1.325 | 1.073 | 0.775 | -0.457 | -5.108 | -8.796 | -12.444 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NPg Best View | 6.606 | 6.598 | 6.577 | 6.552 | 6.537 | 6.523 | 6.506 | 6.419 | 6.077 | 5.809 | 5.548 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NPg Best View | 6.12 | 5.368 | 5.065 | 4.766 | 4.539 | 4.374 | 4.178 | 3.412 | 1.053 | -0.692 | -2.582 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NPg Best View | 12.099 | 11.587 | 10.749 | 9.801 | 8.969 | 8.178 | 7.252 | 2.695 | -7.2 | -14.844 | -22.103 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NPg Best View | 10.566 | 9.13 | 8.246 | 7.724 | 7.311 | 6.927 | 6.46 | 4.252 | -1.338 | -5.576 | -9.662 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NPg Best View | 15.194 | 15.055 | 14.845 | 14.613 | 14.378 | 14.134 | 13.85 | 12.39 | 9.669 | 7.488 | 5.451 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NPg Best View | 15.984 | 15.955 | 15.911 | 15.859 | 15.803 | 15.74 | 15.663 | 15.279 | 14.778 | 14.331 | 13.904 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NPg Best View | 2.142 | 1.778 | 22.828 | 22.508 | 22.249 | 21.998 | 21.675 | 19.72 | 16.02 | 13.459 | 10.901 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NPg Best View | 13.753 | 13.264 | 12.899 | 12.515 | 12.207 | 11.918 | 11.563 | 10.002 | 7.887 | 6.548 | 5.311 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NPg Best View | 3.305 | 3.138 | 2.89 | 2.624 | 2.427 | 2.246 | 2.036 | 1.129 | -0.618 | -1.952 | -3.246 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NPg Best View | 2.856 | 2.739 | 2.568 | 2.386 | 2.217 | 2.044 | 1.839 | 0.795 | -0.785 | -1.96 | -3.052 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 12.485 | 11.909 | 11.524 | 11.06 | 10.694 | 10.371 | 9.978 | 8.047 | 2.117 | -2.58 | -7.112 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NPg Best View | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NPg Best View | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NPg Best View | 17.692 | 17.209 | 17.006 | 16.768 | 16.602 | 16.46 | 16.284 | 15.512 | 12.537 | 10.137 | 7.792 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NPg Best View | 11.241 | 10.209 | 10.117 | 9.997 | 9.86 | 9.701 | 9.495 | 8.456 | 6.907 | 5.737 | 4.67 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NPg Best View | 10.522 | 10.321 | 9.968 | 9.592 | 9.323 | 9.098 | 8.824 | 7.499 | 4.221 | 1.811 | -0.666 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NPg Best View | 13.052 | 12.821 | 12.482 | 12.144 | 11.858 | 11.583 | 11.252 | 9.617 | 6.696 | 4.503 | 2.378 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NPg Best View | 10.549 | 9.799 | 9.599 | 9.352 | 9.143 | 8.945 | 8.707 | 7.593 | 4.442 | 1.857 | -0.622 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NPg Best View | 10.371 | 10.245 | 9.979 | 9.665 | 9.45 | 9.273 | 9.052 | 7.953 | 4.651 | 2.105 | -0.494 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NPg Best View | 16.893 | 16.153 | 16.141 | 16.09 | 16.069 | 16.058 | 16.015 | 15.68 | 13.602 | 11.954 | 10.321 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NPg Best View | 15.836 | 15.557 | 15.08 | 14.546 | 14.128 | 13.726 | 13.233 | 10.661 | 5.851 | 2.44 | -0.876 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | 5.614 | 5.522 | 5.366 | 5.194 | 5.058 | 4.92 | 4.741 | 3.825 | 2.333 | 1.281 | 0.319 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NPg Best View | 12.532 | 12.124 | 10.164 | 9.541 | 9.088 | 8.693 | 8.223 | 6.044 | 0.32 | -3.82 | -7.899 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NPg Best View | 23.294 | 13.78 | 2.638 | 1.954 | 1.41 | 0.919 | 0.331 | -2.133 | -7.074 | -10.746 | -14.412 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NPg Best View | 0.835 | 0.105 | -0.57 | -3.026 | -3.547 | -3.998 | -4.549 | -6.955 | -12.403 | -16.585 | -20.762 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NPg Best View | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NPg Best View | 3.307 | 3.181 | 2.983 | 2.744 | 2.556 | 2.374 | 2.16 | 0.933 | -2.013 | -4.385 | -6.714 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NPg Best View | 12.117 | 11.335 | 10.967 | 10.498 | 10.132 | 9.809 | 9.44 | 7.781 | 3.779 | 0.842 | -2.067 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 5.948 | 4.336 | 4.181 | 3.945 | 3.818 | 3.722 | 3.575 | 2.773 | -0.513 | -2.995 | -5.472 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 27.967 | 27.997 | 28.024 | 28.049 | 28.072 | 28.094 | 28.112 | 28.193 | 28.257 | 28.31 | 28.358 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NPg Best View | 20.025 | 18.997 | 18.591 | 18.139 | 17.805 | 17.52 | 17.193 | 15.793 | 12.165 | 9.297 | 6.413 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NPg Best View | 8.53 | 8.027 | 8.23 | 8.33 | 8.343 | 8.254 | 8.035 | 6.348 | 4.359 | 3.538 | 3.012 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NPg Best View | 3.242 | 3.207 | 3.229 | 3.239 | 3.237 | 3.222 | 3.188 | 2.973 | 2.624 | 2.242 | 1.854 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NPg Best View | 13.887 | 13.571 | 13.072 | 12.543 | 12.196 | 11.924 | 11.606 | 10.148 | 4.907 | 0.585 | -3.801 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NPg Best View | 2.413 | 2.153 | 1.762 | 1.328 | 0.932 | 0.528 | 0.046 | -2.428 | -6.595 | -9.778 | -12.775 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NPg Best View | 7.857 | 6.95 | 6.62 | 6.272 | 5.971 | 5.698 | 5.372 | 3.928 | 1.789 | 0.321 | -1.142 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 23.611 | 23.098 | 22.601 | 22.037 | 21.579 | 21.153 | 20.655 | 18.245 | 12.133 | 7.25 | 2.582 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NPg Best View | 11.27 | 10.981 | 10.445 | 9.829 | 9.406 | 9.073 | 8.681 | 6.981 | 1.977 | -1.794 | -5.688 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NPg Best View | 11.202 | 10.892 | 10.395 | 9.855 | 9.45 | 9.101 | 8.698 | 6.77 | 1.498 | -2.742 | -6.965 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NPg Best View | 12.977 | 12.854 | 12.995 | 13.106 | 13.229 | 13.351 | 13.449 | 13.826 | 13.099 | 12.524 | 11.908 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NPg Best View | 6.108 | 5.748 | 5.23 | 4.698 | 4.255 | 3.827 | 3.33 | 0.97 | -4.819 | -9.667 | -14.344 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NPg Best View | 8.627 | 7.094 | 7.04 | 6.945 | 6.867 | 6.771 | 6.62 | 5.779 | 3.555 | 1.872 | 0.335 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NPg Best View | 7.849 | 7.163 | 6.799 | 6.396 | 6.047 | 5.728 | 5.363 | 3.754 | -0.836 | -4.632 | -8.301 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NPg Best View | 31.102 | 31.112 | 31.121 | 31.128 | 31.136 | 31.144 | 31.151 | 31.181 | 31.178 | 31.176 | 31.17 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NPg Best View | 10.328 | 10.334 | 10.278 | 10.199 | 25.563 | 25.551 | 25.527 | 25.405 | 23.845 | 22.548 | 21.209 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NPg Best View | 7.685 | 6.042 | 20.602 | 20.134 | 19.745 | 19.374 | 18.925 | 16.969 | 11.886 | 7.854 | 4.047 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NPg Best View | 9.035 | 8.817 | 8.499 | 8.14 | 7.798 | 7.455 | 7.053 | 4.944 | 1.366 | -1.44 | -4.157 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NPg Best View | 11.714 | 11.632 | 11.503 | 11.37 | 11.262 | 11.158 | 11.031 | 10.494 | 9.285 | 8.331 | 7.471 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NPg Best View | 19.977 | 19.485 | 19.407 | 19.305 | 19.239 | 19.182 | 19.098 | 18.685 | 16.165 | 14.027 | 11.986 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NPg Best View | 10.765 | 10.425 | 9.885 | 9.348 | 8.935 | 8.549 | 8.065 | 5.688 | 0.854 | -2.632 | -5.987 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NPg Best View | 11.967 | 11.602 | 11.282 | 10.916 | 10.642 | 10.408 | 10.138 | 8.935 | 4.608 | 0.985 | -2.575 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NPg Best View | 10.986 | 10.449 | 10.111 | 9.734 | 9.434 | 9.156 | 8.82 | 7.28 | 3.395 | 0.277 | -2.69 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NPg Best View | 13.931 | 13.931 | 13.893 | 13.837 | 13.808 | 13.787 | 13.758 | 13.584 | 12.547 | 11.74 | 10.944 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NPg Best View | 14.122 | 14.123 | 14.086 | 14.028 | 13.979 | 13.933 | 13.874 | 13.518 | 12.354 | 11.508 | 10.704 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NPg Best View | 18.69 | 18.601 | 18.444 | 18.27 | 18.134 | 18.016 | 17.874 | 17.187 | 15.792 | 14.793 | 13.799 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NPg Best View | 18.893 | 18.8 | 18.64 | 18.455 | 18.32 | 18.21 | 18.082 | 17.468 | 15.696 | 14.349 | 12.993 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NPg Best View | 12.176 | 11.992 | 11.683 | 11.352 | 11.053 | 10.768 | 10.442 | 9.032 | 4.583 | 0.693 | -2.982 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 22.233 | 21.909 | 21.431 | 20.971 | 20.637 | 20.349 | 19.998 | 18.341 | 14.821 | 12.228 | 9.594 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NPg Best View | 26.986 | 26.072 | 25.976 | 25.879 | 25.768 | 25.638 | 25.474 | 24.907 | 24.472 | 24.13 | 23.812 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NPg Best View | 5.602 | 5.191 | 5.161 | 5.126 | 5.097 | 5.073 | 5.042 | 4.902 | 4.413 | 4.023 | 3.644 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NPg Best View | 11.223 | 11.295 | 11.312 | 11.305 | 11.314 | 11.327 | 11.324 | 11.275 | 9.561 | 8.122 | 6.767 | Primary

## Generation Headroom
Version 1.1 | [7 empty] | Generation Headroom Capacity (MW)
| Please filter on your selected substation | [6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2035 | 2040 | 2045 | 2050
Licence Area | Substation Name | Voltage (kV) | Supply Voltage (kV) | BSP Group | GSP | Substation Location | Scenario Name | [11 empty] | Bulk Supply Point or Primary
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Consumer Transformation | 27.415 | 27.294 | 74.953 | 74.445 | 74.297 | 74.095 | 73.793 | 71.733 | 63.886 | 58.126 | 52.782 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Consumer Transformation | 37.242 | 35.553 | 33.144 | 30.299 | 28.209 | 26.007 | 23.336 | -5.46 | -28.645 | -45.954 | -61.996 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Consumer Transformation | 138.656 | 137.578 | 136.017 | 134.331 | 133.161 | 131.84 | 130.1 | 120.901 | 98.12 | 81.465 | 66.9 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Consumer Transformation | 19.081 | 17.092 | 14.169 | 10.661 | 8.161 | 5.554 | 2.376 | -11.864 | -41.35 | -64.372 | -86.353 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 68.992 | 67.956 | 66.349 | 64.4 | 63.033 | 61.588 | 59.776 | 51.592 | 35.44 | 23.604 | 12.836 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Consumer Transformation | 16.932 | 17.106 | 17.119 | 16.987 | 17.028 | 16.985 | 16.831 | 14.946 | 8.5 | 4.067 | 0.321 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Consumer Transformation | 31.546 | 30.118 | 28.172 | 25.927 | 24.052 | 22.09 | 19.737 | 8.843 | -9.273 | -23.176 | -35.881 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Consumer Transformation | 44.715 | 43.214 | 41.084 | 38.744 | 37.221 | 35.581 | 33.48 | 23.629 | 2.928 | -12.047 | -25.795 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 53.412 | 49.594 | 48.85 | 47.956 | 47.353 | 46.627 | 38.291 | 12.044 | -1.093 | -10.145 | -17.833 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Consumer Transformation | 72.476 | 71.844 | 70.749 | 69.362 | 68.476 | 67.562 | 66.412 | 61.53 | 48.392 | 37.965 | 28.019 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Consumer Transformation | 51.343 | 50.452 | 48.97 | 47.123 | 45.901 | 44.57 | 42.857 | 7.795 | -9.411 | -21.886 | -33.261 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Consumer Transformation | 113.495 | 109.983 | 105.107 | 99.488 | 95.086 | 90.414 | 84.749 | 33.424 | -19.224 | -58.558 | -93.681 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Consumer Transformation | 91.413 | 90.938 | 90.231 | 89.374 | 88.798 | 88.186 | 87.427 | 83.968 | 77.119 | 71.872 | 66.812 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Consumer Transformation | 42.513 | 41.643 | 40.333 | 38.654 | 37.409 | 36.05 | 34.426 | 25.56 | 0.389 | -20.331 | -39.621 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Consumer Transformation | 44.084 | 41.971 | 39.049 | 35.586 | 32.816 | 29.845 | 26.272 | 8.203 | -22.395 | -44.503 | -64.051 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Consumer Transformation | 64.919 | 64.809 | 64.416 | 63.805 | 63.651 | 63.457 | 63.149 | 61.418 | 51.846 | 44.455 | 37.45 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 44.694 | 44.43 | 43.961 | 43.347 | 42.933 | 42.479 | 41.883 | 39.048 | 32.523 | 27.632 | 23.135 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Consumer Transformation | 17.338 | 16.455 | 15.069 | 13.389 | 12.288 | 11.095 | 9.59 | 2.345 | -10.474 | -19.248 | -27.218 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Consumer Transformation | 58.445 | 56.653 | 53.94 | 50.712 | 48.684 | 46.566 | 43.943 | 32.293 | 8.749 | -8.529 | -24.78 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Consumer Transformation | 58.333 | 57.514 | 56.174 | 93.47 | 92.126 | 90.681 | 88.874 | 80.168 | 64.4 | 52.842 | 42.602 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Consumer Transformation | 48.869 | 48.01 | 46.49 | 44.499 | 43.111 | 41.614 | 39.677 | 30.514 | 7.428 | -10.544 | -27.171 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Consumer Transformation | 65.967 | 64.617 | 62.686 | 60.446 | 58.723 | 56.909 | 54.703 | 44.504 | 26.597 | 13.509 | 1.765 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Consumer Transformation | 91.063 | 90.557 | 89.71 | 88.641 | 87.921 | 87.173 | 86.233 | 82.168 | 72.315 | 64.657 | 57.525 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Consumer Transformation | 84.852 | 84.115 | 83.083 | 81.862 | 80.847 | 79.786 | 78.51 | 72.732 | 64.198 | 58.046 | 52.539 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Consumer Transformation | 97.219 | 96.393 | 95.267 | 94.003 | 93.077 | 92.111 | 90.936 | 85.573 | 75.208 | 67.42 | 60.212 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Consumer Transformation | 66.73 | 66.335 | 65.735 | 64.94 | 64.105 | 63.086 | 61.808 | 53.17 | 40.995 | 33.78 | 29.001 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Consumer Transformation | 59.814 | 58.949 | 57.727 | 56.282 | 55.215 | 54.077 | 52.711 | 45.956 | 33.167 | 23.455 | 14.453 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 69.241 | 69.379 | 69.445 | 69.487 | 69.606 | 69.699 | 69.733 | 69.733 | 65.498 | 62.086 | 58.958 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 38.457 | 33.518 | 28.251 | 24.305 | 21.392 | 18.398 | 14.783 | -1.062 | -31.867 | -55.007 | -75.955 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Consumer Transformation | 49.921 | 49.66 | 49.129 | 48.438 | 47.951 | 47.349 | 46.526 | 41.353 | 26.965 | 16.541 | 7.813 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Consumer Transformation | 61.354 | 59.391 | 57.034 | 54.921 | 53.213 | 51.429 | 49.178 | 39.398 | 21.125 | 7.426 | -4.717 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Consumer Transformation | 48.823 | 47.331 | 45.024 | 42.271 | 40.315 | 38.266 | 35.698 | 24.398 | 0.659 | -17.241 | -33.641 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Consumer Transformation | 139.027 | 138.943 | 138.548 | 137.89 | 137.524 | 136.982 | 136.181 | 110.374 | 91.802 | 78.825 | 68.171 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Consumer Transformation | 60.147 | 60.129 | 59.939 | 59.598 | 59.391 | 59.108 | 58.707 | 55.834 | 48.12 | 42.25 | 37.058 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Consumer Transformation | 68.454 | 67.277 | 65.708 | 64.086 | 62.978 | 61.816 | 60.357 | 53.973 | 40.359 | 30.285 | 20.969 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Consumer Transformation | 27.569 | 27.63 | 27.584 | 27.434 | 27.365 | 27.272 | 27.113 | 26.109 | 19.56 | 14.091 | 9.092 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 58.124 | 57.665 | 57.047 | 56.287 | 55.472 | 54.537 | 53.408 | 46.546 | 36.641 | 29.96 | 24.897 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Consumer Transformation | 51.216 | 49.512 | 47.214 | 44.821 | 43.209 | 41.517 | 39.39 | 30.056 | 11.922 | -1.224 | -13.316 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 9.371 | 9.08 | 8.443 | 7.552 | 7.195 | 6.763 | 6.169 | 2.54 | -11.127 | -21.717 | -31.593 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Consumer Transformation | 40.728 | 40.732 | 40.734 | 40.732 | 106.929 | 106.922 | 106.912 | 106.83 | 106.701 | 106.554 | 106.405 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 28.997 | 28.112 | 27.091 | 25.961 | 24.909 | 23.781 | 22.536 | 15.402 | 5.503 | -2.486 | -9.509 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Consumer Transformation | 54.483 | 53.762 | 52.858 | 51.754 | 50.693 | 49.494 | 48.107 | 39.407 | 25.147 | 14.756 | 6.059 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Consumer Transformation | 80.836 | 80.358 | 79.738 | 79.021 | 78.377 | 77.714 | 76.96 | 73.419 | 67.877 | 63.352 | 59.208 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Consumer Transformation | 30.311 | 28.925 | 26.765 | 24.163 | 22.149 | 20.012 | 17.287 | 4.901 | -21.585 | -41.625 | -59.513 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Consumer Transformation | 53.698 | 52.53 | 50.705 | 48.502 | 46.96 | 45.308 | 43.216 | 33.412 | 12.73 | -2.705 | -16.699 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Consumer Transformation | 53.638 | 52.831 | 51.396 | 49.54 | 48.391 | 47.106 | 45.43 | 36.802 | 18.566 | 5.916 | -5.353 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 33.714 | 31.842 | 28.955 | 25.47 | 23.111 | 20.587 | 17.409 | 2.633 | -23.46 | -41.807 | -58.817 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Consumer Transformation | 72.557 | 71.83 | 70.817 | 69.572 | 68.811 | 67.985 | 67.025 | 61.63 | 47.937 | 37.102 | 26.732 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Consumer Transformation | 35.61 | 33.33 | 30.2 | 26.65 | 24.15 | 21.524 | 18.37 | 3.646 | -21.321 | -39.12 | -55.51 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Consumer Transformation | 63.873 | 61.109 | 57.406 | 53.288 | 49.877 | 46.328 | 42.068 | 22.78 | -10.611 | -35.48 | -57.804 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Consumer Transformation | 57.045 | 54.916 | 52.148 | 49.305 | 47.11 | 44.839 | 42.058 | 30.144 | 10.604 | -3.331 | -15.765 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Consumer Transformation | 52.615 | 51.203 | 49.276 | 47.041 | 45.232 | 43.364 | 41.126 | 31.217 | 14.556 | 1.502 | -10.828 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Consumer Transformation | 59.155 | 58.552 | 57.471 | 56.089 | 55.034 | 53.914 | 52.472 | 45.904 | 29.438 | 16.673 | 5.285 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Falling Short | 26.957 | 26.939 | 74.859 | 74.702 | 74.465 | 74.157 | 73.813 | 71.775 | 69.345 | 67.572 | 66.604 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Falling Short | 37.021 | 35.978 | 34.711 | 33.198 | 31.36 | 29.23 | 27.119 | 0.992 | -7.343 | -13.111 | -17.029 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Falling Short | 138.576 | 138.045 | 137.386 | 136.571 | 135.458 | 134.075 | 132.646 | 125.479 | 118.776 | 114.474 | 112.49 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Falling Short | 18.631 | 17.424 | 15.921 | 14.1 | 11.872 | 9.29 | 6.77 | -4.444 | -13.466 | -19.842 | -24.562 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 69.051 | 68.583 | 67.933 | 67.097 | 66.005 | 64.686 | 63.392 | 57.778 | 53.598 | 51.151 | 49.897 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Falling Short | 16.192 | 16.171 | 16.089 | 15.933 | 15.696 | 15.377 | 14.994 | 12.334 | 8.781 | 5.892 | 4.122 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Falling Short | 31.289 | 30.194 | 28.916 | 27.444 | 25.706 | 23.727 | 21.773 | 12.748 | 5.14 | -0.467 | -4.633 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Falling Short | 44.836 | 44.24 | 43.488 | 42.567 | 41.335 | 39.832 | 38.347 | 31.574 | 26.099 | 22.819 | 21.133 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 52.786 | 49.078 | 48.621 | 48.049 | 47.317 | 46.433 | 38.062 | 12.053 | 5.475 | 0.49 | -2.345 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Falling Short | 72.27 | 71.947 | 71.477 | 70.856 | 70.049 | 69.084 | 68.154 | 64.35 | 61.876 | 60.431 | 59.433 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Falling Short | 51.1 | 50.727 | 50.168 | 49.405 | 48.379 | 47.118 | 45.856 | 13.111 | 8.133 | 5.032 | 3.469 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Falling Short | 113.65 | 111.533 | 108.969 | 105.914 | 102.148 | 97.732 | 93.312 | 48.6 | 30.602 | 18.536 | 11.444 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Falling Short | 91.239 | 90.964 | 90.616 | 90.187 | 89.659 | 89.044 | 88.44 | 85.686 | 83.358 | 81.667 | 80.398 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Falling Short | 41.241 | 40.194 | 38.988 | 37.583 | 35.959 | 34.145 | 32.283 | 22.627 | 12.771 | 4.59 | -1.949 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Falling Short | 43.855 | 42.43 | 40.723 | 38.689 | 36.235 | 33.387 | 30.491 | 16.109 | 2.493 | -7.267 | -13.202 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Falling Short | 64.486 | 64.504 | 64.446 | 64.296 | 64.047 | 63.719 | 63.381 | 61.669 | 59.992 | 58.882 | 58.217 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 44.584 | 44.467 | 44.283 | 44.023 | 43.669 | 43.235 | 42.804 | 40.802 | 39.15 | 38.138 | 37.577 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Falling Short | 17.094 | 16.765 | 16.277 | 15.626 | 14.761 | 13.7 | 12.63 | 7.537 | 2.947 | -0.036 | -1.494 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Falling Short | 58.519 | 57.805 | 56.821 | 55.568 | 53.951 | 52.005 | 50.115 | 42.08 | 36.258 | 32.873 | 31.112 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Falling Short | 57.975 | 57.374 | 56.584 | 94.592 | 93.347 | 91.873 | 90.394 | 83.416 | 77.348 | 73.081 | 70.417 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Falling Short | 48.568 | 48.148 | 47.517 | 46.644 | 45.484 | 44.082 | 42.696 | 36.431 | 31.57 | 28.746 | 27.231 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Falling Short | 65.925 | 65.095 | 64.077 | 62.861 | 61.361 | 59.602 | 57.863 | 49.955 | 43.366 | 38.796 | 35.864 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Falling Short | 90.985 | 90.765 | 90.433 | 89.987 | 89.401 | 88.696 | 88.016 | 85.226 | 83.427 | 82.491 | 81.991 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Falling Short | 84.654 | 84.098 | 83.429 | 82.639 | 81.698 | 80.62 | 79.556 | 74.667 | 70.69 | 67.936 | 65.958 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Falling Short | 97.278 | 96.837 | 96.306 | 95.68 | 94.906 | 94.002 | 93.114 | 89.148 | 86.043 | 84.066 | 82.84 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Falling Short | 66.425 | 65.999 | 65.476 | 64.825 | 64.008 | 63.009 | 61.871 | 54.725 | 45.924 | 39.317 | 36.181 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Falling Short | 59.186 | 58.414 | 57.526 | 56.507 | 55.318 | 53.976 | 52.623 | 45.933 | 39.524 | 34.346 | 30.297 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 68.899 | 68.975 | 69.031 | 69.056 | 69.032 | 68.97 | 68.9 | 68.456 | 67.913 | 67.539 | 67.286 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 41.516 | 39.23 | 37.093 | 35.159 | 32.746 | 29.902 | 27.147 | 15.705 | 8.065 | 3.627 | 0.905 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Falling Short | 49.616 | 49.438 | 49.167 | 48.777 | 48.216 | 47.497 | 46.707 | 42.263 | 37.452 | 34.181 | 32.797 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Falling Short | 62.296 | 61.337 | 60.319 | 59.248 | 57.872 | 56.223 | 54.635 | 48.1 | 43.852 | 41.532 | 40.249 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Falling Short | 48.863 | 48.157 | 47.197 | 45.974 | 44.387 | 42.476 | 40.628 | 32.829 | 27.389 | 24.294 | 22.581 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Falling Short | 138.486 | 138.451 | 138.313 | 138.021 | 137.541 | 136.88 | 136.095 | 111.253 | 104.486 | 99.778 | 97.983 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Falling Short | 59.165 | 58.801 | 58.366 | 57.847 | 57.233 | 56.529 | 55.772 | 51.408 | 46.381 | 41.936 | 38.433 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Falling Short | 68.778 | 68.262 | 67.657 | 66.956 | 66.042 | 64.943 | 63.877 | 59.379 | 56.222 | 54.434 | 53.43 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Falling Short | 27.291 | 27.293 | 27.252 | 27.155 | 27.003 | 26.809 | 26.605 | 25.534 | 24.512 | 23.867 | 23.467 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Falling Short | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Falling Short | 57.537 | 56.865 | 56.11 | 55.252 | 54.26 | 53.131 | 51.918 | 45.049 | 37.309 | 30.985 | 26.76 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Falling Short | 51.705 | 50.954 | 50.064 | 49.037 | 47.705 | 46.102 | 44.541 | 37.971 | 33.379 | 30.751 | 29.311 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 8.849 | 8.749 | 8.553 | 8.247 | 7.815 | 7.272 | 6.694 | 3.566 | 0.359 | -1.801 | -2.904 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Falling Short | 40.598 | 40.54 | 40.479 | 40.415 | 106.547 | 106.477 | 106.404 | 106.006 | 105.563 | 105.089 | 104.603 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 27.387 | 25.785 | 24.119 | 22.38 | 20.552 | 18.631 | 16.643 | 5.993 | -5.477 | -16.403 | -26.265 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Falling Short | 53.56 | 52.548 | 51.452 | 50.235 | 48.882 | 47.387 | 45.782 | 36.508 | 25.719 | 16.543 | 9.952 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Falling Short | 80.387 | 79.766 | 79.089 | 78.35 | 77.538 | 76.659 | 75.783 | 71.572 | 67.617 | 64.031 | 60.762 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Falling Short | 30.374 | 29.658 | 28.684 | 27.437 | 25.805 | 23.836 | 21.912 | 13.532 | 7.333 | 3.765 | 1.87 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Falling Short | 53.648 | 53.117 | 52.378 | 51.416 | 50.152 | 48.62 | 47.104 | 40.269 | 34.882 | 31.643 | 29.973 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Falling Short | 53.194 | 52.918 | 52.439 | 51.737 | 50.759 | 49.529 | 48.264 | 41.941 | 35.862 | 31.928 | 30.2 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 33.162 | 32.356 | 31.223 | 29.754 | 27.849 | 25.54 | 23.259 | 12.642 | 3.285 | -2.923 | -6.463 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Falling Short | 71.944 | 71.337 | 70.65 | 69.864 | 68.97 | 67.981 | 66.955 | 61.398 | 55.352 | 50.307 | 46.371 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Falling Short | 35.417 | 34.141 | 32.611 | 30.82 | 28.642 | 26.111 | 23.596 | 11.849 | 1.485 | -5.898 | -10.783 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Falling Short | 64.009 | 62.23 | 60.142 | 57.722 | 54.793 | 51.405 | 48.076 | 33.068 | 21.163 | 13.381 | 8.25 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Falling Short | 57.724 | 56.669 | 55.433 | 54.022 | 52.238 | 50.117 | 48.06 | 39.503 | 33.639 | 30.268 | 28.447 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Falling Short | 52.454 | 51.411 | 50.197 | 48.803 | 47.166 | 45.321 | 43.524 | 35.531 | 29.125 | 24.366 | 20.508 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Falling Short | 58.944 | 58.591 | 58.065 | 57.355 | 56.411 | 55.26 | 54.131 | 49.211 | 45.601 | 43.507 | 42.376 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Leading the Way | 27.416 | 27.257 | 74.864 | 74.318 | 74.137 | 73.882 | 73.28 | 64.455 | 57.545 | 52.889 | 54.054 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Leading the Way | 37.317 | 35.588 | 33.097 | 30.214 | 28.174 | 25.986 | 22.757 | -21.502 | -42.675 | -57.536 | -57.505 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Leading the Way | 138.741 | 137.627 | 135.935 | 134.142 | 132.921 | 131.499 | 129.036 | 102.375 | 82.158 | 68.399 | 70.834 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Leading the Way | 19.153 | 17.135 | 14.137 | 10.61 | 8.222 | 5.696 | 1.85 | -33.661 | -61.089 | -81.402 | -81.208 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 69.056 | 68.028 | 66.392 | 64.433 | 63.125 | 61.714 | 59.473 | 39.727 | 25.262 | 15.497 | 16.825 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Leading the Way | 16.915 | 17.042 | 16.991 | 16.793 | 16.761 | 16.617 | 16.177 | 9.162 | 3.749 | 0.367 | 1.317 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Leading the Way | 31.585 | 30.144 | 28.143 | 25.85 | 24.013 | 22.059 | 19.31 | -2.448 | -19.131 | -31.317 | -32.521 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Leading the Way | 44.835 | 43.339 | 41.148 | 38.793 | 37.344 | 35.754 | 33.177 | 7.68 | -10.807 | -23.074 | -20.702 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 53.427 | 49.55 | 48.696 | 47.698 | 46.975 | 46.076 | 37.323 | 2.252 | -9.133 | -16.588 | -16.049 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Leading the Way | 72.506 | 71.868 | 70.742 | 69.332 | 68.505 | 67.635 | 66.053 | 50.519 | 38.287 | 29.241 | 30.342 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Leading the Way | 51.37 | 50.448 | 48.898 | 47.008 | 45.816 | 44.49 | 42.307 | -5.542 | -20.977 | -31.293 | -29.616 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Leading the Way | 113.61 | 110.026 | 104.928 | 99.1 | 94.671 | 89.854 | 82.694 | -3.371 | -50.89 | -84.33 | -84.066 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Leading the Way | 91.429 | 90.948 | 90.225 | 89.367 | 88.822 | 88.237 | 87.336 | 78.941 | 72.64 | 68.112 | 68.227 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Leading the Way | 42.515 | 41.544 | 40.097 | 38.323 | 37.034 | 35.593 | 33.268 | 5.565 | -17.781 | -36.278 | -37.073 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Leading the Way | 44.096 | 41.906 | 38.825 | 35.202 | 32.332 | 29.171 | 24.782 | -11.481 | -38.953 | -57.864 | -59.158 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Leading the Way | 64.941 | 64.8 | 64.367 | 63.746 | 63.605 | 63.412 | 62.788 | 51.951 | 43.46 | 37.492 | 39.51 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 44.705 | 44.424 | 43.93 | 43.308 | 42.921 | 42.491 | 41.761 | 33.757 | 27.849 | 23.74 | 24.51 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Leading the Way | 17.361 | 16.448 | 15.005 | 13.283 | 12.185 | 10.964 | 9.073 | -6.802 | -18.119 | -25.169 | -24.259 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Leading the Way | 58.547 | 56.784 | 54.051 | 50.811 | 48.878 | 46.81 | 43.454 | 14.75 | -6.349 | -20.484 | -18.519 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Leading the Way | 58.348 | 57.507 | 56.103 | 93.331 | 91.989 | 90.508 | 88.254 | 69.323 | 55.144 | 45.399 | 45.648 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Leading the Way | 48.908 | 48.005 | 46.402 | 44.367 | 43.064 | 41.64 | 39.112 | 11.396 | -9.85 | -25.31 | -23.332 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Leading the Way | 66.025 | 64.673 | 62.693 | 60.411 | 58.709 | 56.876 | 54.21 | 32.627 | 16.547 | 5.532 | 5.805 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Leading the Way | 91.084 | 90.573 | 89.705 | 88.622 | 87.95 | 87.239 | 85.997 | 74.188 | 65.188 | 58.765 | 59.733 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Leading the Way | 84.923 | 84.196 | 83.153 | 81.927 | 80.943 | 79.891 | 78.447 | 67.877 | 60.124 | 54.848 | 54.496 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Leading the Way | 97.276 | 96.453 | 95.296 | 94.012 | 93.114 | 92.158 | 90.727 | 78.167 | 68.698 | 62.015 | 62.263 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Leading the Way | 66.667 | 66.192 | 65.45 | 64.462 | 63.384 | 62.041 | 60.245 | 46.516 | 36.643 | 31.279 | 30.553 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Leading the Way | 59.833 | 58.936 | 57.657 | 56.174 | 55.097 | 53.924 | 52.245 | 37.374 | 25.731 | 17.307 | 16.602 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 69.261 | 69.38 | 69.415 | 69.448 | 69.576 | 69.678 | 69.6 | 64.896 | 61.093 | 58.25 | 59.656 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 38.959 | 34.238 | 28.868 | 24.832 | 22.002 | 19.041 | 14.452 | -22.546 | -50.537 | -69.882 | -67.926 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Leading the Way | 49.92 | 49.593 | 48.94 | 48.12 | 47.529 | 46.777 | 45.388 | 29.246 | 16.699 | 8.234 | 9.782 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Leading the Way | 61.56 | 59.686 | 57.302 | 55.183 | 53.583 | 51.889 | 49.194 | 26.531 | 10.131 | -1.099 | 0.641 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Leading the Way | 48.901 | 47.407 | 45.044 | 42.257 | 40.414 | 38.449 | 35.229 | 6.315 | -15.146 | -30.011 | -27.874 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Leading the Way | 138.997 | 138.79 | 138.213 | 137.383 | 136.837 | 136.051 | 134.54 | 94.246 | 78.368 | 68.07 | 70.521 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Leading the Way | 60.137 | 60.082 | 59.836 | 59.437 | 59.172 | 58.806 | 58.126 | 49.84 | 43.033 | 38.106 | 38.031 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Leading the Way | 68.567 | 67.414 | 65.815 | 64.195 | 63.153 | 62.042 | 60.28 | 43.579 | 31.291 | 22.841 | 24.28 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Leading the Way | 27.569 | 27.601 | 27.516 | 27.344 | 27.279 | 27.183 | 26.802 | 19.591 | 13.53 | 8.758 | 9.696 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Leading the Way | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Leading the Way | 58.089 | 57.574 | 56.86 | 55.976 | 55.024 | 53.9 | 52.43 | 41.387 | 32.922 | 27.43 | 25.962 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Leading the Way | 51.369 | 49.716 | 47.391 | 44.995 | 43.474 | 41.844 | 39.242 | 16.826 | 0.699 | -9.93 | -7.993 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 9.391 | 9.057 | 8.344 | 7.384 | 7.004 | 6.524 | 5.407 | -9.834 | -22.138 | -30.961 | -29.44 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Leading the Way | 40.728 | 40.732 | 40.734 | 40.733 | 106.93 | 106.924 | 106.914 | 106.813 | 106.686 | 106.541 | 106.413 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 28.967 | 28.049 | 26.972 | 25.766 | 24.634 | 23.397 | 21.877 | 11.419 | 2.434 | -4.635 | -8.575 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Leading the Way | 54.432 | 53.629 | 52.596 | 51.343 | 50.098 | 48.651 | 46.84 | 31.445 | 18.888 | 9.902 | 7.24 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Leading the Way | 80.842 | 80.36 | 79.727 | 78.995 | 78.352 | 77.68 | 76.807 | 70.557 | 65.386 | 61.29 | 60.029 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Leading the Way | 30.395 | 28.997 | 26.76 | 24.118 | 22.217 | 20.171 | 16.789 | -15.424 | -39.236 | -55.792 | -53.172 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Leading the Way | 53.72 | 52.519 | 50.618 | 48.36 | 46.872 | 45.249 | 42.578 | 17.546 | -1.022 | -13.753 | -11.955 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Leading the Way | 53.656 | 52.806 | 51.285 | 49.353 | 48.172 | 46.803 | 44.548 | 22.634 | 6.681 | -3.441 | -1.519 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 33.748 | 31.799 | 28.792 | 25.245 | 22.951 | 20.447 | 16.576 | -16.174 | -39.658 | -54.869 | -53.209 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Leading the Way | 72.543 | 71.731 | 70.622 | 69.321 | 68.517 | 67.626 | 66.267 | 51.009 | 38.401 | 28.889 | 28.221 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Leading the Way | 35.682 | 33.348 | 30.11 | 26.496 | 24.012 | 21.343 | 17.5 | -12.803 | -35.137 | -49.901 | -49.85 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Leading the Way | 64.097 | 61.335 | 57.534 | 53.363 | 50.046 | 46.524 | 41.497 | 1.211 | -29.323 | -50.837 | -51.057 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Leading the Way | 57.243 | 55.186 | 52.385 | 49.513 | 47.405 | 45.172 | 41.878 | 17.455 | -0.047 | -11.58 | -10.373 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Leading the Way | 52.683 | 51.275 | 49.326 | 47.099 | 45.389 | 43.607 | 41.119 | 20.741 | 5.223 | -6.357 | -7.281 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Leading the Way | 59.187 | 58.566 | 57.434 | 56.013 | 55.005 | 53.907 | 51.946 | 32.562 | 17.679 | 7.033 | 8.801 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - System Transformation | 27.011 | 26.902 | 74.676 | 74.36 | 74.035 | 73.646 | 73.167 | 70.081 | 64.753 | 58.601 | 50.168 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - System Transformation | 36.528 | 34.904 | 32.864 | 30.579 | 28.265 | 25.827 | 23.218 | -6.294 | -22.088 | -39.282 | -62.234 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - System Transformation | 137.914 | 136.738 | 135.366 | 134.002 | 132.573 | 130.976 | 129.16 | 118.936 | 102.494 | 86.025 | 64.598 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - System Transformation | 18.152 | 16.149 | 13.582 | 10.681 | 7.846 | 4.891 | 1.744 | -13.639 | -34.868 | -58.064 | -89.324 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 68.6 | 67.589 | 66.229 | 64.677 | 63.18 | 61.604 | 59.912 | 51.586 | 40.837 | 29.325 | 13.43 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - System Transformation | 16.451 | 16.481 | 16.409 | 16.238 | 16.017 | 15.697 | 15.262 | 11.84 | 6.085 | 0.495 | -6.217 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - System Transformation | 31.029 | 29.551 | 27.744 | 25.742 | 23.684 | 21.532 | 19.264 | 7.923 | -5.809 | -19.97 | -38.059 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - System Transformation | 43.999 | 42.53 | 40.777 | 38.994 | 37.256 | 35.4 | 33.359 | 22.967 | 8.681 | -6.124 | -25.985 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 52.815 | 48.941 | 48.273 | 47.529 | 46.683 | 45.698 | 37.131 | 9.638 | -1.265 | -11.333 | -22.933 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - System Transformation | 72.082 | 71.423 | 70.469 | 69.342 | 68.284 | 67.187 | 66.029 | 60.457 | 52.116 | 41.823 | 26.592 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - System Transformation | 50.774 | 49.88 | 48.631 | 47.177 | 45.744 | 44.201 | 42.5 | 6.784 | -5.164 | -17.62 | -34.489 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - System Transformation | 112.332 | 108.88 | 104.651 | 100.011 | 95.275 | 90.247 | 84.851 | 33.095 | -3.804 | -41.816 | -91.579 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - System Transformation | 91.139 | 90.667 | 90.059 | 89.367 | 88.685 | 87.968 | 87.195 | 83.344 | 78.35 | 72.896 | 65.591 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - System Transformation | 41.577 | 40.507 | 39.17 | 37.61 | 35.951 | 34.146 | 32.146 | 20.812 | 0.258 | -21.814 | -49.767 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - System Transformation | 43.317 | 41.207 | 38.608 | 35.671 | 32.646 | 29.406 | 25.893 | 7.257 | -15.852 | -37.908 | -64.889 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - System Transformation | 64.504 | 64.362 | 64.067 | 63.667 | 63.324 | 62.929 | 62.446 | 59.599 | 53.007 | 45.301 | 34.538 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 44.492 | 44.201 | 43.786 | 43.287 | 42.803 | 42.28 | 41.692 | 38.634 | 33.686 | 28.783 | 22.371 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - System Transformation | 16.82 | 16.062 | 14.998 | 13.756 | 12.483 | 11.115 | 9.62 | 1.859 | -6.126 | -14.871 | -26.948 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - System Transformation | 57.742 | 56.105 | 53.939 | 51.496 | 49.205 | 46.823 | 44.301 | 32.056 | 17.9 | 0.828 | -24.265 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - System Transformation | 57.877 | 56.963 | 55.683 | 93.155 | 91.611 | 89.959 | 88.173 | 78.865 | 66.955 | 55.107 | 39.778 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - System Transformation | 48.327 | 47.448 | 46.149 | 44.576 | 43.02 | 41.354 | 39.52 | 29.932 | 13.834 | -3.29 | -26.884 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - System Transformation | 65.472 | 64.078 | 62.331 | 60.407 | 58.5 | 56.494 | 54.362 | 43.757 | 30.754 | 17.461 | 0.221 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - System Transformation | 90.821 | 90.342 | 89.642 | 88.805 | 88.001 | 87.166 | 86.281 | 82.021 | 75.847 | 68.535 | 57.856 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - System Transformation | 84.508 | 83.818 | 82.934 | 81.913 | 80.799 | 79.631 | 78.403 | 72.354 | 66.515 | 60.225 | 52.146 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - System Transformation | 96.928 | 96.153 | 95.221 | 94.225 | 93.225 | 92.18 | 91.066 | 85.594 | 78.671 | 71.171 | 61.011 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - System Transformation | 66.479 | 65.981 | 65.319 | 64.494 | 63.532 | 62.381 | 61.022 | 52.055 | 41.03 | 33.487 | 26.721 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - System Transformation | 59.22 | 58.255 | 57.075 | 55.76 | 54.424 | 53.005 | 51.469 | 43.377 | 32.892 | 22.062 | 8.664 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 68.957 | 68.989 | 68.996 | 69.005 | 68.995 | 68.95 | 68.853 | 68.056 | 64.338 | 60.474 | 55.511 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 37.342 | 32.38 | 27.901 | 24.741 | 21.605 | 18.359 | 15.002 | -0.927 | -18.985 | -41.169 | -73.27 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - System Transformation | 49.493 | 49.128 | 48.617 | 48.022 | 47.353 | 46.552 | 45.594 | 39.521 | 28.756 | 18.336 | 5.147 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - System Transformation | 60.834 | 58.776 | 56.66 | 54.836 | 53.011 | 51.107 | 49.1 | 39.519 | 27.01 | 13.861 | -4.122 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - System Transformation | 48.215 | 46.731 | 44.756 | 42.532 | 40.371 | 38.111 | 35.715 | 24.071 | 8.601 | -8.726 | -33.204 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - System Transformation | 138.465 | 138.249 | 137.872 | 137.353 | 136.746 | 135.945 | 134.897 | 107.786 | 93.121 | 80.025 | 64.445 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - System Transformation | 59.57 | 59.307 | 58.92 | 58.422 | 57.881 | 57.246 | 56.499 | 51.66 | 43.829 | 36.137 | 27.141 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - System Transformation | 68.026 | 66.831 | 65.494 | 64.209 | 62.975 | 61.682 | 60.293 | 53.654 | 44.363 | 34.367 | 20.738 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - System Transformation | 27.364 | 27.378 | 27.325 | 27.21 | 27.058 | 26.872 | 26.641 | 25.091 | 20.416 | 15.026 | 7.573 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - System Transformation | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - System Transformation | 57.78 | 57.176 | 56.442 | 55.58 | 54.573 | 53.434 | 52.156 | 44.436 | 35.345 | 28.289 | 21.72 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - System Transformation | 50.623 | 48.912 | 46.967 | 45.072 | 43.262 | 41.368 | 39.349 | 29.637 | 17.981 | 4.852 | -13.645 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 8.89 | 8.64 | 8.195 | 7.619 | 7.06 | 6.418 | 5.66 | 0.946 | -8.002 | -18.704 | -34.033 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - System Transformation | 40.663 | 40.633 | 40.598 | 40.558 | 106.713 | 106.663 | 106.609 | 106.273 | 105.838 | 105.386 | 104.936 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 28.123 | 26.813 | 25.386 | 23.855 | 22.262 | 20.565 | 18.757 | 8.364 | -3.799 | -15.643 | -28.232 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - System Transformation | 53.947 | 53.023 | 51.954 | 50.729 | 49.39 | 47.895 | 46.214 | 36.002 | 21.8 | 9.777 | -2.389 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - System Transformation | 80.566 | 79.965 | 79.26 | 78.478 | 77.674 | 76.841 | 75.976 | 71.635 | 66.574 | 61.621 | 56.147 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - System Transformation | 29.722 | 28.27 | 26.345 | 24.169 | 21.985 | 19.676 | 17.186 | 4.696 | -13.851 | -33.008 | -58.829 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - System Transformation | 53.154 | 51.983 | 50.421 | 48.648 | 46.918 | 45.079 | 43.083 | 32.888 | 18.659 | 3.628 | -16.974 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - System Transformation | 52.974 | 52.215 | 51.072 | 49.676 | 48.272 | 46.722 | 44.977 | 35.436 | 22.854 | 10.086 | -6.832 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 32.541 | 30.853 | 28.562 | 25.903 | 23.146 | 20.212 | 17.055 | 0.933 | -15.536 | -34.111 | -59.881 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - System Transformation | 71.98 | 71.257 | 70.397 | 69.421 | 68.42 | 67.336 | 66.132 | 59.217 | 49.153 | 37.671 | 22.799 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - System Transformation | 34.641 | 32.501 | 29.912 | 27.107 | 24.269 | 21.286 | 18.112 | 2.151 | -14.009 | -32.266 | -56.85 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - System Transformation | 62.95 | 60.317 | 57.155 | 53.761 | 50.158 | 46.388 | 42.427 | 23.017 | 0.777 | -23.37 | -55.388 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - System Transformation | 56.428 | 54.338 | 51.967 | 49.626 | 47.268 | 44.82 | 42.263 | 30.368 | 18.056 | 4.338 | -14.777 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - System Transformation | 52.14 | 50.667 | 48.875 | 46.897 | 44.928 | 42.895 | 40.76 | 30.48 | 17.535 | 4.107 | -13.07 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - System Transformation | 58.739 | 58.061 | 57.069 | 55.879 | 54.665 | 53.373 | 51.983 | 44.909 | 33.634 | 21.203 | 3.923 | BSP
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NPg Best View | 27.518 | 27.477 | 75.139 | 74.658 | 74.427 | 74.134 | 73.749 | 71.655 | 64.415 | 59.043 | 53.793 | BSP
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NPg Best View | 37.77 | 36.411 | 34.35 | 31.864 | 30.172 | 28.338 | 26.149 | -0.469 | -21.746 | -38.037 | -53.69 | BSP
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NPg Best View | 139.4 | 138.712 | 137.399 | 135.925 | 134.859 | 133.595 | 131.957 | 123.718 | 102.876 | 87.355 | 73.108 | BSP
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NPg Best View | 19.822 | 18.293 | 15.871 | 12.895 | 10.989 | 8.945 | 6.479 | -4.645 | -32.028 | -54.009 | -75.536 | BSP
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 69.346 | 68.553 | 67.202 | 65.536 | 64.47 | 63.312 | 61.888 | 55.496 | 40.744 | 29.619 | 19.135 | BSP
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NPg Best View | 17.316 | 17.634 | 17.747 | 17.673 | 17.73 | 17.651 | 17.403 | 15.189 | 9.458 | 5.516 | 1.841 | BSP
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NPg Best View | 31.992 | 30.849 | 29.218 | 27.303 | 25.794 | 24.173 | 22.26 | 13.309 | -3.146 | -16.175 | -28.544 | BSP
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NPg Best View | 45.312 | 44.192 | 42.348 | 40.315 | 39.034 | 37.64 | 35.93 | 28.16 | 9.136 | -4.93 | -18.291 | BSP
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 53.691 | 50.042 | 49.316 | 48.439 | 47.658 | 46.72 | 38.167 | 11.621 | 0.098 | -7.881 | -15.302 | BSP
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NPg Best View | 72.82 | 72.407 | 71.545 | 70.413 | 69.798 | 69.137 | 68.296 | 64.833 | 52.489 | 42.406 | 32.634 | BSP
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NPg Best View | 51.682 | 51.037 | 49.741 | 48.127 | 47.07 | 45.898 | 44.445 | 10.884 | -4.83 | -16.468 | -27.521 | BSP
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NPg Best View | 114.547 | 111.682 | 107.46 | 102.477 | 98.746 | 94.644 | 89.731 | 42.151 | -5.751 | -42.439 | -76.697 | BSP
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NPg Best View | 91.552 | 91.182 | 90.563 | 89.819 | 89.336 | 88.823 | 88.208 | 85.467 | 79.121 | 74.129 | 69.183 | BSP
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NPg Best View | 42.776 | 42.143 | 40.89 | 39.361 | 37.998 | 36.518 | 34.825 | 26.433 | 2.755 | -17.064 | -36.103 | BSP
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NPg Best View | 44.705 | 42.955 | 40.394 | 37.273 | 34.845 | 32.125 | 28.873 | 12.528 | -14.764 | -34.923 | -53.907 | BSP
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NPg Best View | 65.054 | 65.068 | 64.711 | 64.188 | 63.997 | 63.772 | 63.47 | 62.101 | 53.005 | 45.868 | 38.94 | BSP
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 44.855 | 44.689 | 44.306 | 43.792 | 43.47 | 43.109 | 42.644 | 40.436 | 34.356 | 29.714 | 25.331 | BSP
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NPg Best View | 17.515 | 16.791 | 15.519 | 13.989 | 12.979 | 11.866 | 10.52 | 4.308 | -7.139 | -15.137 | -22.849 | BSP
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NPg Best View | 58.952 | 57.518 | 55.213 | 52.429 | 50.894 | 49.24 | 47.219 | 38.304 | 16.808 | 0.534 | -15.312 | BSP
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NPg Best View | 58.713 | 58.131 | 57.032 | 94.583 | 93.497 | 92.274 | 90.748 | 83.417 | 69.256 | 58.589 | 48.647 | BSP
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NPg Best View | 49.323 | 48.759 | 47.528 | 45.866 | 44.815 | 43.654 | 42.183 | 35.094 | 13.467 | -3.754 | -20.073 | BSP
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NPg Best View | 66.465 | 65.421 | 63.814 | 61.901 | 60.526 | 59.023 | 57.209 | 48.853 | 32.741 | 20.604 | 9.202 | BSP
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NPg Best View | 91.255 | 90.885 | 90.196 | 89.306 | 88.788 | 88.235 | 87.546 | 84.585 | 75.385 | 68.026 | 61.034 | BSP
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NPg Best View | 85.122 | 84.554 | 83.717 | 82.705 | 81.923 | 81.079 | 80.07 | 75.444 | 67.822 | 62.134 | 56.808 | BSP
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NPg Best View | 97.75 | 97.197 | 96.332 | 95.316 | 94.642 | 93.896 | 92.967 | 88.699 | 79.197 | 71.848 | 64.808 | BSP
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NPg Best View | 67.011 | 66.712 | 66.129 | 65.285 | 64.311 | 63.054 | 61.457 | 51.865 | 41.949 | 36.286 | 31.795 | BSP
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NPg Best View | 60.173 | 59.513 | 58.449 | 57.171 | 56.214 | 55.16 | 53.903 | 47.88 | 36.156 | 27.057 | 18.258 | BSP
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NPg Best View | 69.61 | 69.917 | 70.095 | 70.231 | 70.391 | 70.514 | 70.571 | 70.736 | 66.63 | 63.278 | 60.158 | BSP
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NPg Best View | 41.045 | 37.365 | 33.123 | 29.863 | 27.656 | 25.313 | 22.513 | 10.687 | -17.591 | -39.532 | -59.889 | BSP
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NPg Best View | 50.27 | 50.222 | 49.755 | 49.134 | 48.518 | 47.758 | 46.786 | 41.588 | 28.648 | 19.114 | 10.552 | BSP
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NPg Best View | 62.692 | 61.397 | 59.707 | 58.135 | 57.079 | 55.915 | 54.417 | 47.687 | 31.092 | 18.143 | 6.344 | BSP
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NPg Best View | 49.491 | 48.424 | 46.585 | 44.329 | 42.93 | 41.416 | 39.533 | 31.226 | 9.385 | -7.618 | -23.626 | BSP
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NPg Best View | 139.516 | 139.634 | 139.32 | 138.678 | 138.196 | 137.46 | 136.407 | 109.904 | 93.211 | 81.501 | 71.054 | BSP
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NPg Best View | 60.615 | 60.807 | 60.752 | 60.531 | 60.355 | 60.056 | 59.59 | 56.652 | 49.686 | 44.301 | 39.209 | BSP
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NPg Best View | 69.052 | 68.207 | 66.942 | 65.6 | 64.783 | 63.901 | 62.804 | 58.089 | 45.536 | 35.968 | 26.879 | BSP
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NPg Best View | 27.69 | 27.832 | 27.823 | 27.732 | 27.666 | 27.575 | 27.43 | 26.611 | 20.299 | 14.954 | 9.985 | BSP
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NPg Best View | 27.81 | 27.814 | 27.817 | 27.819 | 27.821 | 27.822 | 27.823 | 27.824 | 27.824 | 27.824 | 27.824 | BSP
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NPg Best View | 58.441 | 58.125 | 57.59 | 56.884 | 56.045 | 55.022 | 53.758 | 46.58 | 38.177 | 32.491 | 27.622 | BSP
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NPg Best View | 51.994 | 50.735 | 48.849 | 46.843 | 45.634 | 44.327 | 42.705 | 35.726 | 19.168 | 6.781 | -4.975 | BSP
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 9.45 | 9.264 | 8.621 | 7.783 | 7.317 | 6.779 | 6.115 | 2.655 | -10.093 | -20.108 | -29.814 | BSP
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NPg Best View | 40.792 | 40.823 | 40.847 | 40.865 | 107.076 | 107.08 | 107.074 | 107.008 | 106.884 | 106.742 | 106.594 | BSP
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NPg Best View | 29.18 | 28.279 | 27.046 | 25.626 | 24.181 | 22.585 | 20.718 | 11.44 | 1.509 | -6.119 | -12.993 | BSP
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NPg Best View | 55.038 | 54.548 | 53.767 | 52.739 | 51.626 | 50.28 | 48.644 | 39.253 | 26.752 | 17.578 | 9.128 | BSP
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NPg Best View | 81.089 | 80.755 | 80.278 | 79.713 | 79.204 | 78.657 | 78.023 | 75.05 | 70.008 | 65.742 | 61.696 | BSP
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NPg Best View | 31.066 | 30.136 | 28.458 | 26.358 | 24.911 | 23.322 | 21.311 | 11.979 | -12.467 | -31.503 | -48.973 | BSP
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NPg Best View | 54.215 | 53.359 | 51.862 | 49.998 | 48.833 | 47.535 | 45.905 | 38.186 | 19.172 | 4.639 | -8.984 | BSP
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NPg Best View | 53.942 | 53.352 | 52.059 | 50.378 | 49.306 | 48.067 | 46.503 | 38.832 | 22.472 | 10.924 | -0.021 | BSP
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 34.518 | 33.122 | 30.745 | 27.783 | 26.006 | 24.016 | 21.517 | 9.739 | -13.727 | -30.69 | -47.193 | BSP
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NPg Best View | 72.733 | 72.118 | 71.151 | 69.966 | 69.175 | 68.301 | 67.297 | 61.967 | 49.069 | 38.732 | 28.47 | BSP
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NPg Best View | 36.311 | 34.455 | 31.758 | 28.633 | 26.58 | 24.347 | 21.685 | 9.324 | -13.165 | -29.639 | -45.572 | BSP
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NPg Best View | 64.7 | 62.473 | 59.315 | 55.755 | 52.938 | 49.947 | 46.436 | 30.71 | 0.25 | -23.11 | -44.828 | BSP
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NPg Best View | 58.112 | 56.557 | 54.421 | 52.134 | 50.618 | 48.97 | 46.931 | 38.136 | 20.726 | 7.789 | -4.243 | BSP
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NPg Best View | 53.051 | 51.922 | 50.314 | 48.425 | 47.017 | 45.544 | 43.819 | 36.083 | 20.687 | 8.242 | -3.793 | BSP
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NPg Best View | 59.619 | 59.287 | 58.492 | 57.406 | 56.672 | 55.843 | 54.757 | 49.799 | 34.535 | 22.364 | 11.214 | BSP
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Consumer Transformation | 13.035 | 12.763 | 12.518 | 12.428 | 12.41 | 12.388 | 12.352 | 12.14 | 10.539 | 9.233 | 8 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Consumer Transformation | 12.597 | 10.967 | 10.895 | 10.771 | 10.699 | 10.594 | 10.443 | 9.241 | 6.398 | 4.504 | 3.014 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Consumer Transformation | 11.561 | 11.285 | 10.914 | 10.461 | 9.991 | 9.504 | 8.935 | 6.343 | 1.786 | -1.787 | -4.935 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Consumer Transformation | 5.928 | 4.543 | 4.567 | 4.548 | 4.535 | 4.504 | 4.442 | 3.951 | 1.803 | 0.246 | -1.051 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 5.351 | 5.025 | 4.619 | 4.232 | 3.939 | 3.638 | 3.27 | 1.739 | -1.13 | -3.322 | -5.329 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 5.346 | 5.338 | 5.309 | 5.273 | 5.266 | 5.256 | 5.231 | 5.114 | 4.43 | 3.878 | 3.344 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Consumer Transformation | 10.066 | 9.573 | 8.906 | 8.14 | 7.588 | 7.022 | 6.358 | 3.433 | -1.809 | -5.773 | -9.558 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Consumer Transformation | 17.135 | 17.166 | 17.174 | 17.161 | 17.176 | 17.188 | 17.189 | 17.183 | 15.908 | 14.855 | 13.871 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Consumer Transformation | 1.402 | 1.217 | 0.948 | 0.617 | 0.316 | 0.003 | -0.372 | -2.094 | -5.939 | -9.048 | -11.844 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Consumer Transformation | 2.978 | 2.454 | 2.571 | 2.659 | 2.765 | 2.863 | 2.944 | 3.278 | 2.64 | 2.15 | 1.681 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Consumer Transformation | 12.159 | 11.937 | 11.601 | 11.195 | 10.914 | 10.622 | 10.264 | 8.691 | 5.664 | 3.353 | 1.112 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Consumer Transformation | 2.594 | 2.298 | 1.918 | 1.541 | 1.243 | 0.909 | 0.471 | -1.751 | -5.587 | -8.138 | -10.327 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Consumer Transformation | 3.091 | 3.087 | 3.074 | 3.054 | 3.039 | 3.021 | 2.996 | 2.85 | 2.511 | 2.251 | 2.016 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Consumer Transformation | 15.827 | 15.638 | 15.343 | 14.987 | 14.778 | 14.562 | 14.295 | 13.153 | 10.154 | 7.836 | 5.601 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Consumer Transformation | 12.947 | 12.484 | 12.453 | 12.404 | 12.39 | 12.372 | 12.346 | 12.198 | 11.391 | 10.706 | 10.032 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Consumer Transformation | 10.595 | 10.599 | 10.561 | 10.482 | 10.446 | 10.398 | 10.324 | 9.867 | 7.889 | 6.46 | 5.229 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Consumer Transformation | 15.623 | 15.283 | 14.802 | 14.244 | 13.816 | 13.367 | 12.826 | 10.305 | 6.43 | 3.745 | 1.373 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Consumer Transformation | 8.451 | 8.48 | 8.486 | 8.466 | 8.461 | 8.446 | 8.414 | 8.123 | 6.793 | 5.799 | 4.978 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Consumer Transformation | 6.686 | 6.57 | 6.392 | 6.158 | 6.002 | 5.837 | 5.645 | 4.663 | 1.33 | -1.528 | -4.303 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Consumer Transformation | 21.811 | 21.773 | 21.677 | 21.54 | 21.444 | 21.343 | 21.208 | 20.654 | 19.423 | 18.49 | 17.642 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Consumer Transformation | 3.809 | 3.682 | 3.52 | 3.334 | 3.216 | 3.095 | 2.96 | 2.258 | 0.419 | -1.18 | -2.764 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Consumer Transformation | 11.545 | 11.082 | 10.429 | 9.655 | 9.092 | 8.499 | 7.784 | 4.375 | -1.634 | -6.028 | -10.07 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Consumer Transformation | 9.539 | 9.175 | 8.682 | 8.159 | 7.762 | 7.349 | 6.84 | 4.586 | 0.266 | -2.963 | -5.877 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Consumer Transformation | 14.891 | 14.622 | 14.273 | 13.922 | 13.65 | 13.37 | 13.027 | 11.607 | 9.447 | 7.915 | 6.524 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Consumer Transformation | 2.557 | 2.515 | 2.363 | 2.124 | 2.025 | 1.893 | 1.698 | 0.424 | -3.285 | -5.884 | -8.19 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Consumer Transformation | 5.913 | 5.714 | 5.429 | 5.089 | 4.817 | 4.529 | 4.183 | 2.491 | -0.089 | -1.898 | -3.475 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 15.138 | 15.119 | 15.084 | 15.034 | 15 | 14.961 | 14.909 | 14.589 | 13.243 | 12.191 | 11.269 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 4.309 | 1.26 | 1.222 | 1.129 | 1.069 | 0.974 | 0.822 | -0.39 | -4.554 | -7.554 | -10.022 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Consumer Transformation | 8.297 | 8.198 | 8.016 | 7.761 | 7.583 | 7.37 | 7.098 | 5.378 | 1.542 | -1.157 | -3.446 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Consumer Transformation | 11.759 | 11.47 | 11.025 | 10.481 | 10.11 | 9.726 | 9.254 | 7.169 | 2.406 | -1.34 | -4.841 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Consumer Transformation | 6.154 | 5.724 | 5.081 | 4.306 | 3.718 | 3.094 | 2.326 | -1.338 | -8.245 | -13.364 | -17.933 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Consumer Transformation | 6.843 | 6.826 | 6.806 | 6.779 | 6.757 | 6.734 | 6.71 | 6.593 | 6.262 | 5.972 | 5.689 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Consumer Transformation | 4.338 | 4.307 | 4.263 | 4.209 | 4.161 | 4.106 | 4.038 | 3.689 | 3.075 | 2.611 | 2.197 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Consumer Transformation | 13.781 | 13.462 | 12.999 | 12.451 | 12.103 | 11.74 | 11.296 | 9.327 | 5.447 | 2.517 | -0.326 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 13.961 | 13.88 | 13.795 | 13.7 | 13.602 | 13.504 | 13.404 | 12.89 | 11.709 | 10.546 | 9.377 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Consumer Transformation | 5.537 | 5.459 | 5.35 | 5.222 | 5.123 | 5.021 | 4.899 | 4.372 | 3.605 | 3.047 | 2.532 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 10.599 | 10.302 | 9.846 | 9.301 | 8.932 | 8.546 | 8.058 | 5.923 | 1.446 | -1.926 | -5.088 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Consumer Transformation | 11.531 | 11.266 | 10.858 | 10.375 | 9.985 | 9.571 | 9.049 | 6.659 | 2.354 | -0.798 | -3.566 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Consumer Transformation | 9.31 | 9.34 | 9.324 | 9.27 | 9.283 | 9.283 | 9.259 | 8.996 | 7.251 | 5.933 | 4.718 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Consumer Transformation | 10.353 | 10.345 | 10.285 | 10.19 | 10.121 | 10.038 | 9.91 | 9.336 | 8.165 | 7.346 | 6.601 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Consumer Transformation | 17.45 | 17.281 | 17.043 | 16.764 | 16.542 | 16.303 | 16.013 | 14.607 | 12.73 | 11.536 | 10.563 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Consumer Transformation | 7.901 | 22.421 | 22.157 | 21.85 | 21.604 | 21.347 | 21.028 | 19.619 | 16.307 | 13.689 | 11.336 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Consumer Transformation | 10.732 | 10.322 | 9.724 | 9.004 | 8.42 | 7.828 | 7.127 | 4.147 | -1.727 | -6.488 | -10.929 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Consumer Transformation | 3.852 | 3.736 | 3.586 | 3.44 | 3.342 | 3.241 | 3.116 | 2.614 | 1.798 | 1.228 | 0.675 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Consumer Transformation | 6.224 | 5.576 | 4.786 | 4.011 | 3.358 | 2.678 | 1.872 | -1.794 | -7.438 | -11.532 | -15.027 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Consumer Transformation | 4.637 | 4.264 | 3.741 | 3.107 | 2.435 | 1.726 | 0.861 | -3.128 | -10.052 | -15.63 | -20.61 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Consumer Transformation | 5.992 | 5.454 | 4.683 | 3.761 | 3.025 | 2.268 | 1.369 | -2.63 | -10.168 | -16.142 | -21.683 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Consumer Transformation | 4.316 | 4.377 | 4.43 | 4.473 | 4.514 | 4.548 | 4.574 | 4.624 | 4.4 | 4.274 | 4.192 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Consumer Transformation | 7.945 | 7.49 | 6.803 | 5.962 | 5.319 | 4.614 | 3.745 | -0.777 | -8.121 | -13.122 | -17.348 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Consumer Transformation | 13.031 | 13.118 | 13.194 | 13.247 | 13.295 | 13.336 | 13.368 | 13.424 | 12.629 | 12.062 | 11.603 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Consumer Transformation | 10.29 | 10.419 | 10.54 | 10.652 | 10.757 | 10.858 | 10.952 | 11.361 | 11.459 | 11.548 | 11.631 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Consumer Transformation | 11.049 | 11.142 | 11.213 | 11.282 | 11.371 | 11.447 | 11.499 | 11.655 | 9.934 | 8.586 | 7.377 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Consumer Transformation | 11.735 | 11.79 | 11.824 | 11.843 | 11.879 | 11.909 | 11.922 | 11.975 | 11.359 | 10.891 | 10.451 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Consumer Transformation | 10.926 | 10.637 | 10.201 | 9.686 | 9.315 | 8.907 | 8.394 | 5.774 | 1.673 | -0.969 | -3.188 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Consumer Transformation | 4.283 | 4.208 | 4.099 | 3.975 | 3.845 | 3.711 | 3.545 | 2.872 | 2.467 | 2.253 | 2.105 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Consumer Transformation | 5.255 | 5.235 | 5.193 | 5.136 | 5.089 | 5.037 | 4.969 | 4.627 | 4.022 | 3.485 | 2.955 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Consumer Transformation | 13.699 | 13.225 | 12.63 | 12.043 | 11.581 | 11.101 | 10.511 | 7.905 | 3.066 | -0.552 | -3.767 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Consumer Transformation | 0.005 | 0.006 | -0.005 | -0.026 | -0.042 | -0.063 | -0.093 | -0.272 | -0.665 | -0.97 | -1.247 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Consumer Transformation | 3.318 | 3.116 | 2.853 | 2.556 | 2.316 | 2.068 | 1.769 | 0.489 | -1.243 | -2.509 | -3.694 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 9.658 | 9.442 | 9.095 | 8.661 | 8.379 | 8.071 | 7.683 | 5.762 | 2.297 | -0.03 | -2.15 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Consumer Transformation | 9.173 | 9.041 | 8.872 | 8.727 | 8.628 | 8.517 | 8.359 | 7.634 | 5.405 | 3.676 | 2.103 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Consumer Transformation | 5.399 | 5.107 | 4.711 | 4.259 | 3.93 | 3.587 | 3.179 | 1.243 | -2.741 | -5.87 | -8.84 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Consumer Transformation | 4.798 | 4.822 | 4.841 | 4.853 | 4.864 | 4.871 | 4.872 | 4.831 | 4.589 | 4.425 | 4.299 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Consumer Transformation | 21.963 | 21.777 | 21.52 | 21.244 | 21.072 | 20.894 | 20.67 | 19.711 | 17.097 | 15.064 | 13.166 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Consumer Transformation | 7.932 | 7.979 | 8.003 | 8.018 | 8.065 | 8.102 | 8.124 | 8.185 | 7.074 | 6.192 | 5.357 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Consumer Transformation | 13.472 | 13.127 | 12.711 | 12.338 | 12.047 | 11.744 | 11.364 | 9.753 | 6.649 | 4.298 | 2.199 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Consumer Transformation | 7.275 | 7.252 | 7.149 | 6.981 | 6.853 | 6.706 | 6.494 | 5.465 | 2.654 | 0.498 | -1.442 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Consumer Transformation | 4.723 | 4.037 | 3.11 | 2.125 | 1.459 | 0.768 | -0.08 | -3.785 | -10.811 | -15.952 | -20.715 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Consumer Transformation | 0.957 | 0.922 | 0.878 | 0.824 | 0.773 | 0.718 | 0.655 | 0.325 | -0.359 | -0.93 | -1.466 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Consumer Transformation | 3.191 | 3.084 | 2.93 | 2.73 | 2.556 | 2.359 | 2.124 | 0.722 | -2.12 | -4.291 | -6.196 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Consumer Transformation | 12.976 | 12.923 | 12.806 | 12.642 | 12.505 | 12.361 | 12.174 | 11.373 | 9.613 | 8.303 | 7.179 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Consumer Transformation | 14.821 | 14.621 | 15.294 | 14.881 | 14.59 | 14.288 | 13.905 | 12.249 | 8.676 | 5.904 | 3.308 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Consumer Transformation | 22.332 | 22.338 | 22.261 | 22.083 | 21.896 | 21.637 | 21.283 | 18.534 | 13.043 | 9.634 | 7.246 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Consumer Transformation | 9.824 | 9.532 | 9.128 | 8.651 | 8.263 | 7.859 | 7.381 | 5.166 | 0.977 | -2.345 | -5.439 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Consumer Transformation | 2.434 | 2.196 | 1.881 | 1.517 | 1.271 | 1.014 | 0.704 | -0.722 | -3.203 | -5.062 | -6.876 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Consumer Transformation | 8.157 | 7.777 | 7.15 | 6.374 | 5.933 | 5.48 | 4.917 | 2.522 | -3.89 | -8.959 | -13.907 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Consumer Transformation | 6.097 | 3.811 | 3.8 | 3.768 | 3.74 | 3.702 | 3.644 | 3.258 | 1.991 | 1.032 | 0.216 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Consumer Transformation | 7.456 | 6.98 | 6.294 | 5.505 | 4.918 | 4.31 | 3.555 | 0.34 | -5.126 | -9.145 | -12.837 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Consumer Transformation | 3.905 | 3.643 | 17.947 | 17.476 | 17.083 | 16.67 | 16.154 | 13.761 | 8.816 | 5.083 | 1.853 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Consumer Transformation | -0.178 | -0.315 | -0.507 | -0.738 | -0.933 | -1.133 | -1.371 | -2.417 | -4.468 | -6.161 | -7.761 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Consumer Transformation | 2.851 | 2.859 | 2.849 | 2.82 | 2.811 | 2.796 | 2.769 | 2.585 | 1.813 | 1.264 | 0.789 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Consumer Transformation | 10.428 | 10.133 | 9.673 | 9.121 | 8.708 | 8.282 | 7.755 | 5.557 | 1.449 | -1.636 | -4.45 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Consumer Transformation | 8.547 | 8.191 | 7.656 | 7.023 | 6.628 | 6.209 | 5.685 | 3.263 | -1.641 | -5.214 | -8.591 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Consumer Transformation | 12.473 | 12.36 | 12.175 | 11.948 | 11.778 | 11.593 | 11.357 | 10.231 | 8.506 | 7.329 | 6.283 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Consumer Transformation | 3.817 | 2.888 | 2.904 | 2.866 | 2.866 | 2.839 | 2.771 | 2.143 | -0.345 | -2.121 | -3.602 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Consumer Transformation | 15.285 | 15.209 | 15.1 | 14.953 | 14.818 | 14.662 | 14.477 | 13.291 | 10.888 | 9.134 | 7.64 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Consumer Transformation | 4.094 | 3.994 | 3.851 | 3.686 | 3.56 | 3.431 | 3.279 | 2.613 | 1.233 | 0.137 | -0.898 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Consumer Transformation | 2.456 | 2.39 | 2.287 | 2.161 | 2.073 | 1.981 | 1.866 | 1.375 | 0.193 | -0.721 | -1.562 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Consumer Transformation | 14.966 | 14.617 | 14.103 | 13.487 | 13.041 | 12.562 | 11.974 | 9.082 | 3.676 | -0.337 | -4.016 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Consumer Transformation | 1.958 | 1.803 | 1.516 | 1.137 | 0.821 | 0.48 | 0.03 | -2.053 | -7.037 | -10.948 | -14.476 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Consumer Transformation | 14.832 | 14.76 | 14.618 | 14.429 | 14.368 | 14.298 | 14.203 | 13.681 | 11.402 | 9.65 | 7.967 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Consumer Transformation | 4.717 | 4.617 | 4.483 | 4.326 | 4.188 | 4.046 | 3.878 | 3.135 | 1.83 | 0.811 | -0.119 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Consumer Transformation | 6.897 | 6.436 | 5.782 | 5.024 | 4.426 | 3.801 | 3.038 | -0.299 | -5.229 | -8.783 | -12.088 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Consumer Transformation | 12.608 | 12.252 | 11.756 | 11.191 | 10.784 | 10.364 | 9.859 | 7.723 | 4.122 | 1.396 | -1.248 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Consumer Transformation | 12.907 | 11.26 | 11.174 | 11.014 | 10.905 | 10.737 | 10.501 | 8.56 | 4.887 | 2.775 | 1.345 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Consumer Transformation | 2.917 | 2.637 | 2.333 | 2.103 | 1.906 | 1.705 | 1.458 | 0.467 | -0.588 | -1.229 | -1.763 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Consumer Transformation | 7.97 | 7.267 | 6.326 | 5.265 | 4.505 | 3.729 | 2.819 | -1.132 | -7.291 | -11.756 | -15.997 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Consumer Transformation | 8.537 | 8.535 | 8.526 | 8.511 | 8.496 | 8.478 | 8.454 | 8.31 | 8.12 | 7.933 | 7.745 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Consumer Transformation | 2.007 | 1.818 | 1.533 | 1.161 | 0.763 | 0.282 | -0.321 | -4.319 | -9.612 | -12.584 | -14.393 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Consumer Transformation | 11.771 | 11.39 | 10.916 | 10.459 | 10.154 | 9.832 | 9.439 | 7.597 | 3.115 | -0.345 | -3.534 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Consumer Transformation | 9.311 | 8.915 | 8.318 | 7.593 | 7.105 | 6.587 | 5.951 | 2.922 | -2.471 | -6.319 | -9.828 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Consumer Transformation | 0.886 | 0.783 | 0.635 | 0.45 | 0.276 | 0.072 | -0.178 | -1.722 | -3.736 | -4.944 | -5.799 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Consumer Transformation | 7.414 | 7.066 | 6.546 | 5.926 | 5.461 | 4.983 | 4.402 | 1.935 | -3.379 | -7.592 | -11.553 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Consumer Transformation | 0.9 | 0.869 | 0.775 | 0.636 | 0.586 | 0.524 | 0.432 | -0.084 | -2.409 | -4.158 | -5.755 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Consumer Transformation | 1.488 | 1.487 | 1.487 | 1.486 | 1.485 | 1.483 | 1.482 | 1.473 | 1.457 | 1.44 | 1.425 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 10.478 | 10.508 | 10.497 | 10.448 | 10.457 | 10.459 | 10.442 | 10.358 | 8.789 | 7.545 | 6.345 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 7.122 | 7.084 | 7.017 | 6.931 | 6.879 | 6.822 | 6.746 | 6.403 | 5.479 | 4.781 | 4.111 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 8.498 | 8.413 | 8.289 | 8.143 | 8.009 | 7.872 | 7.707 | 7.03 | 6.172 | 5.555 | 5.012 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 3.914 | 3.708 | 3.425 | 3.11 | 2.882 | 2.636 | 2.335 | 0.807 | -1.786 | -3.622 | -5.247 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Consumer Transformation | 14.545 | 14.254 | 13.851 | 14.369 | 13.918 | 13.461 | 12.926 | 10.67 | 7.246 | 4.709 | 2.475 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Consumer Transformation | 10.096 | 9.016 | 8.611 | 8.115 | 7.794 | 7.461 | 7.049 | 5.278 | 1.484 | -1.445 | -4.289 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Consumer Transformation | 3.259 | 3.081 | 2.843 | 2.561 | 2.28 | 1.972 | 1.597 | -0.432 | -3.443 | -5.587 | -7.346 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Consumer Transformation | 10.667 | 9.94 | 9.193 | 8.692 | 8.371 | 8.042 | 7.635 | 5.843 | 1.601 | -1.645 | -4.684 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Consumer Transformation | 10.773 | 10.722 | 10.648 | 10.554 | 10.498 | 10.438 | 10.371 | 9.989 | 8.566 | 7.263 | 5.965 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Consumer Transformation | -2.998 | -3.691 | -4.658 | -5.775 | -6.651 | -7.551 | -8.624 | -13.323 | -21.511 | -27.763 | -33.545 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Consumer Transformation | 7.014 | 6.331 | 5.465 | 4.607 | 4.013 | 3.409 | 2.682 | -0.29 | -5.009 | -8.275 | -11.316 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Consumer Transformation | 5.264 | 5.276 | 5.194 | 5.041 | 5.08 | 5.105 | 5.099 | 4.906 | 1.985 | -0.443 | -2.937 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 17.262 | 14.224 | 14.034 | 13.813 | 13.635 | 13.454 | 13.247 | 12.301 | 10.22 | 8.433 | 6.672 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Consumer Transformation | 13.888 | 13.855 | 13.8 | 13.719 | 13.644 | 13.553 | 13.442 | 12.699 | 11.186 | 10.083 | 9.15 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Consumer Transformation | 9.622 | 9.429 | 9.188 | 8.891 | 8.591 | 8.246 | 7.845 | 5.264 | 1.343 | -1.397 | -3.58 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Consumer Transformation | 12.753 | 12.741 | 12.674 | 12.563 | 12.535 | 12.502 | 12.447 | 12.183 | 10.166 | 8.531 | 6.932 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Consumer Transformation | 11.523 | 11.567 | 11.575 | 11.553 | 11.574 | 11.588 | 11.585 | 11.552 | 10.761 | 10.176 | 9.615 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 4.187 | 4.025 | 3.834 | 3.602 | 3.352 | 3.064 | 2.732 | 0.522 | -2.606 | -4.762 | -6.434 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Consumer Transformation | 16.339 | 16.273 | 16.164 | 16.024 | 15.961 | 15.888 | 15.798 | 15.212 | 13.424 | 12.037 | 10.746 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Consumer Transformation | 10.803 | 10.512 | 10.058 | 9.511 | 9.2 | 8.876 | 8.476 | 6.723 | 2.504 | -0.67 | -3.738 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Consumer Transformation | 10.321 | 10.212 | 10.001 | 9.718 | 9.611 | 9.489 | 9.327 | 8.408 | 5.015 | 2.443 | 0.022 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Consumer Transformation | 7.07 | 6.705 | 6.142 | 5.456 | 4.971 | 4.452 | 3.798 | 0.72 | -4.544 | -8.196 | -11.416 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Consumer Transformation | 4.522 | 4.149 | 3.631 | 3.042 | 2.592 | 2.111 | 1.532 | -1.364 | -6.375 | -9.908 | -12.979 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Consumer Transformation | 11.735 | 11.73 | 11.69 | 11.625 | 11.548 | 11.435 | 11.272 | 10.104 | 8.599 | 7.884 | 7.553 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Consumer Transformation | 15.409 | 15.085 | 14.586 | 13.978 | 13.63 | 13.275 | 12.842 | 11.012 | 6.837 | 3.628 | 0.461 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Consumer Transformation | 9.265 | 8.808 | 8.14 | 7.335 | 6.694 | 5.992 | 5.127 | 0.648 | -6.217 | -10.891 | -14.847 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Consumer Transformation | 3.291 | 3.174 | 3.012 | 3.326 | 3.172 | 3.014 | 2.823 | 1.971 | 0.624 | -0.42 | -1.393 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Consumer Transformation | 8.024 | 7.806 | 7.453 | 7.03 | 6.679 | 6.319 | 5.865 | 3.963 | -0.683 | -4.359 | -7.633 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Consumer Transformation | 4.125 | 3.915 | 3.611 | 3.263 | 3.046 | 2.825 | 2.554 | 1.426 | -0.771 | -2.428 | -4.058 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 12.299 | 12.288 | 12.251 | 12.192 | 12.162 | 12.126 | 12.076 | 11.778 | 10.696 | 9.799 | 8.929 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 25.328 | 25.291 | 25.232 | 25.151 | 25.101 | 25.048 | 24.984 | 24.655 | 23.414 | 22.386 | 21.396 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Consumer Transformation | 14.613 | 14.455 | 14.244 | 13.996 | 13.764 | 13.519 | 13.227 | 11.834 | 10.13 | 9.017 | 8.144 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Consumer Transformation | 12.696 | 12.754 | 12.79 | 12.801 | 12.825 | 12.843 | 12.847 | 12.844 | 11.855 | 11.071 | 10.35 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Consumer Transformation | 19.833 | 19.816 | 19.79 | 19.752 | 19.727 | 19.701 | 19.672 | 19.52 | 18.819 | 18.185 | 17.55 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Consumer Transformation | 6.785 | 6.513 | 6.096 | 5.595 | 5.274 | 4.942 | 4.532 | 2.819 | -0.39 | -2.696 | -4.914 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 22.482 | 22.48 | 22.406 | 22.273 | 22.23 | 22.173 | 22.076 | 21.549 | 19.146 | 17.298 | 15.562 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Consumer Transformation | 14.569 | 14.501 | 14.377 | 14.219 | 14.187 | 14.152 | 14.1 | 13.805 | 11.417 | 9.472 | 7.578 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Consumer Transformation | 4.73 | 4.642 | 4.508 | 4.347 | 4.248 | 4.142 | 4.009 | 3.411 | 2.234 | 1.369 | 0.548 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Consumer Transformation | 4.522 | 4.503 | 4.479 | 4.45 | 4.423 | 4.394 | 4.36 | 4.15 | 3.862 | 3.651 | 3.474 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Consumer Transformation | 15.693 | 15.625 | 15.507 | 15.342 | 15.231 | 15.105 | 14.949 | 13.996 | 11.342 | 9.294 | 7.432 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 9.653 | 9.512 | 9.295 | 9.035 | 8.823 | 8.603 | 8.33 | 7.15 | 4.96 | 3.315 | 1.877 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 11.532 | 11.436 | 11.287 | 11.105 | 10.984 | 10.86 | 10.705 | 10.037 | 8.341 | 7.008 | 5.776 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Consumer Transformation | 2.323 | 2.177 | 1.987 | 1.777 | 1.57 | 1.358 | 1.106 | -0.009 | -1.757 | -3.179 | -4.459 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Consumer Transformation | 3.476 | 3.283 | 3.009 | 2.67 | 2.479 | 2.264 | 2.006 | 0.48 | -3.772 | -7.149 | -10.372 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Consumer Transformation | 18.932 | 18.915 | 18.883 | 18.837 | 18.804 | 18.76 | 18.703 | 18.297 | 17.577 | 17.122 | 16.775 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Consumer Transformation | 4.842 | 4.76 | 4.638 | 4.495 | 4.39 | 4.281 | 4.146 | 3.562 | 2.231 | 1.175 | 0.211 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Consumer Transformation | 14.795 | 14.782 | 14.754 | 14.726 | 14.713 | 14.692 | 14.655 | 14.385 | 13.294 | 12.45 | 11.709 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Consumer Transformation | 12.648 | 12.744 | 12.825 | 12.889 | 12.961 | 13.024 | 13.077 | 13.224 | 12.88 | 12.67 | 12.506 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Consumer Transformation | 2.211 | 1.901 | 1.464 | 0.95 | 0.524 | 0.081 | -0.453 | -2.852 | -5.899 | -7.946 | -9.712 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 5.914 | 5.885 | 5.829 | 5.754 | 5.714 | 5.669 | 5.612 | 5.285 | 4.207 | 3.366 | 2.579 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 5.276 | 5.237 | 5.166 | 5.073 | 5.011 | 4.936 | 4.839 | 4.211 | 2.957 | 2.101 | 1.381 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Consumer Transformation | 5.241 | 4.912 | 4.451 | 3.911 | 3.483 | 3.032 | 2.491 | -0.03 | -4.34 | -7.597 | -10.559 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Consumer Transformation | 15.34 | 15.264 | 15.149 | 15.001 | 14.918 | 14.829 | 14.725 | 14.149 | 12.27 | 10.76 | 9.337 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Consumer Transformation | 8.149 | 7.571 | 6.842 | 6.128 | 5.513 | 4.879 | 4.094 | 0.792 | -4.752 | -8.959 | -12.704 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Consumer Transformation | 4.887 | 4.82 | 4.7 | 4.552 | 4.468 | 4.361 | 4.212 | 3.275 | -0.116 | -2.699 | -4.971 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Consumer Transformation | 10.384 | 10.081 | 9.591 | 8.98 | 8.566 | 8.141 | 7.623 | 5.372 | -0.501 | -5.239 | -9.729 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Consumer Transformation | 0.258 | 0.185 | 0.083 | -0.047 | -0.135 | -0.231 | -0.344 | -0.97 | -2.57 | -3.856 | -5.064 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Consumer Transformation | 13.431 | 13.124 | 12.674 | 12.162 | 11.775 | 11.37 | 10.867 | 8.646 | 4.604 | 1.62 | -1.083 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Consumer Transformation | 18.433 | 18.429 | 18.41 | 18.377 | 18.355 | 18.327 | 18.289 | 18.067 | 17.162 | 16.47 | 15.863 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Consumer Transformation | 12.617 | 12.397 | 12.1 | 11.758 | 11.586 | 11.405 | 11.198 | 10.165 | 7.329 | 4.986 | 2.566 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Consumer Transformation | 7.168 | 7.057 | 6.892 | 6.681 | 6.51 | 6.327 | 6.108 | 4.94 | 2.047 | -0.283 | -2.378 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Consumer Transformation | 8.254 | 8.13 | 7.917 | 7.628 | 7.433 | 7.199 | 6.906 | 4.929 | 0.176 | -3.388 | -6.482 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Consumer Transformation | 16.349 | 16.336 | 16.32 | 16.303 | 16.284 | 16.263 | 16.239 | 16.1 | 15.921 | 15.729 | 15.536 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Consumer Transformation | 16.963 | 16.877 | 16.731 | 16.544 | 16.38 | 16.206 | 15.984 | 15.012 | 13.117 | 11.687 | 10.418 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Consumer Transformation | 18.992 | 18.949 | 18.885 | 18.804 | 18.746 | 18.687 | 18.616 | 18.298 | 17.303 | 16.474 | 15.693 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Consumer Transformation | 9.081 | 8.526 | 7.888 | 7.351 | 7.028 | 6.695 | 6.286 | 4.53 | 0.48 | -2.559 | -5.482 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Consumer Transformation | 10.426 | 9.976 | 9.368 | 8.724 | 8.266 | 7.79 | 7.192 | 4.626 | 0.021 | -3.4 | -6.593 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Consumer Transformation | -6.477 | -6.357 | -6.261 | -6.186 | -6.11 | -6.047 | -6.003 | -5.92 | -6.391 | -6.652 | -6.819 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Consumer Transformation | 10.09 | 9.397 | 8.612 | 7.953 | 7.466 | 6.969 | 6.358 | 3.746 | -1.894 | -6.293 | -10.355 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Consumer Transformation | 11.425 | 11.32 | 11.15 | 10.921 | 10.766 | 10.585 | 10.36 | 8.949 | 5.42 | 2.771 | 0.409 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Consumer Transformation | 5.217 | 4.911 | 4.485 | 3.985 | 3.598 | 3.204 | 2.736 | 0.746 | -2.878 | -5.731 | -8.452 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Consumer Transformation | 24.502 | 24.485 | 24.4 | 24.254 | 24.219 | 24.176 | 24.107 | 23.72 | 20.927 | 18.692 | 16.563 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Consumer Transformation | 6.493 | 6.312 | 6.059 | 5.758 | 5.529 | 5.286 | 4.998 | 3.56 | 0.946 | -1.058 | -2.925 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Consumer Transformation | 6.768 | 6.759 | 6.743 | 6.722 | 6.709 | 6.694 | 6.676 | 6.59 | 6.409 | 6.276 | 6.153 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Consumer Transformation | 11.664 | 11.087 | 10.236 | 9.225 | 8.582 | 7.917 | 7.115 | 3.585 | -3.385 | -8.707 | -13.912 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Consumer Transformation | 21.999 | 22.028 | 22.029 | 21.995 | 21.935 | 21.832 | 21.682 | 20.317 | 18.512 | 17.721 | 17.463 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Consumer Transformation | 11.262 | 11.015 | 10.637 | 10.185 | 9.901 | 9.602 | 9.23 | 7.561 | 3.698 | 0.816 | -1.881 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Consumer Transformation | 12.127 | 12.015 | 11.836 | 11.581 | 11.294 | 10.935 | 10.486 | 7.253 | 2.006 | -1.266 | -3.492 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Consumer Transformation | 0.761 | 0.674 | 0.547 | 0.39 | 0.245 | 0.086 | -0.11 | -1.131 | -2.855 | -4.142 | -5.268 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Consumer Transformation | 7.064 | 1.318 | 0.97 | 0.565 | 0.246 | -0.083 | -0.478 | -2.229 | -4.927 | -6.876 | -8.649 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Consumer Transformation | 5.062 | 4.802 | 4.439 | 4.018 | 3.712 | 3.394 | 3.014 | 1.321 | -1.652 | -3.984 | -6.255 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Consumer Transformation | 12.931 | 12.743 | 12.463 | 12.114 | 11.791 | 11.392 | 10.88 | 7.412 | 2.134 | -0.907 | -2.913 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Consumer Transformation | 2.303 | 2.066 | 1.713 | 1.322 | 1.08 | 0.817 | 0.478 | -1.114 | -4.319 | -6.532 | -8.536 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Consumer Transformation | 2.25 | 2.05 | 1.808 | 1.598 | 1.463 | 1.322 | 1.148 | 0.442 | -0.773 | -1.621 | -2.442 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Consumer Transformation | 12.982 | 12.835 | 12.581 | 12.261 | 12.092 | 11.91 | 11.673 | 10.575 | 7.763 | 5.648 | 3.638 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Consumer Transformation | 7.9 | 7.95 | 7.984 | 8.01 | 8.041 | 8.067 | 8.076 | 8.1 | 6.897 | 5.96 | 5.123 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Consumer Transformation | 13.581 | 13.513 | 13.377 | 13.186 | 13.127 | 13.057 | 12.963 | 12.432 | 9.995 | 8.093 | 6.249 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Consumer Transformation | 7.113 | 6.719 | 6.178 | 5.552 | 5.001 | 4.427 | 3.733 | 0.62 | -3.691 | -6.954 | -9.924 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Consumer Transformation | 12.796 | 12.767 | 12.678 | 12.535 | 12.445 | 12.311 | 12.124 | 10.608 | 7.829 | 6.192 | 5.032 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Consumer Transformation | 13.776 | 13.821 | 13.861 | 13.893 | 13.926 | 13.956 | 13.982 | 14.089 | 13.941 | 13.826 | 13.719 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Consumer Transformation | 5.911 | 5.894 | 5.862 | 5.824 | 5.803 | 5.779 | 5.745 | 5.595 | 5.348 | 5.174 | 4.995 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Consumer Transformation | 14.197 | 14.231 | 14.242 | 14.227 | 14.228 | 14.225 | 14.211 | 14.131 | 13.012 | 12.146 | 11.366 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Consumer Transformation | -4.042 | -4.333 | -4.788 | -5.344 | -5.685 | -6.039 | -6.471 | -8.374 | -12.308 | -15.199 | -17.932 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Consumer Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Consumer Transformation | 8.941 | 7.827 | 7.179 | 6.417 | 5.867 | 5.304 | 4.631 | 1.739 | -4.291 | -9.025 | -13.456 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Consumer Transformation | 8.894 | 8.275 | 7.42 | 6.493 | 11.899 | 11.287 | 10.529 | 7.324 | 1.465 | -2.866 | -7.075 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Consumer Transformation | 4.05 | 4.137 | 4.198 | 4.226 | 4.25 | 4.264 | 4.259 | 4.148 | 2.408 | 0.985 | -0.263 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Consumer Transformation | 2.286 | 1.973 | 1.529 | 0.998 | 0.453 | -0.105 | -0.769 | -3.557 | -8.617 | -12.747 | -16.406 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Consumer Transformation | 14.378 | 14.189 | 13.908 | 13.586 | 13.338 | 13.083 | 12.766 | 11.401 | 8.165 | 5.615 | 3.288 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Consumer Transformation | 5.589 | 5.071 | 4.288 | 3.345 | 2.718 | 2.06 | 1.254 | -2.372 | -8.741 | -13.401 | -17.896 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Consumer Transformation | 5.165 | 4.166 | 3.809 | 3.432 | 3.182 | 2.907 | 2.549 | 0.792 | -3.1 | -5.956 | -8.511 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Consumer Transformation | 15.084 | 14.916 | 14.665 | 14.379 | 14.21 | 14.036 | 13.817 | 12.884 | 10.696 | 9.004 | 7.345 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Consumer Transformation | 4.16 | 3.861 | 3.405 | 2.865 | 2.511 | 2.133 | 1.656 | -0.579 | -4.896 | -8.026 | -10.936 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Consumer Transformation | 7.896 | 7.655 | 7.321 | 6.909 | 6.626 | 6.32 | 5.961 | 3.983 | -0.182 | -3.294 | -6.157 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Consumer Transformation | 8.904 | 8.455 | 7.806 | 7.042 | 6.527 | 5.995 | 5.35 | 2.585 | -2.016 | -5.221 | -8.283 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Consumer Transformation | 6.802 | 6.457 | 5.984 | 5.44 | 4.963 | 4.478 | 3.901 | 1.477 | -1.694 | -3.919 | -5.847 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Consumer Transformation | 2.255 | 1.493 | 0.591 | -0.209 | -0.862 | -1.536 | -2.37 | -5.943 | -13.014 | -18.441 | -23.214 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Consumer Transformation | 9.656 | 9.111 | 8.397 | 7.676 | 7.247 | 6.806 | 6.262 | 3.94 | -1.135 | -4.967 | -8.679 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Consumer Transformation | 10.588 | 10.065 | 9.394 | 8.726 | 8.214 | 7.664 | 6.975 | 3.639 | -1.77 | -5.469 | -8.636 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Consumer Transformation | 13.419 | 13.428 | 13.39 | 13.303 | 13.244 | 13.154 | 13.026 | 11.991 | 9.54 | 8.003 | 6.868 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Consumer Transformation | 8.81 | 8.687 | 8.497 | 8.267 | 8.094 | 7.912 | 7.678 | 6.63 | 4.361 | 2.608 | 1.001 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Consumer Transformation | 3.591 | 3.535 | 3.419 | 3.255 | 3.165 | 3.051 | 2.896 | 1.848 | -0.295 | -1.637 | -2.718 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Consumer Transformation | 12.891 | 12.662 | 12.306 | 11.879 | 11.596 | 11.304 | 10.94 | 9.396 | 6.05 | 3.498 | 1.09 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Consumer Transformation | 17.595 | 17.494 | 17.314 | 17.081 | 16.887 | 16.685 | 16.429 | 15.336 | 13.351 | 11.84 | 10.483 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Consumer Transformation | 15.444 | 15.336 | 15.169 | 14.955 | 14.855 | 14.75 | 14.627 | 14.021 | 11.805 | 10.002 | 8.183 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Consumer Transformation | 4.162 | 4.005 | 3.774 | 3.466 | 3.198 | 2.867 | 2.457 | -0.421 | -5.284 | -8.397 | -10.732 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Consumer Transformation | 10.147 | 10.195 | 10.213 | 10.197 | 10.208 | 10.207 | 10.186 | 9.962 | 8.382 | 7.226 | 6.222 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Consumer Transformation | -1.195 | -1.286 | -1.422 | -1.594 | -1.701 | -1.822 | -1.971 | -2.904 | -5.073 | -6.676 | -8.099 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Consumer Transformation | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Consumer Transformation | 6.75 | 6.228 | 5.552 | 4.85 | 4.389 | 3.9 | 3.292 | 0.491 | -4.258 | -7.608 | -10.768 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Consumer Transformation | 14.344 | 14.023 | 13.545 | 12.966 | 12.631 | 12.284 | 11.861 | 9.965 | 5.868 | 2.702 | -0.412 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Consumer Transformation | 3.456 | 3.311 | 3.111 | 2.881 | 2.709 | 2.532 | 2.32 | 1.389 | -0.296 | -1.633 | -2.933 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Consumer Transformation | 8.846 | 8.553 | 8.135 | 7.586 | 7.101 | 6.506 | 5.773 | 0.581 | -7.702 | -12.839 | -16.61 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Consumer Transformation | 13.018 | 12.504 | 11.884 | 11.301 | 10.878 | 10.44 | 9.898 | 7.545 | 3.268 | 0.083 | -2.895 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Consumer Transformation | 5.061 | 4.97 | 4.842 | 4.696 | 4.578 | 4.459 | 4.317 | 3.704 | 2.496 | 1.523 | 0.619 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Consumer Transformation | 6.722 | 6.285 | 5.667 | 4.938 | 4.413 | 3.873 | 3.228 | 0.433 | -5.373 | -9.985 | -14.454 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Consumer Transformation | 10.158 | 9.88 | 9.44 | 8.907 | 8.545 | 8.172 | 7.712 | 5.727 | 0.992 | -2.666 | -6.032 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Consumer Transformation | 14.827 | 14.483 | 14.047 | 13.619 | 13.283 | 12.944 | 12.537 | 10.887 | 7.675 | 5.213 | 2.979 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Consumer Transformation | 6.44 | 6.242 | 5.9 | 5.458 | 5.209 | 4.94 | 4.597 | 3.017 | -0.992 | -3.976 | -6.795 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Consumer Transformation | 14.012 | 13.636 | 13.141 | 12.575 | 12.019 | 11.434 | 10.734 | 7.452 | 2.522 | -1.189 | -4.407 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Consumer Transformation | 13.128 | 13.084 | 13.006 | 12.9 | 12.855 | 12.806 | 12.744 | 12.423 | 11.001 | 9.852 | 8.735 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Consumer Transformation | 9.269 | 8.928 | 8.447 | 7.904 | 7.527 | 7.126 | 6.635 | 4.289 | 0.547 | -2.01 | -4.342 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Consumer Transformation | 12.454 | 12.474 | 12.45 | 12.383 | 12.338 | 12.266 | 12.156 | 11.3 | 9.473 | 8.368 | 7.566 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Consumer Transformation | 6.959 | 6.907 | 6.769 | 6.557 | 6.447 | 6.301 | 6.099 | 4.7 | 1.412 | -0.743 | -2.538 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Consumer Transformation | 25.647 | 25.545 | 25.378 | 25.16 | 24.983 | 24.779 | 24.524 | 23.02 | 20.562 | 18.924 | 17.588 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Consumer Transformation | 4.555 | 4.365 | 4.125 | 3.844 | 3.631 | 3.408 | 3.158 | 1.756 | -1.852 | -5.017 | -8.038 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Consumer Transformation | 1.869 | 1.829 | 1.767 | 1.692 | 1.63 | 1.564 | 1.483 | 1.135 | 0.684 | 0.336 | 0.008 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Consumer Transformation | 12.478 | 12.178 | 11.776 | 11.321 | 10.997 | 10.661 | 10.257 | 8.432 | 4.775 | 1.934 | -0.79 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Consumer Transformation | 10.198 | 10.205 | 10.175 | 10.11 | 10.097 | 10.072 | 10.024 | 9.685 | 8.157 | 7.007 | 5.953 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Consumer Transformation | 10.309 | 10.239 | 10.078 | 9.836 | 9.708 | 9.569 | 9.39 | 8.438 | 3.468 | -0.702 | -4.59 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Consumer Transformation | 0.736 | 0.678 | 0.592 | 0.48 | 0.394 | 0.295 | 0.177 | -0.548 | -2.095 | -3.246 | -4.259 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Consumer Transformation | 9.459 | 9.486 | 9.456 | 9.35 | 9.192 | 8.954 | 8.628 | 5.868 | 1.184 | -1.411 | -2.894 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Consumer Transformation | 16.447 | 16.404 | 16.336 | 16.263 | 16.219 | 16.165 | 16.087 | 15.662 | 14.557 | 13.778 | 13.093 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Consumer Transformation | 8.965 | 7.81 | 7.275 | 6.644 | 6.147 | 5.633 | 5.019 | 2.255 | -3.197 | -7.531 | -11.602 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Consumer Transformation | 12.233 | 12.129 | 11.941 | 11.707 | 11.544 | 11.372 | 11.15 | 10.217 | 8.045 | 6.372 | 4.856 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Consumer Transformation | 18.152 | 18.221 | 18.211 | 18.115 | 17.961 | 17.708 | 17.34 | 14.216 | 9.921 | 7.914 | 7.101 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Consumer Transformation | 10.205 | 9.84 | 9.269 | 8.581 | 8.192 | 7.781 | 7.261 | 4.86 | -0.663 | -4.758 | -8.64 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Consumer Transformation | 4.303 | 4.245 | 4.159 | 4.055 | 3.981 | 3.902 | 3.805 | 3.374 | 2.629 | 2.052 | 1.503 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Consumer Transformation | 9.451 | 9.111 | 8.653 | 8.174 | 7.904 | 7.62 | 7.262 | 5.637 | 1.64 | -1.348 | -4.153 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 15.277 | 15.128 | 14.892 | 14.585 | 14.382 | 14.158 | 13.89 | 12.445 | 8.775 | 5.859 | 3.111 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 13.7 | 13.582 | 13.381 | 13.095 | 12.902 | 12.687 | 12.43 | 10.954 | 6.325 | 2.538 | -1.031 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Consumer Transformation | 13.396 | 13.406 | 13.385 | 13.335 | 13.311 | 13.276 | 13.217 | 12.828 | 11.371 | 10.362 | 9.517 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Consumer Transformation | 8.171 | 8.206 | 8.2 | 8.158 | 8.186 | 8.21 | 8.22 | 8.228 | 6.921 | 5.842 | 4.773 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Consumer Transformation | 17.576 | 17.445 | 17.24 | 16.994 | 16.834 | 16.667 | 16.461 | 15.561 | 13.977 | 12.875 | 11.84 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Consumer Transformation | 5.826 | 5.829 | 5.817 | 5.789 | 5.754 | 5.706 | 5.642 | 5.148 | 4.241 | 3.526 | 2.918 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Consumer Transformation | 2.151 | 1.649 | 1.004 | 0.362 | -0.047 | -0.468 | -0.99 | -3.229 | -8.104 | -11.778 | -15.236 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Consumer Transformation | 12.717 | 12.348 | 11.871 | 11.382 | 11.026 | 10.661 | 10.217 | 8.341 | 4.476 | 1.539 | -1.157 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Consumer Transformation | 10 | 9.485 | 8.775 | 8.01 | 7.522 | 6.996 | 6.342 | 3.109 | -2.959 | -7.113 | -10.768 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 11.65 | 11.674 | 11.658 | 11.598 | 11.539 | 11.449 | 11.313 | 10.223 | 8.224 | 7.115 | 6.428 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Consumer Transformation | 16.035 | 15.816 | 15.473 | 15.061 | 14.802 | 14.534 | 14.2 | 12.788 | 10.062 | 8.044 | 6.121 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Consumer Transformation | 12.896 | 12.792 | 12.603 | 12.352 | 12.139 | 11.913 | 11.621 | 10.313 | 7.187 | 4.765 | 2.649 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Consumer Transformation | 9.414 | 9.157 | 8.751 | 8.257 | 7.928 | 7.569 | 7.11 | 4.836 | 0.581 | -2.343 | -4.926 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Consumer Transformation | 11.539 | 9.792 | 9.59 | 9.326 | 9.167 | 9.001 | 8.786 | 7.888 | 5.284 | 3.222 | 1.246 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Consumer Transformation | 5.204 | 5.115 | 4.991 | 4.856 | 4.741 | 4.62 | 4.473 | 3.841 | 2.864 | 2.134 | 1.472 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Consumer Transformation | 14.274 | 13.825 | 13.187 | 12.463 | 11.93 | 11.376 | 10.691 | 7.746 | 2.974 | -0.572 | -3.935 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Consumer Transformation | 3.133 | 2.796 | 2.259 | 1.607 | 1.113 | 0.601 | -0.04 | -2.775 | -8.925 | -13.69 | -17.994 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Consumer Transformation | 14.842 | 14.561 | 14.156 | 13.703 | 13.386 | 13.053 | 12.638 | 10.837 | 7.694 | 5.411 | 3.275 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Consumer Transformation | 7.077 | 6.605 | 5.928 | 5.162 | 4.67 | 4.16 | 3.53 | 0.846 | -4.911 | -9.288 | -13.526 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Consumer Transformation | 19.376 | 19.432 | 19.412 | 19.315 | 19.281 | 19.227 | 19.127 | 18.454 | 14.844 | 11.992 | 9.418 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Consumer Transformation | 12.535 | 12.382 | 12.168 | 11.926 | 11.722 | 11.507 | 11.242 | 10.048 | 8.078 | 6.752 | 5.662 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Consumer Transformation | 4.577 | 4.259 | 3.793 | 3.233 | 2.823 | 2.39 | 1.857 | -0.634 | -5.127 | -8.516 | -11.679 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Consumer Transformation | 8.789 | 8.079 | 7.151 | 6.109 | 5.039 | 3.936 | 2.629 | -3.128 | -10.799 | -16.535 | -21.363 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Consumer Transformation | 4.565 | 4.228 | 3.774 | 3.296 | 2.918 | 2.526 | 2.04 | -0.109 | -5.205 | -9.24 | -12.893 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Consumer Transformation | 12.946 | 12.453 | 11.779 | 11.01 | 10.489 | 9.959 | 9.332 | 6.69 | 2.105 | -1.396 | -4.846 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Consumer Transformation | 20.883 | 17.794 | 17.829 | 17.857 | 17.883 | 17.907 | 17.931 | 18.036 | 17.809 | 17.627 | 17.466 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Consumer Transformation | 3.507 | 3.302 | 3.016 | 2.66 | 2.355 | 1.987 | 1.541 | -1.506 | -6.436 | -9.617 | -12.085 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Consumer Transformation | 13.874 | 13.764 | 13.574 | 13.338 | 13.274 | 13.202 | 13.104 | 12.577 | 9.732 | 7.403 | 5.054 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Consumer Transformation | 14.304 | 14.363 | 14.405 | 14.435 | 14.487 | 14.536 | 14.576 | 14.738 | 14.462 | 14.249 | 14.022 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Consumer Transformation | 15.689 | 15.726 | 15.742 | 15.738 | 15.755 | 15.768 | 15.769 | 15.758 | 15.023 | 14.443 | 13.892 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Consumer Transformation | 9.621 | 9.06 | 8.251 | 7.305 | 6.642 | 5.961 | 5.142 | 1.622 | -4.211 | -8.489 | -12.554 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Consumer Transformation | 14.757 | 14.657 | 14.502 | 14.304 | 14.211 | 14.108 | 13.987 | 13.257 | 10.509 | 8.226 | 6.017 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Consumer Transformation | 6.032 | 5.96 | 5.806 | 5.587 | 5.5 | 5.404 | 5.274 | 4.592 | 1.182 | -1.539 | -4.13 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Consumer Transformation | 14.001 | 13.819 | 13.535 | 13.191 | 12.935 | 12.665 | 12.327 | 10.819 | 8.068 | 6.107 | 4.344 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Consumer Transformation | 17.532 | 13.967 | 13.916 | 13.858 | 13.816 | 13.77 | 13.704 | 13.434 | 13.032 | 12.799 | 12.61 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Consumer Transformation | 10.948 | 10.691 | 10.337 | 9.944 | 9.678 | 9.399 | 9.061 | 7.516 | 4.83 | 2.851 | 0.958 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Consumer Transformation | 2.71 | 2.514 | 2.232 | 1.895 | 1.64 | 1.357 | 1.014 | -0.877 | -3.772 | -5.667 | -7.233 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Consumer Transformation | 11.13 | 10.751 | 10.227 | 9.663 | 9.311 | 8.949 | 8.503 | 6.685 | 3.504 | 1.191 | -1.136 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Consumer Transformation | 12.603 | 12.39 | 12.058 | 11.662 | 11.42 | 11.165 | 10.843 | 9.405 | 6.373 | 4.146 | 2.045 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Consumer Transformation | 5.61 | 5.455 | 5.223 | 4.908 | 4.623 | 4.287 | 3.88 | 1.176 | -4.281 | -8.247 | -11.508 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Consumer Transformation | 16.526 | 16.384 | 16.187 | 15.952 | 15.755 | 15.55 | 15.306 | 14.174 | 12.195 | 10.638 | 9.217 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Consumer Transformation | 11.725 | 9.958 | 9.638 | 9.234 | 8.946 | 8.618 | 8.229 | 5.746 | 0.211 | -3.901 | -7.451 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Consumer Transformation | 4.698 | 4.576 | 4.411 | 4.22 | 4.063 | 3.901 | 3.707 | 2.874 | 1.679 | 0.772 | -0.081 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Consumer Transformation | 14.8 | 14.512 | 14.079 | 13.563 | 13.195 | 12.813 | 12.344 | 10.344 | 7.126 | 4.882 | 2.834 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Consumer Transformation | 0.025 | -0.152 | -0.401 | -0.694 | -0.946 | -1.212 | -1.536 | -3.07 | -5.88 | -8.018 | -9.927 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Consumer Transformation | 9.318 | 8.976 | 8.487 | 7.91 | 7.47 | 7.013 | 6.461 | 3.995 | -0.884 | -4.686 | -8.257 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Consumer Transformation | 8.424 | 8.121 | 7.646 | 7.068 | 6.683 | 6.274 | 5.756 | 3.41 | -1.281 | -4.72 | -7.914 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Consumer Transformation | 5.533 | 5.087 | 4.452 | 3.696 | 3.142 | 2.564 | 1.868 | -1.269 | -7.744 | -12.851 | -17.77 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Consumer Transformation | 16.05 | 15.755 | 15.31 | 14.775 | 14.39 | 13.98 | 13.466 | 11.12 | 7.191 | 4.455 | 1.972 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Consumer Transformation | 8.271 | 8.311 | 8.307 | 8.256 | 8.255 | 8.238 | 8.197 | 7.809 | 5.918 | 4.581 | 3.439 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Consumer Transformation | 16.408 | 17.192 | 16.903 | 8.368 | 8.055 | 7.735 | 7.35 | 5.688 | 2.376 | -0.34 | -2.788 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Consumer Transformation | 10.962 | 10.51 | 9.874 | 9.121 | 8.502 | 7.861 | 7.093 | 3.682 | -1.612 | -5.506 | -9.015 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Consumer Transformation | 8.803 | 8.813 | 8.785 | 8.719 | 8.709 | 8.69 | 8.652 | 8.388 | 6.735 | 5.451 | 4.25 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Consumer Transformation | 10.772 | 10.305 | 9.639 | 8.866 | 8.348 | 7.816 | 7.165 | 4.424 | -0.564 | -4.27 | -7.803 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Consumer Transformation | 5.074 | 4.55 | 3.835 | 2.979 | 2.245 | 1.457 | 0.511 | -4.293 | -12.021 | -17.852 | -23.137 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Consumer Transformation | 13.01 | 13.079 | 13.144 | 13.2 | 13.253 | 13.303 | 13.351 | 13.554 | 13.479 | 13.426 | 13.381 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Consumer Transformation | 13.761 | 13.852 | 13.925 | 13.976 | 14.008 | 14.019 | 14.007 | 13.677 | 12.888 | 12.522 | 12.375 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Consumer Transformation | 2.767 | 2.852 | 2.926 | 2.988 | 3.049 | 3.105 | 3.151 | 3.327 | 3.089 | 2.942 | 2.829 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Consumer Transformation | 6.342 | 6.184 | 5.963 | 5.725 | 5.574 | 5.416 | 5.213 | 4.318 | 2.368 | 0.989 | -0.242 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Consumer Transformation | 1.865 | 1.707 | 1.503 | 1.281 | 1.083 | 0.877 | 0.629 | -0.521 | -2.164 | -3.363 | -4.402 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Consumer Transformation | 12.678 | 12.433 | 12.064 | 11.612 | 11.246 | 10.852 | 10.373 | 8.054 | 4.345 | 1.75 | -0.442 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Consumer Transformation | 12.617 | 10.64 | 10.646 | 10.629 | 10.607 | 10.574 | 10.521 | 10.138 | 8.595 | 7.487 | 6.589 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Consumer Transformation | 9.171 | 8.791 | 15.295 | 14.798 | 14.438 | 14.062 | 13.591 | 11.574 | 7.753 | 4.895 | 2.252 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Consumer Transformation | 11.49 | 11.383 | 11.223 | 11.017 | 10.896 | 10.755 | 10.586 | 9.443 | 6.385 | 4.011 | 1.852 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Consumer Transformation | 3.11 | 1.442 | 0.91 | 0.486 | 0.177 | -0.148 | -0.559 | -2.432 | -7.286 | -11.132 | -14.648 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Consumer Transformation | 12.954 | 12.932 | 12.888 | 12.822 | 12.797 | 12.768 | 12.729 | 12.503 | 11.457 | 10.54 | 9.623 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Consumer Transformation | 8.521 | 8.363 | 15.074 | 14.702 | 14.511 | 14.304 | 14.029 | 12.728 | 9.095 | 6.394 | 3.852 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Consumer Transformation | 5.153 | 3.919 | 3.314 | 2.82 | 2.418 | 1.99 | 1.464 | -1.134 | -5.931 | -9.462 | -12.591 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Consumer Transformation | 10.172 | 9.698 | 8.993 | 8.166 | 7.672 | 7.163 | 6.542 | 3.929 | -1.546 | -5.678 | -9.732 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Consumer Transformation | 12.836 | 12.711 | 10.432 | 10.17 | 9.931 | 9.625 | 9.238 | 6.402 | 2.286 | -0.094 | -1.677 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Consumer Transformation | 9.441 | 9.016 | 8.419 | 7.731 | 7.239 | 6.724 | 6.097 | 3.239 | -1.144 | -4.262 | -7.159 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Consumer Transformation | 7.784 | 5.814 | 5.349 | 4.842 | 4.516 | 4.174 | 3.749 | 1.826 | -2.653 | -6.033 | -9.187 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Consumer Transformation | 8.563 | 7.895 | 7.965 | 7.99 | 7.996 | 7.976 | 7.926 | 7.324 | 5.259 | 3.963 | 3.052 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Consumer Transformation | 18.889 | 18.869 | 18.818 | 18.73 | 18.629 | 18.491 | 18.31 | 16.893 | 14.705 | 13.536 | 12.876 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Consumer Transformation | 8.635 | 8.514 | 8.28 | 7.979 | 7.816 | 7.645 | 7.416 | 6.452 | 3.671 | 1.504 | -0.614 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Consumer Transformation | 10.564 | 10.397 | 10.14 | 9.824 | 9.497 | 9.146 | 8.71 | 6.657 | 3.272 | 0.714 | -1.416 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Consumer Transformation | 12.427 | 12.183 | 11.8 | 11.327 | 11.041 | 10.744 | 10.377 | 8.789 | 4.759 | 1.67 | -1.273 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Consumer Transformation | 12.365 | 12.35 | 12.286 | 12.186 | 12.156 | 12.115 | 12.051 | 11.623 | 9.915 | 8.7 | 7.592 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Consumer Transformation | 8.405 | 8.529 | 8.644 | 8.758 | 8.868 | 8.967 | 9.053 | 9.407 | 9.081 | 8.841 | 8.626 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Consumer Transformation | 8.256 | 6.392 | 6.219 | 6.001 | 5.943 | 5.865 | 5.746 | 4.931 | 1.801 | -0.53 | -2.708 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Consumer Transformation | 10.373 | 9.199 | 9.267 | 9.311 | 9.359 | 9.402 | 9.432 | 9.555 | 8.801 | 8.226 | 7.707 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Consumer Transformation | 1.697 | 1.513 | 1.261 | 0.969 | 0.745 | 0.51 | 0.226 | -1.065 | -3.338 | -5.125 | -6.84 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 3.426 | 3.388 | 3.328 | 3.261 | 3.248 | 3.233 | 3.21 | 3.093 | 2.284 | 1.629 | 0.943 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Consumer Transformation | 13.863 | 13.78 | 13.643 | 13.458 | 13.307 | 13.123 | 12.894 | 11.366 | 8.823 | 7.229 | 6.019 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Consumer Transformation | 24.617 | 24.651 | 24.681 | 24.696 | 24.708 | 24.718 | 24.726 | 24.735 | 24.11 | 23.535 | 22.977 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Consumer Transformation | 14.97 | 14.996 | 14.993 | 14.968 | 14.973 | 14.974 | 14.961 | 14.914 | 14.066 | 13.378 | 12.719 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Consumer Transformation | -0.824 | -0.922 | -1.07 | -1.263 | -1.419 | -1.591 | -1.793 | -2.919 | -5.25 | -7.12 | -8.832 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Consumer Transformation | 3.752 | 3.528 | 3.208 | 2.784 | 2.426 | 1.996 | 1.473 | -2.09 | -8.865 | -13.574 | -17.439 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Consumer Transformation | 11.081 | 10.898 | 10.584 | 10.192 | 9.946 | 9.691 | 9.366 | 8.014 | 4.829 | 2.424 | 0.151 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Consumer Transformation | 11.733 | 11.844 | 11.939 | 12.018 | 12.082 | 12.129 | 12.156 | 12.095 | 11.776 | 11.706 | 11.764 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Consumer Transformation | 8.611 | 8.219 | 7.639 | 6.945 | 6.449 | 5.922 | 5.28 | 2.161 | -3.996 | -8.532 | -12.605 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Consumer Transformation | 17.103 | 16.434 | 16.358 | 16.261 | 16.203 | 16.144 | 16.076 | 15.735 | 14.213 | 12.881 | 11.581 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Consumer Transformation | 4.926 | 4.616 | 4.226 | 3.846 | 3.539 | 3.227 | 2.848 | 1.291 | -1.812 | -4.232 | -6.408 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Consumer Transformation | 8.595 | 8.368 | 7.972 | 7.459 | 7.08 | 6.685 | 6.189 | 4.05 | -0.953 | -4.931 | -8.63 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Consumer Transformation | -1.179 | -1.381 | -1.672 | -2.008 | -2.236 | -2.472 | -2.759 | -4.014 | -7.094 | -9.521 | -11.815 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Consumer Transformation | 15.398 | 15.355 | 15.278 | 15.159 | 15.043 | 14.905 | 14.734 | 13.572 | 10.912 | 9.005 | 7.444 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Consumer Transformation | 15.759 | 15.175 | 14.591 | 14.209 | 13.892 | 13.557 | 13.144 | 11.187 | 7.644 | 5.049 | 2.808 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Consumer Transformation | 10.773 | 10.406 | 9.841 | 9.17 | 8.756 | 8.323 | 7.786 | 5.489 | 1.402 | -1.523 | -4.404 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Consumer Transformation | 24.272 | 24.316 | 24.355 | 24.394 | 24.433 | 24.468 | 24.498 | 24.621 | 24.437 | 24.291 | 24.157 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Consumer Transformation | 8.481 | 8.512 | 8.538 | 8.558 | 8.575 | 8.589 | 8.599 | 8.63 | 7.687 | 6.93 | 6.259 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Consumer Transformation | 11.261 | 10.953 | 10.471 | 9.887 | 9.533 | 9.169 | 8.718 | 6.853 | 3.094 | 0.274 | -2.516 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Consumer Transformation | -0.7 | -0.722 | -0.763 | -0.818 | -0.84 | -0.866 | -0.898 | -1.105 | -1.829 | -2.482 | -3.138 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Consumer Transformation | 9.306 | 9.206 | 9.062 | 8.88 | 8.757 | 8.627 | 8.474 | 7.66 | 5.532 | 3.781 | 2.095 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Consumer Transformation | 13.414 | 13.117 | 12.67 | 12.144 | 11.807 | 11.458 | 11.026 | 9.17 | 5.095 | 1.903 | -1.189 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Consumer Transformation | 11.59 | 11.353 | 11.021 | 10.627 | 10.34 | 10.042 | 9.69 | 8.051 | 4.816 | 2.381 | 0.147 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Consumer Transformation | 8.312 | 7.961 | 7.467 | 6.88 | 6.344 | 5.784 | 5.113 | 2.089 | -2.326 | -5.55 | -8.356 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Consumer Transformation | 13.557 | 13.351 | 13.096 | 12.792 | 12.517 | 12.217 | 11.874 | 9.846 | 5.978 | 2.932 | 0.232 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Consumer Transformation | 7.706 | 7.686 | 7.585 | 7.41 | 7.291 | 7.141 | 6.934 | 5.524 | 1.253 | -1.888 | -4.522 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Consumer Transformation | 14.047 | 13.791 | 13.398 | 12.931 | 12.649 | 12.357 | 11.997 | 10.482 | 7.329 | 4.959 | 2.619 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Consumer Transformation | 7.395 | 6.988 | 6.458 | 5.924 | 5.537 | 5.135 | 4.637 | 2.472 | -2.46 | -6.306 | -9.859 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Consumer Transformation | 8.096 | 7.948 | 7.738 | 7.469 | 7.277 | 7.064 | 6.816 | 5.399 | 1.641 | -1.405 | -4.297 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Falling Short | 13.225 | 13.111 | 13.032 | 12.994 | 12.94 | 12.872 | 12.804 | 12.502 | 12.279 | 12.121 | 11.98 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Falling Short | 12.519 | 10.893 | 10.865 | 10.812 | 10.727 | 10.61 | 10.467 | 9.494 | 8.244 | 7.364 | 7.053 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Falling Short | 11.479 | 11.189 | 10.854 | 10.468 | 10.022 | 9.522 | 9.029 | 6.704 | 4.714 | 3.293 | 2.177 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Falling Short | 5.801 | 4.383 | 4.396 | 4.384 | 4.349 | 4.294 | 4.231 | 3.782 | 3.184 | 2.781 | 2.628 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 5.489 | 5.328 | 5.151 | 4.961 | 4.721 | 4.438 | 4.168 | 3.101 | 2.478 | 2.156 | 1.965 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 5.319 | 5.319 | 5.313 | 5.302 | 5.281 | 5.252 | 5.222 | 5.092 | 4.996 | 4.934 | 4.89 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Falling Short | 10.054 | 9.751 | 9.398 | 8.994 | 8.517 | 7.976 | 7.45 | 5.086 | 3.096 | 1.628 | 0.474 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Falling Short | 17.051 | 17.071 | 17.085 | 17.087 | 17.076 | 17.059 | 17.04 | 16.945 | 16.839 | 16.768 | 16.715 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Falling Short | 1.355 | 1.19 | 0.988 | 0.747 | 0.458 | 0.127 | -0.2 | -1.68 | -2.866 | -3.693 | -4.313 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Falling Short | 2.78 | 2.187 | 2.251 | 2.299 | 2.334 | 2.359 | 2.379 | 2.415 | 2.35 | 2.285 | 2.233 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Falling Short | 12.056 | 11.929 | 11.766 | 11.563 | 11.315 | 11.026 | 10.744 | 9.491 | 8.481 | 7.764 | 7.236 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Falling Short | 2.623 | 2.487 | 2.332 | 2.146 | 1.893 | 1.581 | 1.261 | -0.357 | -1.919 | -2.927 | -3.389 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Falling Short | 3.04 | 3.018 | 2.991 | 2.961 | 2.925 | 2.884 | 2.842 | 2.612 | 2.357 | 2.125 | 1.929 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Falling Short | 15.803 | 15.734 | 15.634 | 15.504 | 15.334 | 15.132 | 14.938 | 14.145 | 13.614 | 13.318 | 13.129 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Falling Short | 12.837 | 12.34 | 12.292 | 12.236 | 12.17 | 12.098 | 12.025 | 11.647 | 11.256 | 10.879 | 10.504 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Falling Short | 10.487 | 10.495 | 10.487 | 10.457 | 10.406 | 10.336 | 10.261 | 9.823 | 9.309 | 8.955 | 8.779 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Falling Short | 15.568 | 15.361 | 15.106 | 14.8 | 14.427 | 13.992 | 13.56 | 11.558 | 9.883 | 8.758 | 8.074 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Falling Short | 8.386 | 8.396 | 8.397 | 8.386 | 8.362 | 8.325 | 8.282 | 7.997 | 7.639 | 7.39 | 7.291 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Falling Short | 6.495 | 6.34 | 6.166 | 5.967 | 5.743 | 5.501 | 5.258 | 4.043 | 2.887 | 1.902 | 0.986 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Falling Short | 21.767 | 21.738 | 21.686 | 21.613 | 21.515 | 21.394 | 21.277 | 20.803 | 20.515 | 20.35 | 20.246 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Falling Short | 3.695 | 3.557 | 3.41 | 3.254 | 3.086 | 2.907 | 2.728 | 1.825 | 0.931 | 0.099 | -0.687 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Falling Short | 11.444 | 11.134 | 10.764 | 10.331 | 9.811 | 9.212 | 8.615 | 5.746 | 3.156 | 1.25 | -0.102 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Falling Short | 9.667 | 9.484 | 9.265 | 9.012 | 8.69 | 8.306 | 7.933 | 6.36 | 5.285 | 4.678 | 4.363 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Falling Short | 14.907 | 14.748 | 14.566 | 14.364 | 14.117 | 13.827 | 13.548 | 12.399 | 11.695 | 11.311 | 11.045 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Falling Short | 2.357 | 2.362 | 2.33 | 2.257 | 2.135 | 1.97 | 1.787 | 0.691 | -0.588 | -1.479 | -1.867 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Falling Short | 5.809 | 5.64 | 5.44 | 5.207 | 4.932 | 4.617 | 4.3 | 2.744 | 1.27 | 0.121 | -0.698 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 15.112 | 15.097 | 15.075 | 15.044 | 15.002 | 14.952 | 14.897 | 14.595 | 14.274 | 14.057 | 13.944 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 4.13 | 1.053 | 1.023 | 0.957 | 0.849 | 0.701 | 0.528 | -0.617 | -2.04 | -3.029 | -3.441 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Falling Short | 8.122 | 8.029 | 7.904 | 7.739 | 7.529 | 7.275 | 6.997 | 5.391 | 3.564 | 2.194 | 1.429 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Falling Short | 11.795 | 11.637 | 11.43 | 11.175 | 10.857 | 10.483 | 10.12 | 8.606 | 7.613 | 7.039 | 6.662 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Falling Short | 6.135 | 5.868 | 5.53 | 5.118 | 4.605 | 3.999 | 3.394 | 0.605 | -1.726 | -3.295 | -4.22 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Falling Short | 6.826 | 6.806 | 6.784 | 6.759 | 6.732 | 6.704 | 6.675 | 6.538 | 6.406 | 6.287 | 6.174 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Falling Short | 4.296 | 4.259 | 4.216 | 4.167 | 4.109 | 4.043 | 3.977 | 3.631 | 3.283 | 2.997 | 2.777 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Falling Short | 13.759 | 13.616 | 13.43 | 13.2 | 12.914 | 12.577 | 12.248 | 10.82 | 9.711 | 8.98 | 8.488 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 13.763 | 13.585 | 13.405 | 13.218 | 13.027 | 12.833 | 12.637 | 11.617 | 10.518 | 9.398 | 8.263 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Falling Short | 5.543 | 5.494 | 5.436 | 5.369 | 5.288 | 5.196 | 5.107 | 4.725 | 4.431 | 4.225 | 4.071 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 10.622 | 10.492 | 10.316 | 10.091 | 9.799 | 9.447 | 9.108 | 7.68 | 6.687 | 6.121 | 5.783 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Falling Short | 11.584 | 11.443 | 11.254 | 11.015 | 10.705 | 10.327 | 9.957 | 8.337 | 7.134 | 6.439 | 6.122 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Falling Short | 9.178 | 9.199 | 9.205 | 9.194 | 9.165 | 9.12 | 9.067 | 8.715 | 8.274 | 7.958 | 7.79 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Falling Short | 10.271 | 10.27 | 10.251 | 10.21 | 10.143 | 10.053 | 9.966 | 9.567 | 9.246 | 9.058 | 8.957 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Falling Short | 17.459 | 17.36 | 17.234 | 17.083 | 16.894 | 16.671 | 16.446 | 15.36 | 14.35 | 13.645 | 13.251 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Falling Short | 7.939 | 22.533 | 22.401 | 22.241 | 22.036 | 21.794 | 21.56 | 20.581 | 19.927 | 19.56 | 19.335 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Falling Short | 10.715 | 10.398 | 10.015 | 9.565 | 9.033 | 8.427 | 7.844 | 5.392 | 3.685 | 2.492 | 1.504 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Falling Short | 3.862 | 3.813 | 3.757 | 3.695 | 3.614 | 3.517 | 3.425 | 3.06 | 2.84 | 2.726 | 2.66 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Falling Short | 6.527 | 6.174 | 5.774 | 5.334 | 4.799 | 4.172 | 3.553 | 0.795 | -1.167 | -2.34 | -3.038 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Falling Short | 4.539 | 4.18 | 3.752 | 3.245 | 2.643 | 1.953 | 1.273 | -1.851 | -4.449 | -6.307 | -7.685 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Falling Short | 5.929 | 5.523 | 5.037 | 4.468 | 3.796 | 3.029 | 2.282 | -1.003 | -3.55 | -5.401 | -6.847 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Falling Short | 4.23 | 4.254 | 4.274 | 4.287 | 4.295 | 4.295 | 4.292 | 4.212 | 4.057 | 3.927 | 3.856 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Falling Short | 7.86 | 7.607 | 7.27 | 6.846 | 6.308 | 5.66 | 4.99 | 1.62 | -1.613 | -3.813 | -4.865 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Falling Short | 12.915 | 12.955 | 12.988 | 13.008 | 13.018 | 13.021 | 13.019 | 12.924 | 12.72 | 12.571 | 12.508 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Falling Short | 10.149 | 10.211 | 10.267 | 10.317 | 10.361 | 10.4 | 10.436 | 10.557 | 10.602 | 10.616 | 10.616 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Falling Short | 10.869 | 10.919 | 10.963 | 10.994 | 11.003 | 10.994 | 10.98 | 10.836 | 10.594 | 10.421 | 10.317 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Falling Short | 11.643 | 11.673 | 11.696 | 11.709 | 11.71 | 11.702 | 11.692 | 11.626 | 11.543 | 11.485 | 11.446 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Falling Short | 10.93 | 10.811 | 10.643 | 10.426 | 10.138 | 9.78 | 9.41 | 7.573 | 5.796 | 4.625 | 4.14 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Falling Short | 4.256 | 4.185 | 4.1 | 4 | 3.879 | 3.739 | 3.604 | 3.031 | 2.606 | 2.284 | 2.021 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Falling Short | 5.005 | 4.877 | 4.737 | 4.586 | 4.421 | 4.244 | 4.065 | 3.144 | 2.196 | 1.24 | 0.277 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Falling Short | 13.906 | 13.674 | 13.414 | 13.127 | 12.765 | 12.333 | 11.917 | 10.18 | 9.014 | 8.368 | 8.039 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Falling Short | -0.08 | -0.113 | -0.15 | -0.195 | -0.246 | -0.304 | -0.365 | -0.692 | -1.051 | -1.387 | -1.684 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Falling Short | 3.338 | 3.212 | 3.064 | 2.895 | 2.692 | 2.46 | 2.237 | 1.265 | 0.516 | -0.01 | -0.418 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 9.514 | 9.444 | 9.328 | 9.165 | 8.945 | 8.672 | 8.393 | 6.982 | 5.504 | 4.456 | 3.889 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Falling Short | 9.186 | 9.13 | 9.07 | 9.003 | 8.906 | 8.782 | 8.662 | 8.138 | 7.738 | 7.501 | 7.358 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Falling Short | 5.311 | 5.092 | 4.843 | 4.559 | 4.226 | 3.851 | 3.478 | 1.715 | 0.146 | -1.066 | -2.014 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Falling Short | 4.763 | 4.773 | 4.78 | 4.784 | 4.782 | 4.777 | 4.769 | 4.7 | 4.597 | 4.524 | 4.495 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Falling Short | 22.005 | 21.923 | 21.826 | 21.711 | 21.561 | 21.381 | 21.208 | 20.507 | 20.059 | 19.817 | 19.665 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Falling Short | 7.823 | 7.855 | 7.883 | 7.901 | 7.906 | 7.9 | 7.892 | 7.82 | 7.702 | 7.616 | 7.556 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Falling Short | 13.624 | 13.46 | 13.285 | 13.101 | 12.865 | 12.579 | 12.306 | 11.214 | 10.547 | 10.196 | 9.997 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Falling Short | 7.186 | 7.174 | 7.134 | 7.058 | 6.941 | 6.789 | 6.637 | 5.927 | 5.338 | 5.003 | 4.849 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Falling Short | 4.926 | 4.615 | 4.245 | 3.819 | 3.277 | 2.634 | 2.007 | -0.601 | -2.368 | -3.373 | -3.913 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Falling Short | 0.931 | 0.89 | 0.846 | 0.796 | 0.74 | 0.679 | 0.616 | 0.289 | -0.056 | -0.349 | -0.586 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Falling Short | 2.994 | 2.823 | 2.632 | 2.417 | 2.171 | 1.899 | 1.611 | 0.02 | -1.75 | -3.269 | -4.436 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Falling Short | 12.942 | 12.908 | 12.847 | 12.76 | 12.639 | 12.489 | 12.344 | 11.74 | 11.334 | 11.119 | 11.021 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Falling Short | 14.805 | 14.715 | 15.584 | 15.408 | 15.181 | 14.907 | 14.645 | 13.568 | 12.878 | 12.524 | 12.333 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Falling Short | 22.201 | 22.19 | 22.139 | 22.031 | 21.861 | 21.627 | 21.334 | 19.243 | 16.426 | 14.472 | 13.857 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Falling Short | 9.7 | 9.449 | 9.158 | 8.823 | 8.433 | 7.995 | 7.562 | 5.546 | 3.821 | 2.493 | 1.426 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Falling Short | 2.461 | 2.34 | 2.192 | 2.014 | 1.797 | 1.547 | 1.3 | 0.172 | -0.756 | -1.384 | -1.797 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Falling Short | 8.028 | 7.863 | 7.626 | 7.318 | 6.926 | 6.461 | 6.016 | 4.201 | 3.091 | 2.494 | 2.098 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Falling Short | 6.042 | 3.741 | 3.728 | 3.702 | 3.661 | 3.61 | 3.552 | 3.215 | 2.837 | 2.58 | 2.459 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Falling Short | 7.554 | 7.328 | 7.036 | 6.676 | 6.221 | 5.678 | 5.153 | 3.012 | 1.589 | 0.781 | 0.314 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Falling Short | 3.954 | 3.796 | 18.289 | 18.035 | 17.71 | 17.321 | 16.938 | 15.248 | 13.979 | 13.234 | 12.859 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Falling Short | -0.199 | -0.312 | -0.443 | -0.595 | -0.774 | -0.975 | -1.17 | -2.022 | -2.686 | -3.193 | -3.625 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Falling Short | 2.809 | 2.816 | 2.816 | 2.808 | 2.791 | 2.767 | 2.741 | 2.57 | 2.356 | 2.209 | 2.142 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Falling Short | 10.394 | 10.23 | 10.009 | 9.732 | 9.382 | 8.966 | 8.567 | 6.947 | 5.942 | 5.408 | 5.086 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Falling Short | 8.507 | 8.367 | 8.175 | 7.93 | 7.615 | 7.238 | 6.863 | 5.181 | 3.808 | 2.949 | 2.477 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Falling Short | 12.355 | 12.263 | 12.147 | 12.003 | 11.825 | 11.615 | 11.404 | 10.383 | 9.437 | 8.717 | 8.2 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Falling Short | 3.648 | 2.67 | 2.675 | 2.651 | 2.594 | 2.505 | 2.399 | 1.707 | 0.85 | 0.25 | 0.011 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Falling Short | 15.159 | 15.055 | 14.936 | 14.796 | 14.633 | 14.448 | 14.248 | 13.054 | 11.615 | 10.433 | 9.639 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Falling Short | 4.061 | 3.989 | 3.903 | 3.803 | 3.684 | 3.549 | 3.417 | 2.837 | 2.382 | 2.048 | 1.775 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Falling Short | 2.459 | 2.426 | 2.382 | 2.324 | 2.249 | 2.159 | 2.073 | 1.72 | 1.493 | 1.368 | 1.289 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Falling Short | 14.939 | 14.72 | 14.449 | 14.123 | 13.722 | 13.253 | 12.78 | 10.522 | 8.517 | 7.101 | 6.202 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Falling Short | 1.897 | 1.804 | 1.662 | 1.464 | 1.198 | 0.874 | 0.554 | -0.875 | -1.956 | -2.562 | -2.891 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Falling Short | 14.751 | 14.739 | 14.709 | 14.66 | 14.589 | 14.501 | 14.41 | 13.952 | 13.504 | 13.2 | 13.022 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Falling Short | 4.698 | 4.621 | 4.53 | 4.423 | 4.297 | 4.153 | 4.013 | 3.388 | 2.89 | 2.538 | 2.273 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Falling Short | 6.85 | 6.581 | 6.249 | 5.848 | 5.354 | 4.777 | 4.215 | 1.749 | -0.182 | -1.488 | -2.369 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Falling Short | 12.547 | 12.35 | 12.107 | 11.82 | 11.471 | 11.07 | 10.681 | 9.032 | 7.827 | 7.008 | 6.378 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Falling Short | 12.76 | 11.125 | 11.097 | 11.028 | 10.91 | 10.738 | 10.522 | 8.95 | 6.799 | 5.274 | 4.775 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Falling Short | 3.083 | 2.952 | 2.826 | 2.707 | 2.555 | 2.372 | 2.199 | 1.516 | 1.085 | 0.843 | 0.703 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Falling Short | 7.986 | 7.586 | 7.111 | 6.568 | 5.923 | 5.185 | 4.466 | 1.288 | -1.288 | -3.152 | -4.582 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Falling Short | 8.401 | 8.337 | 8.268 | 8.195 | 8.117 | 8.033 | 7.948 | 7.497 | 7.011 | 6.504 | 5.991 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Falling Short | 2.029 | 1.896 | 1.718 | 1.484 | 1.174 | 0.779 | 0.323 | -2.565 | -6.116 | -8.606 | -9.465 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Falling Short | 11.909 | 11.726 | 11.529 | 11.318 | 11.051 | 10.734 | 10.421 | 9.043 | 8.01 | 7.386 | 7.035 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Falling Short | 9.281 | 9.075 | 8.805 | 8.471 | 8.051 | 7.553 | 7.055 | 4.763 | 2.847 | 1.577 | 0.863 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Falling Short | 0.79 | 0.682 | 0.553 | 0.4 | 0.217 | 0.001 | -0.235 | -1.614 | -3.214 | -4.459 | -5.169 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Falling Short | 7.387 | 7.169 | 6.894 | 6.56 | 6.15 | 5.673 | 5.213 | 3.293 | 1.96 | 1.091 | 0.429 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Falling Short | 0.791 | 0.786 | 0.762 | 0.715 | 0.641 | 0.545 | 0.447 | -0.067 | -0.589 | -0.95 | -1.156 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Falling Short | 1.481 | 1.479 | 1.475 | 1.471 | 1.467 | 1.463 | 1.458 | 1.435 | 1.411 | 1.385 | 1.359 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 10.321 | 10.341 | 10.345 | 10.327 | 10.291 | 10.24 | 10.188 | 9.932 | 9.684 | 9.514 | 9.38 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 7.077 | 7.064 | 7.041 | 7.008 | 6.961 | 6.904 | 6.848 | 6.597 | 6.396 | 6.276 | 6.199 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 8.488 | 8.421 | 8.339 | 8.241 | 8.124 | 7.987 | 7.856 | 7.309 | 6.922 | 6.651 | 6.436 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 3.864 | 3.729 | 3.571 | 3.389 | 3.167 | 2.908 | 2.644 | 1.343 | 0.146 | -0.72 | -1.261 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Falling Short | 14.502 | 14.258 | 13.968 | 14.631 | 14.235 | 13.787 | 13.353 | 11.431 | 9.921 | 8.894 | 8.088 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Falling Short | 10.041 | 9.1 | 8.934 | 8.721 | 8.449 | 8.129 | 7.819 | 6.519 | 5.627 | 5.086 | 4.724 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Falling Short | 3.231 | 3.072 | 2.887 | 2.673 | 2.416 | 2.119 | 1.81 | 0.181 | -1.489 | -2.742 | -3.496 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Falling Short | 11.144 | 10.826 | 10.551 | 10.327 | 10.043 | 9.705 | 9.378 | 8.046 | 7.2 | 6.735 | 6.458 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Falling Short | 10.578 | 10.452 | 10.32 | 10.178 | 10.028 | 9.872 | 9.714 | 8.883 | 8.006 | 7.132 | 6.249 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Falling Short | -3.015 | -3.484 | -4.041 | -4.692 | -5.469 | -6.36 | -7.225 | -10.994 | -13.842 | -15.807 | -17.268 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Falling Short | 7.22 | 6.929 | 6.594 | 6.226 | 5.763 | 5.216 | 4.693 | 2.588 | 1.122 | 0.209 | -0.404 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Falling Short | 5.088 | 5.128 | 5.146 | 5.139 | 5.107 | 5.055 | 4.996 | 4.658 | 4.318 | 4.087 | 3.93 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 17.183 | 14.152 | 14.001 | 13.831 | 13.641 | 13.435 | 13.232 | 12.273 | 11.396 | 10.643 | 9.948 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Falling Short | 13.726 | 13.637 | 13.539 | 13.423 | 13.292 | 13.144 | 12.985 | 12.044 | 10.938 | 9.994 | 9.295 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Falling Short | 9.387 | 9.107 | 8.803 | 8.464 | 8.086 | 7.665 | 7.208 | 4.521 | 1.344 | -1.34 | -3.198 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Falling Short | 12.62 | 12.628 | 12.619 | 12.59 | 12.541 | 12.478 | 12.416 | 12.121 | 11.868 | 11.715 | 11.603 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Falling Short | 11.431 | 11.462 | 11.48 | 11.483 | 11.471 | 11.447 | 11.42 | 11.285 | 11.144 | 11.044 | 10.981 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 3.923 | 3.65 | 3.36 | 3.042 | 2.695 | 2.314 | 1.898 | -0.575 | -3.539 | -6.104 | -7.95 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Falling Short | 16.245 | 16.183 | 16.11 | 16.024 | 15.924 | 15.811 | 15.691 | 15.018 | 14.274 | 13.651 | 13.183 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Falling Short | 10.743 | 10.646 | 10.503 | 10.313 | 10.064 | 9.765 | 9.474 | 8.25 | 7.363 | 6.841 | 6.546 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Falling Short | 10.228 | 10.202 | 10.151 | 10.072 | 9.959 | 9.819 | 9.672 | 8.92 | 8.185 | 7.692 | 7.43 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Falling Short | 7.104 | 6.935 | 6.7 | 6.398 | 6.006 | 5.529 | 5.056 | 2.916 | 1.2 | 0.167 | -0.297 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Falling Short | 4.494 | 4.255 | 3.972 | 3.639 | 3.232 | 2.753 | 2.27 | -0.097 | -2.325 | -3.963 | -4.984 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Falling Short | 11.686 | 11.679 | 11.655 | 11.611 | 11.533 | 11.422 | 11.287 | 10.387 | 9.236 | 8.436 | 8.191 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Falling Short | 15.381 | 15.254 | 15.076 | 14.849 | 14.563 | 14.226 | 13.903 | 12.606 | 11.822 | 11.403 | 11.133 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Falling Short | 9.252 | 8.981 | 8.636 | 8.21 | 7.679 | 7.041 | 6.387 | 3.101 | -0.042 | -2.197 | -3.263 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Falling Short | 3.266 | 3.176 | 3.07 | 3.449 | 3.307 | 3.148 | 2.991 | 2.29 | 1.717 | 1.28 | 0.928 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Falling Short | 8.035 | 7.899 | 7.715 | 7.479 | 7.173 | 6.805 | 6.451 | 5.032 | 4.168 | 3.716 | 3.446 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Falling Short | 4.08 | 3.981 | 3.854 | 3.701 | 3.512 | 3.289 | 3.076 | 2.203 | 1.656 | 1.341 | 1.119 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 12.147 | 12.093 | 12.028 | 11.952 | 11.863 | 11.764 | 11.661 | 11.112 | 10.51 | 9.954 | 9.447 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 25.269 | 25.236 | 25.195 | 25.144 | 25.083 | 25.014 | 24.945 | 24.591 | 24.223 | 23.922 | 23.675 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Falling Short | 14.529 | 14.375 | 14.194 | 13.985 | 13.74 | 13.462 | 13.182 | 11.839 | 10.692 | 9.88 | 9.313 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Falling Short | 12.588 | 12.617 | 12.637 | 12.643 | 12.637 | 12.623 | 12.608 | 12.509 | 12.38 | 12.295 | 12.234 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Falling Short | 19.753 | 19.713 | 19.669 | 19.62 | 19.566 | 19.509 | 19.453 | 19.154 | 18.83 | 18.516 | 18.204 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Falling Short | 6.681 | 6.557 | 6.385 | 6.165 | 5.889 | 5.564 | 5.249 | 3.917 | 2.926 | 2.302 | 1.862 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 22.332 | 22.336 | 22.317 | 22.27 | 22.192 | 22.087 | 21.98 | 21.435 | 20.901 | 20.53 | 20.295 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Falling Short | 14.519 | 14.503 | 14.477 | 14.439 | 14.386 | 14.323 | 14.259 | 13.957 | 13.705 | 13.547 | 13.419 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Falling Short | 4.74 | 4.704 | 4.655 | 4.593 | 4.511 | 4.412 | 4.317 | 3.907 | 3.62 | 3.458 | 3.378 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Falling Short | 4.47 | 4.429 | 4.386 | 4.339 | 4.29 | 4.235 | 4.178 | 3.866 | 3.517 | 3.189 | 2.908 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Falling Short | 15.52 | 15.43 | 15.323 | 15.191 | 15.034 | 14.855 | 14.665 | 13.599 | 12.391 | 11.395 | 10.673 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 9.677 | 9.601 | 9.497 | 9.367 | 9.199 | 8.999 | 8.806 | 8.012 | 7.498 | 7.219 | 7.068 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 11.531 | 11.485 | 11.422 | 11.342 | 11.242 | 11.121 | 11.006 | 10.536 | 10.247 | 10.096 | 10.001 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Falling Short | 2.299 | 2.16 | 2.003 | 1.827 | 1.624 | 1.397 | 1.174 | 0.179 | -0.608 | -1.217 | -1.737 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Falling Short | 3.341 | 3.208 | 3.054 | 2.87 | 2.654 | 2.41 | 2.153 | 0.73 | -0.838 | -2.1 | -2.997 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Falling Short | 18.887 | 18.866 | 18.838 | 18.804 | 18.759 | 18.705 | 18.643 | 18.256 | 17.778 | 17.407 | 17.207 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Falling Short | 4.859 | 4.817 | 4.762 | 4.695 | 4.61 | 4.508 | 4.41 | 4.015 | 3.769 | 3.637 | 3.558 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Falling Short | 14.775 | 14.765 | 14.755 | 14.739 | 14.713 | 14.677 | 14.636 | 14.397 | 14.13 | 13.948 | 13.864 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Falling Short | 12.524 | 12.571 | 12.613 | 12.643 | 12.666 | 12.679 | 12.687 | 12.641 | 12.493 | 12.375 | 12.33 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Falling Short | 2.211 | 2.016 | 1.776 | 1.487 | 1.136 | 0.726 | 0.324 | -1.483 | -2.938 | -3.921 | -4.542 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 5.857 | 5.831 | 5.797 | 5.753 | 5.699 | 5.636 | 5.57 | 5.221 | 4.855 | 4.563 | 4.348 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 5.206 | 5.167 | 5.118 | 5.056 | 4.978 | 4.884 | 4.78 | 4.174 | 3.47 | 2.919 | 2.593 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Falling Short | 5.222 | 5.003 | 4.74 | 4.433 | 4.063 | 3.634 | 3.212 | 1.278 | -0.339 | -1.487 | -2.265 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Falling Short | 15.271 | 15.204 | 15.124 | 15.032 | 14.924 | 14.804 | 14.682 | 14.05 | 13.415 | 12.896 | 12.478 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Falling Short | 8.402 | 8.09 | 7.736 | 7.342 | 6.848 | 6.264 | 5.703 | 3.448 | 2.084 | 1.362 | 0.935 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Falling Short | 4.817 | 4.779 | 4.726 | 4.649 | 4.537 | 4.394 | 4.24 | 3.382 | 2.466 | 1.846 | 1.545 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Falling Short | 10.333 | 10.152 | 9.912 | 9.612 | 9.241 | 8.806 | 8.388 | 6.644 | 5.481 | 4.771 | 4.253 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Falling Short | 0.178 | 0.1 | 0.015 | -0.084 | -0.194 | -0.316 | -0.442 | -1.12 | -1.873 | -2.522 | -3.052 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Falling Short | 13.453 | 13.308 | 13.117 | 12.881 | 12.575 | 12.208 | 11.85 | 10.33 | 9.252 | 8.633 | 8.323 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Falling Short | 18.394 | 18.389 | 18.378 | 18.358 | 18.33 | 18.294 | 18.256 | 18.046 | 17.82 | 17.665 | 17.58 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Falling Short | 12.463 | 12.324 | 12.164 | 11.984 | 11.782 | 11.559 | 11.335 | 10.227 | 9.147 | 8.235 | 7.43 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Falling Short | 7.095 | 6.966 | 6.817 | 6.646 | 6.448 | 6.224 | 5.995 | 4.845 | 3.77 | 2.95 | 2.335 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Falling Short | 8.093 | 7.954 | 7.786 | 7.585 | 7.341 | 7.054 | 6.74 | 4.895 | 2.778 | 1.123 | 0.124 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Falling Short | 16.234 | 16.165 | 16.092 | 16.018 | 15.941 | 15.862 | 15.782 | 15.35 | 14.878 | 14.378 | 13.868 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Falling Short | 16.942 | 16.891 | 16.817 | 16.717 | 16.585 | 16.426 | 16.272 | 15.611 | 15.13 | 14.856 | 14.709 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Falling Short | 18.981 | 18.949 | 18.911 | 18.865 | 18.809 | 18.745 | 18.683 | 18.414 | 18.206 | 18.053 | 17.922 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Falling Short | 9.328 | 9.11 | 8.894 | 8.686 | 8.415 | 8.09 | 7.778 | 6.498 | 5.642 | 5.159 | 4.865 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Falling Short | 10.561 | 10.369 | 10.136 | 9.866 | 9.517 | 9.097 | 8.696 | 7.058 | 6.003 | 5.438 | 5.125 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Falling Short | -6.631 | -6.575 | -6.53 | -6.499 | -6.484 | -6.483 | -6.491 | -6.623 | -6.869 | -7.055 | -7.123 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Falling Short | 10.474 | 10.15 | 9.827 | 9.511 | 9.115 | 8.646 | 8.198 | 6.396 | 5.282 | 4.683 | 4.314 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Falling Short | 11.314 | 11.225 | 11.116 | 10.976 | 10.806 | 10.605 | 10.389 | 9.132 | 7.69 | 6.585 | 5.914 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Falling Short | 5.208 | 5.009 | 4.771 | 4.491 | 4.157 | 3.779 | 3.416 | 1.872 | 0.756 | -0.001 | -0.604 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Falling Short | 24.376 | 24.382 | 24.371 | 24.335 | 24.277 | 24.203 | 24.126 | 23.742 | 23.372 | 23.138 | 22.98 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Falling Short | 6.253 | 6.039 | 5.8 | 5.532 | 5.228 | 4.893 | 4.552 | 2.825 | 1.066 | -0.474 | -1.785 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Falling Short | 6.767 | 6.764 | 6.758 | 6.751 | 6.74 | 6.728 | 6.716 | 6.662 | 6.625 | 6.605 | 6.594 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Falling Short | 11.522 | 11.24 | 10.874 | 10.425 | 9.876 | 9.236 | 8.613 | 5.903 | 3.886 | 2.556 | 1.615 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Falling Short | 21.932 | 21.938 | 21.929 | 21.896 | 21.834 | 21.737 | 21.603 | 20.529 | 18.97 | 17.861 | 17.548 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Falling Short | 11.276 | 11.174 | 11.033 | 10.854 | 10.62 | 10.337 | 10.06 | 8.865 | 7.971 | 7.438 | 7.139 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Falling Short | 12.048 | 11.918 | 11.752 | 11.538 | 11.264 | 10.921 | 10.52 | 7.9 | 4.606 | 2.21 | 1.206 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Falling Short | 0.692 | 0.603 | 0.497 | 0.373 | 0.225 | 0.054 | -0.121 | -1.014 | -1.911 | -2.621 | -3.122 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Falling Short | 6.989 | 1.304 | 1.083 | 0.824 | 0.517 | 0.166 | -0.178 | -1.722 | -2.907 | -3.715 | -4.322 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Falling Short | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Falling Short | 4.935 | 4.742 | 4.516 | 4.257 | 3.952 | 3.61 | 3.275 | 1.753 | 0.49 | -0.495 | -1.325 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Falling Short | 12.96 | 12.858 | 12.721 | 12.533 | 12.273 | 11.934 | 11.538 | 9 | 5.854 | 3.687 | 2.991 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Falling Short | 2.248 | 2.143 | 2.007 | 1.838 | 1.614 | 1.341 | 1.066 | -0.207 | -1.284 | -1.984 | -2.366 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Falling Short | 2.284 | 2.202 | 2.115 | 2.027 | 1.912 | 1.774 | 1.641 | 1.113 | 0.779 | 0.598 | 0.491 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Falling Short | 12.955 | 12.904 | 12.824 | 12.715 | 12.568 | 12.388 | 12.212 | 11.445 | 10.885 | 10.562 | 10.381 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Falling Short | 7.794 | 7.819 | 7.839 | 7.847 | 7.842 | 7.826 | 7.81 | 7.701 | 7.548 | 7.444 | 7.37 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Falling Short | 13.501 | 13.488 | 13.458 | 13.409 | 13.339 | 13.255 | 13.168 | 12.701 | 12.207 | 11.853 | 11.617 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Falling Short | 7 | 6.661 | 6.268 | 5.819 | 5.295 | 4.703 | 4.123 | 1.49 | -0.7 | -2.4 | -3.779 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Falling Short | 12.715 | 12.708 | 12.68 | 12.623 | 12.532 | 12.402 | 12.238 | 11.059 | 9.473 | 8.355 | 7.997 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Falling Short | 13.713 | 13.732 | 13.748 | 13.759 | 13.767 | 13.772 | 13.776 | 13.772 | 13.738 | 13.701 | 13.664 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Falling Short | 5.897 | 5.893 | 5.883 | 5.87 | 5.85 | 5.824 | 5.8 | 5.692 | 5.617 | 5.575 | 5.553 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Falling Short | 14.108 | 14.126 | 14.135 | 14.131 | 14.115 | 14.092 | 14.069 | 13.937 | 13.78 | 13.677 | 13.603 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Falling Short | -4.056 | -4.181 | -4.355 | -4.579 | -4.861 | -5.196 | -5.523 | -6.905 | -7.911 | -8.525 | -8.897 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Falling Short | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Falling Short | 8.994 | 8.068 | 7.738 | 7.346 | 6.868 | 6.314 | 5.779 | 3.54 | 2.016 | 1.061 | 0.353 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Falling Short | 8.933 | 8.687 | 8.381 | 8.019 | 13.56 | 13.014 | 12.49 | 10.365 | 8.982 | 8.21 | 7.747 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Falling Short | 3.912 | 3.942 | 3.956 | 3.951 | 3.927 | 3.889 | 3.847 | 3.584 | 3.284 | 3.086 | 2.976 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Falling Short | 2.287 | 2.018 | 1.686 | 1.292 | 0.819 | 0.277 | -0.244 | -2.409 | -3.864 | -4.788 | -5.496 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Falling Short | 14.401 | 14.299 | 14.169 | 14.008 | 13.802 | 13.555 | 13.318 | 12.345 | 11.711 | 11.362 | 11.156 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Falling Short | 5.388 | 5.138 | 4.803 | 4.384 | 3.861 | 3.246 | 2.641 | -0.086 | -2.321 | -3.857 | -4.882 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Falling Short | 5.202 | 4.325 | 4.169 | 3.984 | 3.738 | 3.435 | 3.129 | 1.71 | 0.554 | -0.17 | -0.533 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Falling Short | 15.077 | 15.009 | 14.919 | 14.808 | 14.665 | 14.495 | 14.33 | 13.663 | 13.248 | 13.018 | 12.87 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Falling Short | 4.138 | 4.024 | 3.865 | 3.66 | 3.389 | 3.06 | 2.735 | 1.268 | 0.066 | -0.669 | -1.023 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Falling Short | 7.739 | 7.545 | 7.321 | 7.059 | 6.754 | 6.41 | 6.051 | 4.126 | 2.009 | 0.29 | -0.951 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Falling Short | 8.919 | 8.744 | 8.507 | 8.212 | 7.832 | 7.379 | 6.941 | 5.045 | 3.42 | 2.329 | 1.637 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Falling Short | 6.756 | 6.496 | 6.184 | 5.82 | 5.39 | 4.897 | 4.421 | 2.385 | 0.997 | 0.141 | -0.493 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Falling Short | 2.667 | 2.276 | 1.864 | 1.437 | 0.899 | 0.261 | -0.35 | -2.807 | -4.276 | -5.046 | -5.506 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Falling Short | 9.815 | 9.602 | 9.361 | 9.092 | 8.746 | 8.333 | 7.939 | 6.346 | 5.34 | 4.791 | 4.45 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Falling Short | 10.746 | 10.504 | 10.226 | 9.914 | 9.51 | 9.019 | 8.525 | 6.224 | 4.288 | 3.099 | 2.604 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Falling Short | 13.325 | 13.331 | 13.321 | 13.283 | 13.217 | 13.123 | 13.006 | 12.165 | 11.019 | 10.219 | 9.949 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Falling Short | 8.817 | 8.759 | 8.682 | 8.582 | 8.45 | 8.291 | 8.137 | 7.483 | 7.016 | 6.749 | 6.591 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Falling Short | 3.494 | 3.482 | 3.45 | 3.393 | 3.307 | 3.193 | 3.061 | 2.219 | 1.163 | 0.415 | 0.12 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Falling Short | 12.918 | 12.816 | 12.677 | 12.5 | 12.271 | 11.998 | 11.735 | 10.676 | 10.01 | 9.649 | 9.428 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Falling Short | 17.6 | 17.539 | 17.449 | 17.329 | 17.171 | 16.981 | 16.798 | 16.053 | 15.599 | 15.369 | 15.253 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Falling Short | 15.294 | 15.222 | 15.132 | 15.024 | 14.899 | 14.76 | 14.62 | 13.913 | 13.138 | 12.479 | 11.889 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Falling Short | 4.058 | 3.918 | 3.747 | 3.531 | 3.262 | 2.935 | 2.558 | 0.147 | -2.837 | -5.045 | -6.079 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Falling Short | 10.027 | 10.052 | 10.065 | 10.059 | 10.037 | 10.001 | 9.958 | 9.651 | 9.234 | 8.937 | 8.788 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Falling Short | -1.284 | -1.367 | -1.461 | -1.573 | -1.704 | -1.854 | -2.015 | -2.932 | -3.976 | -4.825 | -5.399 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Falling Short | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Falling Short | 6.861 | 6.644 | 6.389 | 6.094 | 5.715 | 5.262 | 4.813 | 2.802 | 1.211 | 0.234 | -0.273 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Falling Short | 14.401 | 14.272 | 14.094 | 13.867 | 13.585 | 13.251 | 12.924 | 11.537 | 10.619 | 10.108 | 9.809 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Falling Short | 3.448 | 3.355 | 3.245 | 3.116 | 2.965 | 2.794 | 2.628 | 1.904 | 1.336 | 0.919 | 0.577 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Falling Short | 8.687 | 8.452 | 8.164 | 7.8 | 7.342 | 6.784 | 6.133 | 1.884 | -3.523 | -7.543 | -9.37 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Falling Short | 13.284 | 13.054 | 12.809 | 12.549 | 12.221 | 11.834 | 11.462 | 9.926 | 8.929 | 8.4 | 8.107 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Falling Short | 5.059 | 4.989 | 4.907 | 4.813 | 4.704 | 4.581 | 4.461 | 3.955 | 3.591 | 3.33 | 3.11 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Falling Short | 6.717 | 6.458 | 6.142 | 5.766 | 5.312 | 4.788 | 4.283 | 2.116 | 0.445 | -0.73 | -1.651 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Falling Short | 10.189 | 10.053 | 9.87 | 9.635 | 9.333 | 8.974 | 8.627 | 7.218 | 6.316 | 5.822 | 5.537 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Falling Short | 14.969 | 14.789 | 14.584 | 14.359 | 14.078 | 13.747 | 13.432 | 12.205 | 11.516 | 11.159 | 10.931 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Falling Short | 6.359 | 6.293 | 6.181 | 6.023 | 5.808 | 5.546 | 5.286 | 4.129 | 3.196 | 2.627 | 2.316 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Falling Short | 13.939 | 13.602 | 13.214 | 12.769 | 12.248 | 11.656 | 11.065 | 8.293 | 5.904 | 4.165 | 2.918 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Falling Short | 13.057 | 13.024 | 12.982 | 12.926 | 12.859 | 12.782 | 12.705 | 12.309 | 11.893 | 11.55 | 11.258 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Falling Short | 9.17 | 8.998 | 8.783 | 8.52 | 8.192 | 7.805 | 7.412 | 5.553 | 3.892 | 2.748 | 2.09 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Falling Short | 12.348 | 12.357 | 12.346 | 12.312 | 12.251 | 12.163 | 12.055 | 11.318 | 10.356 | 9.682 | 9.445 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Falling Short | 6.813 | 6.808 | 6.774 | 6.703 | 6.593 | 6.442 | 6.266 | 5.128 | 3.662 | 2.611 | 2.17 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Falling Short | 25.531 | 25.419 | 25.284 | 25.118 | 24.916 | 24.68 | 24.427 | 23.008 | 21.41 | 20.136 | 19.324 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Falling Short | 4.301 | 4.011 | 3.707 | 3.388 | 3.048 | 2.692 | 2.327 | 0.429 | -1.524 | -3.354 | -5.05 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Falling Short | 1.801 | 1.744 | 1.677 | 1.602 | 1.516 | 1.419 | 1.324 | 0.882 | 0.49 | 0.132 | -0.206 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Falling Short | 12.444 | 12.257 | 12.04 | 11.79 | 11.489 | 11.147 | 10.811 | 9.291 | 8.062 | 7.193 | 6.521 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Falling Short | 10.122 | 10.132 | 10.131 | 10.115 | 10.084 | 10.04 | 9.991 | 9.687 | 9.329 | 9.088 | 8.973 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Falling Short | 10.208 | 10.16 | 10.083 | 9.97 | 9.821 | 9.645 | 9.468 | 8.627 | 7.937 | 7.516 | 7.229 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Falling Short | 0.638 | 0.567 | 0.486 | 0.39 | 0.279 | 0.152 | 0.018 | -0.753 | -1.639 | -2.369 | -2.878 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Falling Short | 9.336 | 9.33 | 9.29 | 9.2 | 9.05 | 8.833 | 8.551 | 6.397 | 3.365 | 1.226 | 0.589 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Falling Short | 16.424 | 16.405 | 16.381 | 16.347 | 16.299 | 16.233 | 16.165 | 15.811 | 15.459 | 15.228 | 15.12 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Falling Short | 8.926 | 7.882 | 7.562 | 7.186 | 6.742 | 6.237 | 5.744 | 3.544 | 1.797 | 0.553 | -0.414 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Falling Short | 12.213 | 12.153 | 12.066 | 11.95 | 11.797 | 11.609 | 11.427 | 10.701 | 10.26 | 10.018 | 9.862 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Falling Short | 17.975 | 17.987 | 17.956 | 17.866 | 17.702 | 17.456 | 17.131 | 14.665 | 11.215 | 8.774 | 8.064 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Falling Short | 10.185 | 10.052 | 9.861 | 9.615 | 9.29 | 8.893 | 8.506 | 6.808 | 5.513 | 4.744 | 4.356 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Falling Short | 4.267 | 4.22 | 4.164 | 4.099 | 4.021 | 3.932 | 3.845 | 3.45 | 3.125 | 2.868 | 2.654 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Falling Short | 9.555 | 9.418 | 9.259 | 9.078 | 8.847 | 8.57 | 8.301 | 7.149 | 6.322 | 5.839 | 5.551 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 14.989 | 14.799 | 14.579 | 14.322 | 14.025 | 13.696 | 13.358 | 11.591 | 9.76 | 8.185 | 6.856 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 13.358 | 13.164 | 12.939 | 12.674 | 12.368 | 12.032 | 11.682 | 9.797 | 7.75 | 5.974 | 4.489 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Falling Short | 13.311 | 13.321 | 13.32 | 13.303 | 13.268 | 13.219 | 13.164 | 12.815 | 12.368 | 12.058 | 11.917 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Falling Short | 8.059 | 8.082 | 8.094 | 8.091 | 8.076 | 8.051 | 8.023 | 7.878 | 7.741 | 7.641 | 7.552 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Falling Short | 17.534 | 17.481 | 17.403 | 17.301 | 17.172 | 17.016 | 16.865 | 16.204 | 15.681 | 15.352 | 15.167 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Falling Short | 5.55 | 5.418 | 5.278 | 5.125 | 4.96 | 4.783 | 4.593 | 3.505 | 2.231 | 0.994 | -0.111 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Falling Short | 2.337 | 2.117 | 1.872 | 1.603 | 1.262 | 0.858 | 0.469 | -1.117 | -2.136 | -2.695 | -3.035 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Falling Short | 12.846 | 12.672 | 12.471 | 12.247 | 11.964 | 11.63 | 11.308 | 10.011 | 9.103 | 8.551 | 8.187 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Falling Short | 10.054 | 9.825 | 9.549 | 9.225 | 8.809 | 8.305 | 7.799 | 5.384 | 3.277 | 1.937 | 1.313 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 11.546 | 11.549 | 11.533 | 11.492 | 11.42 | 11.316 | 11.188 | 10.275 | 9.055 | 8.202 | 7.923 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Falling Short | 16.055 | 15.964 | 15.838 | 15.677 | 15.47 | 15.222 | 14.985 | 14.034 | 13.455 | 13.152 | 12.977 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Falling Short | 12.885 | 12.829 | 12.742 | 12.62 | 12.455 | 12.253 | 12.057 | 11.232 | 10.655 | 10.343 | 10.19 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Falling Short | 9.389 | 9.289 | 9.142 | 8.945 | 8.676 | 8.345 | 8.008 | 6.394 | 4.947 | 4.029 | 3.639 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Falling Short | 11.496 | 9.809 | 9.732 | 9.623 | 9.476 | 9.296 | 9.123 | 8.422 | 7.989 | 7.76 | 7.616 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Falling Short | 5.211 | 5.156 | 5.091 | 5.014 | 4.919 | 4.807 | 4.701 | 4.245 | 3.914 | 3.7 | 3.555 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Falling Short | 14.307 | 14.097 | 13.83 | 13.505 | 13.099 | 12.619 | 12.157 | 10.245 | 9.002 | 8.321 | 7.932 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Falling Short | 3.111 | 2.932 | 2.682 | 2.361 | 1.943 | 1.443 | 0.96 | -1.02 | -2.306 | -3.02 | -3.442 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Falling Short | 14.847 | 14.728 | 14.572 | 14.38 | 14.131 | 13.829 | 13.537 | 12.308 | 11.443 | 10.941 | 10.676 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Falling Short | 7.072 | 6.876 | 6.623 | 6.312 | 5.912 | 5.437 | 4.98 | 3.09 | 1.82 | 1.095 | 0.638 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Falling Short | 19.203 | 19.227 | 19.223 | 19.183 | 19.105 | 18.998 | 18.883 | 18.229 | 17.536 | 17.085 | 16.872 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Falling Short | 12.521 | 12.418 | 12.294 | 12.145 | 11.96 | 11.742 | 11.525 | 10.548 | 9.778 | 9.301 | 9.035 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Falling Short | 4.489 | 4.272 | 4.009 | 3.695 | 3.316 | 2.878 | 2.443 | 0.431 | -1.314 | -2.615 | -3.562 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Falling Short | 8.788 | 8.138 | 7.386 | 6.529 | 5.527 | 4.391 | 3.28 | -1.66 | -5.373 | -7.892 | -9.773 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Falling Short | 4.672 | 4.47 | 4.235 | 3.966 | 3.627 | 3.228 | 2.839 | 1.2 | 0.117 | -0.496 | -0.876 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Falling Short | 12.968 | 12.703 | 12.383 | 12.01 | 11.564 | 11.054 | 10.563 | 8.502 | 7.067 | 6.116 | 5.371 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Falling Short | 20.836 | 17.726 | 17.742 | 17.753 | 17.762 | 17.77 | 17.777 | 17.794 | 17.784 | 17.774 | 17.764 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Falling Short | 3.212 | 2.998 | 2.751 | 2.457 | 2.108 | 1.702 | 1.242 | -1.621 | -5.175 | -7.984 | -9.608 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Falling Short | 13.802 | 13.78 | 13.744 | 13.693 | 13.622 | 13.535 | 13.448 | 13.029 | 12.657 | 12.407 | 12.215 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Falling Short | 14.201 | 14.236 | 14.264 | 14.287 | 14.301 | 14.311 | 14.318 | 14.324 | 14.297 | 14.269 | 14.242 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Falling Short | 15.614 | 15.638 | 15.654 | 15.661 | 15.659 | 15.65 | 15.641 | 15.579 | 15.488 | 15.424 | 15.382 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Falling Short | 9.612 | 9.325 | 8.956 | 8.509 | 7.96 | 7.316 | 6.693 | 4.05 | 2.142 | 0.913 | 0.076 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Falling Short | 14.644 | 14.552 | 14.449 | 14.33 | 14.194 | 14.046 | 13.892 | 13.069 | 12.193 | 11.441 | 10.814 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Falling Short | 5.93 | 5.908 | 5.863 | 5.791 | 5.69 | 5.569 | 5.446 | 4.842 | 4.274 | 3.905 | 3.654 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Falling Short | 14 | 13.915 | 13.798 | 13.645 | 13.444 | 13.201 | 12.964 | 11.931 | 11.125 | 10.635 | 10.369 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Falling Short | 17.518 | 13.968 | 13.948 | 13.918 | 13.874 | 13.816 | 13.759 | 13.522 | 13.359 | 13.266 | 13.228 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Falling Short | 10.894 | 10.754 | 10.586 | 10.39 | 10.153 | 9.878 | 9.606 | 8.368 | 7.347 | 6.632 | 6.134 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Falling Short | 2.679 | 2.569 | 2.428 | 2.254 | 2.038 | 1.78 | 1.507 | 0.05 | -1.416 | -2.42 | -2.893 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Falling Short | 11.071 | 10.933 | 10.752 | 10.534 | 10.254 | 9.919 | 9.597 | 8.292 | 7.365 | 6.782 | 6.393 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Falling Short | 12.598 | 12.516 | 12.4 | 12.248 | 12.05 | 11.809 | 11.574 | 10.567 | 9.839 | 9.42 | 9.207 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Falling Short | 5.37 | 5.136 | 4.869 | 4.558 | 4.197 | 3.784 | 3.332 | 0.655 | -2.466 | -4.97 | -6.576 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Falling Short | 16.498 | 16.376 | 16.234 | 16.071 | 15.881 | 15.668 | 15.457 | 14.486 | 13.664 | 13.032 | 12.538 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Falling Short | 11.63 | 9.892 | 9.665 | 9.403 | 9.097 | 8.747 | 8.367 | 6.163 | 3.673 | 1.756 | 0.577 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Falling Short | 4.695 | 4.609 | 4.508 | 4.392 | 4.255 | 4.1 | 3.95 | 3.306 | 2.828 | 2.492 | 2.224 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Falling Short | 14.816 | 14.69 | 14.517 | 14.295 | 14.011 | 13.671 | 13.342 | 11.981 | 11.068 | 10.574 | 10.337 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Falling Short | 0.026 | -0.101 | -0.251 | -0.428 | -0.644 | -0.893 | -1.14 | -2.293 | -3.298 | -4.01 | -4.483 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Falling Short | 9.181 | 8.955 | 8.68 | 8.352 | 7.955 | 7.496 | 7.047 | 5.032 | 3.372 | 2.166 | 1.273 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Falling Short | 8.423 | 8.303 | 8.132 | 7.905 | 7.605 | 7.239 | 6.882 | 5.331 | 4.157 | 3.466 | 3.118 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Falling Short | 5.441 | 5.168 | 4.836 | 4.435 | 3.95 | 3.392 | 2.848 | 0.397 | -1.63 | -3.081 | -4.162 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Falling Short | 16.062 | 15.94 | 15.77 | 15.548 | 15.257 | 14.903 | 14.555 | 12.996 | 11.716 | 10.924 | 10.522 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Falling Short | 8.136 | 8.165 | 8.175 | 8.165 | 8.131 | 8.079 | 8.017 | 7.592 | 7.029 | 6.632 | 6.457 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Falling Short | 16.444 | 17.281 | 17.087 | 8.651 | 8.381 | 8.07 | 7.771 | 6.503 | 5.638 | 5.1 | 4.695 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Falling Short | 10.912 | 10.592 | 10.203 | 9.742 | 9.192 | 8.56 | 7.941 | 5.169 | 3.03 | 1.613 | 0.611 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Falling Short | 8.716 | 8.729 | 8.732 | 8.719 | 8.69 | 8.65 | 8.607 | 8.351 | 8.055 | 7.857 | 7.754 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Falling Short | 10.76 | 10.53 | 10.234 | 9.874 | 9.43 | 8.91 | 8.41 | 6.349 | 5.066 | 4.372 | 3.915 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Falling Short | 4.844 | 4.397 | 3.882 | 3.283 | 2.584 | 1.792 | 0.985 | -3.09 | -7.102 | -10.24 | -12.47 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Falling Short | 12.932 | 12.964 | 12.995 | 13.019 | 13.04 | 13.059 | 13.077 | 13.129 | 13.139 | 13.139 | 13.134 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Falling Short | 13.642 | 13.683 | 13.713 | 13.727 | 13.725 | 13.705 | 13.671 | 13.306 | 12.709 | 12.28 | 12.152 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Falling Short | 2.662 | 2.702 | 2.737 | 2.763 | 2.783 | 2.795 | 2.804 | 2.799 | 2.73 | 2.672 | 2.644 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Falling Short | 6.371 | 6.3 | 6.213 | 6.109 | 5.973 | 5.808 | 5.646 | 4.952 | 4.451 | 4.158 | 3.994 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Falling Short | 1.863 | 1.733 | 1.587 | 1.426 | 1.237 | 1.023 | 0.811 | -0.169 | -0.986 | -1.584 | -2.026 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Falling Short | 12.705 | 12.573 | 12.391 | 12.159 | 11.864 | 11.512 | 11.157 | 9.452 | 8.079 | 7.268 | 6.875 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Falling Short | 12.55 | 10.555 | 10.553 | 10.535 | 10.502 | 10.456 | 10.403 | 10.051 | 9.594 | 9.287 | 9.166 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Falling Short | 9.312 | 9.131 | 15.924 | 15.691 | 15.392 | 15.035 | 14.689 | 13.279 | 12.381 | 11.89 | 11.604 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Falling Short | 11.335 | 11.204 | 11.059 | 10.895 | 10.71 | 10.503 | 10.28 | 8.991 | 7.514 | 6.276 | 5.369 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Falling Short | 3.285 | 1.823 | 1.565 | 1.313 | 0.996 | 0.623 | 0.257 | -1.338 | -2.508 | -3.281 | -3.847 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Falling Short | 12.806 | 12.738 | 12.665 | 12.582 | 12.491 | 12.394 | 12.294 | 11.767 | 11.204 | 10.651 | 10.1 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Falling Short | 8.427 | 8.378 | 15.291 | 15.166 | 14.992 | 14.776 | 14.562 | 13.588 | 12.794 | 12.312 | 12.053 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Falling Short | 5.381 | 4.397 | 4.099 | 3.806 | 3.442 | 3.012 | 2.581 | 0.514 | -1.362 | -2.686 | -3.501 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Falling Short | 10.198 | 10.019 | 9.774 | 9.469 | 9.079 | 8.614 | 8.17 | 6.384 | 5.212 | 4.546 | 4.125 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Falling Short | 12.664 | 12.538 | 10.297 | 10.101 | 9.853 | 9.545 | 9.183 | 6.78 | 3.681 | 1.331 | 0.236 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Falling Short | 9.382 | 9.139 | 8.837 | 8.477 | 8.039 | 7.527 | 7.022 | 4.735 | 2.917 | 1.694 | 0.892 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Falling Short | 7.802 | 6.015 | 5.835 | 5.62 | 5.342 | 5.008 | 4.681 | 3.261 | 2.217 | 1.6 | 1.269 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Falling Short | 8.408 | 7.685 | 7.71 | 7.708 | 7.68 | 7.63 | 7.561 | 6.948 | 6.008 | 5.345 | 5.124 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Falling Short | 18.849 | 18.833 | 18.801 | 18.745 | 18.661 | 18.544 | 18.397 | 17.323 | 15.849 | 14.813 | 14.498 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Falling Short | 8.564 | 8.524 | 8.448 | 8.338 | 8.182 | 7.988 | 7.799 | 7.037 | 6.552 | 6.287 | 6.123 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Falling Short | 10.561 | 10.433 | 10.261 | 10.042 | 9.764 | 9.433 | 9.101 | 7.557 | 6.37 | 5.668 | 5.284 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Falling Short | 12.423 | 12.331 | 12.2 | 12.027 | 11.802 | 11.534 | 11.277 | 10.22 | 9.52 | 9.147 | 8.925 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Falling Short | 12.242 | 12.253 | 12.247 | 12.223 | 12.179 | 12.118 | 12.049 | 11.626 | 11.079 | 10.683 | 10.484 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Falling Short | 8.249 | 8.311 | 8.368 | 8.418 | 8.456 | 8.486 | 8.511 | 8.572 | 8.549 | 8.518 | 8.493 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Falling Short | 8.171 | 6.374 | 6.334 | 6.274 | 6.182 | 6.062 | 5.93 | 5.175 | 4.342 | 3.76 | 3.471 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Falling Short | 10.227 | 9.005 | 9.035 | 9.05 | 9.052 | 9.048 | 9.041 | 8.97 | 8.851 | 8.768 | 8.704 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Falling Short | 1.696 | 1.57 | 1.423 | 1.255 | 1.055 | 0.827 | 0.604 | -0.396 | -1.208 | -1.801 | -2.263 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 3.354 | 3.346 | 3.334 | 3.318 | 3.295 | 3.266 | 3.236 | 3.085 | 2.931 | 2.812 | 2.712 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Falling Short | 13.738 | 13.655 | 13.55 | 13.417 | 13.251 | 13.051 | 12.827 | 11.449 | 9.777 | 8.502 | 7.825 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Falling Short | 24.478 | 24.447 | 24.413 | 24.371 | 24.324 | 24.275 | 24.223 | 23.924 | 23.556 | 23.178 | 22.79 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Falling Short | 14.896 | 14.91 | 14.913 | 14.905 | 14.884 | 14.853 | 14.822 | 14.689 | 14.586 | 14.516 | 14.459 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Falling Short | -1.147 | -1.37 | -1.612 | -1.879 | -2.173 | -2.49 | -2.816 | -4.548 | -6.416 | -8.155 | -9.713 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Falling Short | 3.528 | 3.287 | 3.008 | 2.672 | 2.271 | 1.803 | 1.279 | -1.965 | -5.939 | -9.041 | -10.818 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Falling Short | 11.021 | 10.952 | 10.841 | 10.688 | 10.482 | 10.232 | 9.99 | 9.02 | 8.414 | 8.104 | 7.938 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Falling Short | 11.604 | 11.655 | 11.698 | 11.727 | 11.744 | 11.746 | 11.737 | 11.547 | 11.182 | 10.911 | 10.835 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Falling Short | 8.54 | 8.298 | 7.994 | 7.626 | 7.174 | 6.643 | 6.112 | 3.606 | 1.417 | -0.102 | -1.038 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Falling Short | 17.061 | 16.395 | 16.339 | 16.273 | 16.197 | 16.114 | 16.031 | 15.635 | 15.284 | 15.006 | 14.745 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Falling Short | 5.075 | 4.905 | 4.715 | 4.507 | 4.248 | 3.943 | 3.652 | 2.514 | 1.881 | 1.561 | 1.363 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Falling Short | 8.607 | 8.479 | 8.293 | 8.048 | 7.729 | 7.349 | 6.982 | 5.488 | 4.588 | 4.128 | 3.856 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Falling Short | -1.166 | -1.266 | -1.391 | -1.544 | -1.734 | -1.957 | -2.173 | -3.079 | -3.711 | -4.089 | -4.345 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Falling Short | 15.314 | 15.25 | 15.173 | 15.071 | 14.946 | 14.797 | 14.63 | 13.593 | 12.32 | 11.353 | 10.827 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Falling Short | 16.183 | 15.914 | 15.68 | 15.485 | 15.237 | 14.94 | 14.648 | 13.355 | 12.369 | 11.793 | 11.535 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Falling Short | 10.622 | 10.498 | 10.31 | 10.064 | 9.743 | 9.355 | 8.98 | 7.381 | 6.209 | 5.493 | 5.064 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Falling Short | 24.216 | 24.238 | 24.258 | 24.276 | 24.289 | 24.299 | 24.307 | 24.327 | 24.316 | 24.303 | 24.293 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Falling Short | 8.422 | 8.437 | 8.449 | 8.455 | 8.453 | 8.447 | 8.442 | 8.389 | 8.297 | 8.239 | 8.198 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Falling Short | 11.224 | 11.112 | 10.946 | 10.728 | 10.444 | 10.105 | 9.78 | 8.483 | 7.682 | 7.252 | 6.993 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Falling Short | -0.876 | -0.962 | -1.055 | -1.154 | -1.26 | -1.371 | -1.485 | -2.095 | -2.747 | -3.413 | -4.085 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Falling Short | 9.152 | 9.029 | 8.891 | 8.737 | 8.563 | 8.373 | 8.179 | 7.173 | 6.133 | 5.216 | 4.426 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Falling Short | 13.403 | 13.269 | 13.09 | 12.867 | 12.585 | 12.25 | 11.927 | 10.608 | 9.785 | 9.332 | 9.049 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Falling Short | 11.573 | 11.402 | 11.203 | 10.973 | 10.701 | 10.393 | 10.086 | 8.657 | 7.408 | 6.49 | 5.8 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Falling Short | 8.223 | 7.922 | 7.562 | 7.139 | 6.639 | 6.066 | 5.504 | 2.954 | 1.007 | -0.261 | -1.157 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Falling Short | 13.311 | 13.027 | 12.721 | 12.387 | 12.022 | 11.625 | 11.208 | 8.911 | 6.358 | 4.125 | 2.363 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Falling Short | 7.583 | 7.565 | 7.514 | 7.424 | 7.29 | 7.115 | 6.919 | 5.744 | 4.396 | 3.487 | 3.131 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Falling Short | 13.978 | 13.888 | 13.757 | 13.587 | 13.365 | 13.099 | 12.843 | 11.798 | 11.085 | 10.673 | 10.425 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Falling Short | 7.518 | 7.315 | 7.084 | 6.825 | 6.497 | 6.107 | 5.731 | 4.174 | 3.157 | 2.588 | 2.236 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Falling Short | 7.857 | 7.683 | 7.489 | 7.265 | 7.01 | 6.73 | 6.44 | 4.848 | 3.084 | 1.576 | 0.37 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Leading the Way | 13.078 | 12.825 | 12.573 | 12.478 | 12.459 | 12.435 | 12.323 | 10.605 | 9.165 | 8.108 | 8.431 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Leading the Way | 12.589 | 10.944 | 10.846 | 10.69 | 10.58 | 10.422 | 10.132 | 6.993 | 4.614 | 3.177 | 3.422 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Leading the Way | 11.596 | 11.303 | 10.912 | 10.46 | 10.005 | 9.528 | 8.881 | 3.54 | -0.723 | -3.96 | -4.287 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Leading the Way | 5.925 | 4.523 | 4.527 | 4.495 | 4.472 | 4.426 | 4.317 | 1.88 | -0.002 | -1.304 | -0.85 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 5.378 | 5.065 | 4.655 | 4.265 | 3.987 | 3.698 | 3.242 | -0.272 | -2.9 | -4.751 | -4.593 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 5.349 | 5.342 | 5.31 | 5.272 | 5.269 | 5.261 | 5.208 | 4.425 | 3.802 | 3.346 | 3.499 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Leading the Way | 10.083 | 9.571 | 8.882 | 8.117 | 7.588 | 7.039 | 6.258 | -0.064 | -4.882 | -8.298 | -8.413 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Leading the Way | 17.138 | 17.162 | 17.161 | 17.147 | 17.165 | 17.179 | 17.15 | 15.744 | 14.571 | 13.647 | 13.997 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Leading the Way | 1.405 | 1.211 | 0.925 | 0.584 | 0.289 | -0.023 | -0.497 | -4.922 | -8.494 | -11.257 | -11.314 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Leading the Way | 2.981 | 2.451 | 2.562 | 2.651 | 2.761 | 2.863 | 2.933 | 2.227 | 1.675 | 1.286 | 1.802 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Leading the Way | 12.166 | 11.942 | 11.6 | 11.192 | 10.924 | 10.64 | 10.217 | 6.529 | 3.709 | 1.667 | 1.653 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Leading the Way | 2.629 | 2.333 | 1.933 | 1.545 | 1.247 | 0.903 | 0.415 | -4.377 | -7.754 | -9.91 | -9.582 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Leading the Way | 3.091 | 3.086 | 3.071 | 3.049 | 3.032 | 3.012 | 2.979 | 2.609 | 2.305 | 2.078 | 2.061 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Leading the Way | 15.838 | 15.649 | 15.35 | 14.995 | 14.802 | 14.599 | 14.249 | 10.657 | 7.913 | 5.952 | 6.269 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Leading the Way | 12.949 | 12.484 | 12.45 | 12.403 | 12.39 | 12.374 | 12.325 | 11.468 | 10.737 | 10.16 | 10.216 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Leading the Way | 10.607 | 10.603 | 10.552 | 10.468 | 10.429 | 10.373 | 10.255 | 8.004 | 6.297 | 5.152 | 5.616 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Leading the Way | 15.641 | 15.305 | 14.814 | 14.243 | 13.815 | 13.353 | 12.702 | 7.969 | 4.518 | 2.301 | 2.279 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Leading the Way | 8.449 | 8.471 | 8.466 | 8.438 | 8.423 | 8.396 | 8.306 | 6.869 | 5.734 | 4.968 | 5.234 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Leading the Way | 6.698 | 6.574 | 6.385 | 6.15 | 6.002 | 5.843 | 5.574 | 1.914 | -1.253 | -3.853 | -3.947 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Leading the Way | 21.815 | 21.779 | 21.682 | 21.544 | 21.455 | 21.357 | 21.177 | 19.689 | 18.58 | 17.814 | 17.982 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Leading the Way | 3.811 | 3.681 | 3.513 | 3.324 | 3.207 | 3.085 | 2.895 | 0.902 | -0.839 | -2.282 | -2.544 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Leading the Way | 11.559 | 11.075 | 10.391 | 9.603 | 9.045 | 8.445 | 7.572 | 0.376 | -5.045 | -8.75 | -8.834 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Leading the Way | 9.565 | 9.207 | 8.703 | 8.168 | 7.786 | 7.379 | 6.743 | 1.474 | -2.44 | -5.151 | -4.896 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Leading the Way | 14.942 | 14.698 | 14.357 | 14.014 | 13.761 | 13.496 | 13.105 | 10.361 | 8.396 | 7.097 | 7.218 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Leading the Way | 2.552 | 2.49 | 2.31 | 2.045 | 1.924 | 1.757 | 1.415 | -2.834 | -6.056 | -8.123 | -7.601 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Leading the Way | 5.915 | 5.709 | 5.412 | 5.059 | 4.781 | 4.477 | 4.061 | 1 | -1.276 | -2.776 | -2.928 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 15.137 | 15.111 | 15.063 | 15.004 | 14.965 | 14.917 | 14.825 | 13.342 | 12.132 | 11.235 | 11.395 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 4.302 | 1.225 | 1.146 | 1.016 | 0.92 | 0.775 | 0.472 | -4.127 | -7.727 | -10.152 | -9.551 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Leading the Way | 8.297 | 8.183 | 7.971 | 7.682 | 7.469 | 7.205 | 6.79 | 2.485 | -0.859 | -3.08 | -2.983 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Leading the Way | 11.774 | 11.485 | 11.029 | 10.476 | 10.127 | 9.759 | 9.126 | 3.442 | -0.926 | -4.088 | -3.794 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Leading the Way | 6.166 | 5.734 | 5.071 | 4.273 | 3.684 | 3.043 | 2.056 | -6.156 | -12.363 | -16.653 | -16.534 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Leading the Way | 6.844 | 6.825 | 6.803 | 6.777 | 6.755 | 6.733 | 6.706 | 6.346 | 6.03 | 5.757 | 5.726 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Leading the Way | 4.341 | 4.31 | 4.264 | 4.209 | 4.16 | 4.104 | 4.029 | 3.306 | 2.751 | 2.342 | 2.305 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Leading the Way | 13.79 | 13.471 | 13.001 | 12.451 | 12.12 | 11.769 | 11.22 | 6.452 | 2.912 | 0.445 | 0.575 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 13.961 | 13.874 | 13.785 | 13.689 | 13.591 | 13.493 | 13.393 | 12.233 | 11.048 | 9.88 | 9.379 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Leading the Way | 5.542 | 5.463 | 5.353 | 5.227 | 5.135 | 5.039 | 4.905 | 3.929 | 3.242 | 2.784 | 2.788 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 10.62 | 10.325 | 9.863 | 9.322 | 8.98 | 8.618 | 8.026 | 2.478 | -1.608 | -4.46 | -4.052 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Leading the Way | 11.544 | 11.281 | 10.861 | 10.365 | 9.986 | 9.576 | 8.934 | 3.65 | -0.228 | -2.864 | -2.619 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Leading the Way | 9.31 | 9.331 | 9.302 | 9.24 | 9.247 | 9.238 | 9.148 | 7.204 | 5.661 | 4.588 | 4.973 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Leading the Way | 10.361 | 10.352 | 10.291 | 10.2 | 10.144 | 10.076 | 9.947 | 8.37 | 7.322 | 6.643 | 6.926 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Leading the Way | 17.455 | 17.284 | 17.038 | 16.749 | 16.521 | 16.268 | 15.923 | 13.596 | 12.001 | 11.082 | 11.087 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Leading the Way | 7.912 | 22.43 | 22.155 | 21.841 | 21.609 | 21.364 | 20.954 | 17.024 | 13.999 | 11.786 | 12.05 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Leading the Way | 10.743 | 10.335 | 9.726 | 8.994 | 8.436 | 7.863 | 6.997 | 0.086 | -5.446 | -9.676 | -9.893 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Leading the Way | 3.864 | 3.754 | 3.605 | 3.461 | 3.37 | 3.275 | 3.134 | 2.086 | 1.338 | 0.85 | 0.919 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Leading the Way | 6.235 | 5.585 | 4.762 | 3.953 | 3.304 | 2.618 | 1.643 | -5.333 | -10.488 | -13.907 | -13.748 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Leading the Way | 4.644 | 4.256 | 3.709 | 3.064 | 2.42 | 1.736 | 0.772 | -7.604 | -14.114 | -19.208 | -19.699 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Leading the Way | 6.009 | 5.472 | 4.689 | 3.755 | 3.043 | 2.299 | 1.196 | -7.693 | -14.693 | -19.928 | -20.235 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Leading the Way | 4.315 | 4.373 | 4.422 | 4.461 | 4.497 | 4.526 | 4.543 | 4.311 | 4.144 | 4.067 | 4.227 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Leading the Way | 7.938 | 7.467 | 6.741 | 5.846 | 5.162 | 4.387 | 3.25 | -5.514 | -11.923 | -15.953 | -15.969 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Leading the Way | 13.029 | 13.107 | 13.171 | 13.22 | 13.263 | 13.296 | 13.315 | 12.462 | 11.782 | 11.312 | 11.65 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Leading the Way | 10.29 | 10.417 | 10.535 | 10.647 | 10.752 | 10.854 | 10.948 | 11.104 | 11.22 | 11.326 | 11.637 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Leading the Way | 11.059 | 11.144 | 11.198 | 11.263 | 11.352 | 11.428 | 11.442 | 9.558 | 8.028 | 6.897 | 7.607 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Leading the Way | 11.739 | 11.791 | 11.821 | 11.841 | 11.881 | 11.914 | 11.918 | 11.198 | 10.651 | 10.264 | 10.574 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Leading the Way | 10.932 | 10.636 | 10.178 | 9.637 | 9.247 | 8.804 | 8.142 | 3.132 | -0.385 | -2.431 | -2.234 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Leading the Way | 4.289 | 4.219 | 4.113 | 3.992 | 3.871 | 3.745 | 3.592 | 2.937 | 2.584 | 2.404 | 2.326 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Leading the Way | 5.268 | 5.253 | 5.213 | 5.159 | 5.116 | 5.067 | 4.994 | 4.357 | 3.791 | 3.303 | 3.105 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Leading the Way | 13.735 | 13.279 | 12.675 | 12.08 | 11.637 | 11.17 | 10.439 | 4.516 | 0.169 | -2.805 | -2.474 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Leading the Way | 0.005 | 0.004 | -0.009 | -0.031 | -0.049 | -0.072 | -0.11 | -0.543 | -0.896 | -1.165 | -1.19 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Leading the Way | 3.335 | 3.137 | 2.873 | 2.584 | 2.362 | 2.129 | 1.826 | -0.417 | -1.99 | -3.079 | -3.123 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 9.657 | 9.422 | 9.05 | 8.6 | 8.312 | 7.987 | 7.499 | 3.221 | 0.147 | -1.754 | -1.526 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Leading the Way | 9.196 | 9.067 | 8.889 | 8.745 | 8.658 | 8.559 | 8.359 | 5.663 | 3.652 | 2.206 | 2.627 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Leading the Way | 5.41 | 5.114 | 4.705 | 4.246 | 3.921 | 3.574 | 3.072 | -1.565 | -5.264 | -8.048 | -8.249 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Leading the Way | 4.797 | 4.819 | 4.834 | 4.843 | 4.851 | 4.855 | 4.846 | 4.578 | 4.377 | 4.253 | 4.332 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Leading the Way | 21.98 | 21.798 | 21.534 | 21.257 | 21.098 | 20.929 | 20.627 | 17.539 | 15.179 | 13.502 | 13.841 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Leading the Way | 7.939 | 7.981 | 7.997 | 8.013 | 8.064 | 8.107 | 8.108 | 6.847 | 5.844 | 5.096 | 5.528 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Leading the Way | 13.506 | 13.177 | 12.757 | 12.381 | 12.108 | 11.821 | 11.353 | 7.532 | 4.747 | 2.842 | 3.167 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Leading the Way | 7.277 | 7.244 | 7.125 | 6.95 | 6.834 | 6.7 | 6.434 | 2.999 | 0.426 | -1.427 | -0.985 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Leading the Way | 4.774 | 4.107 | 3.172 | 2.182 | 1.541 | 0.862 | -0.202 | -8.804 | -15.114 | -19.349 | -18.867 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Leading the Way | 0.957 | 0.919 | 0.871 | 0.815 | 0.761 | 0.704 | 0.632 | -0.119 | -0.765 | -1.3 | -1.406 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Leading the Way | 3.188 | 3.067 | 2.891 | 2.672 | 2.477 | 2.251 | 1.939 | -1.162 | -3.706 | -5.588 | -5.877 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Leading the Way | 12.98 | 12.927 | 12.805 | 12.638 | 12.508 | 12.367 | 12.128 | 10.008 | 8.44 | 7.369 | 7.628 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Leading the Way | 14.826 | 14.624 | 15.286 | 14.865 | 14.597 | 14.315 | 13.836 | 9.443 | 6.154 | 3.805 | 4.091 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Leading the Way | 22.304 | 22.264 | 22.118 | 21.863 | 21.583 | 21.198 | 20.624 | 14.475 | 9.952 | 7.359 | 7.759 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Leading the Way | 9.832 | 9.536 | 9.121 | 8.636 | 8.256 | 7.854 | 7.281 | 2.377 | -1.522 | -4.472 | -4.752 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Leading the Way | 2.437 | 2.194 | 1.869 | 1.498 | 1.255 | 0.996 | 0.626 | -2.492 | -4.79 | -6.44 | -6.53 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Leading the Way | 8.173 | 7.795 | 7.161 | 6.381 | 5.969 | 5.538 | 4.744 | -2.86 | -8.812 | -13.136 | -12.631 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Leading the Way | 6.094 | 3.8 | 3.778 | 3.735 | 3.702 | 3.657 | 3.559 | 2.125 | 0.998 | 0.197 | 0.36 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Leading the Way | 7.489 | 7.022 | 6.329 | 5.538 | 4.99 | 4.413 | 3.528 | -3.397 | -8.323 | -11.632 | -11.256 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Leading the Way | 3.919 | 3.655 | 17.944 | 17.458 | 17.074 | 16.66 | 15.99 | 10.114 | 5.691 | 2.624 | 2.989 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Leading the Way | -0.173 | -0.309 | -0.504 | -0.735 | -0.92 | -1.111 | -1.39 | -3.804 | -5.743 | -7.27 | -7.394 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Leading the Way | 2.851 | 2.854 | 2.838 | 2.807 | 2.795 | 2.777 | 2.732 | 1.849 | 1.189 | 0.755 | 0.938 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Leading the Way | 10.457 | 10.171 | 9.707 | 9.15 | 8.768 | 8.366 | 7.733 | 2.74 | -0.983 | -3.561 | -3.241 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Leading the Way | 8.563 | 8.204 | 7.657 | 7.018 | 6.637 | 6.225 | 5.562 | -0.465 | -4.884 | -7.838 | -7.487 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Leading the Way | 12.481 | 12.368 | 12.178 | 11.948 | 11.783 | 11.598 | 11.327 | 9.191 | 7.675 | 6.723 | 6.77 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Leading the Way | 3.812 | 2.868 | 2.86 | 2.797 | 2.774 | 2.716 | 2.536 | -0.187 | -2.342 | -3.768 | -3.319 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Leading the Way | 15.278 | 15.184 | 15.052 | 14.884 | 14.723 | 14.534 | 14.287 | 11.663 | 9.54 | 8.023 | 7.847 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Leading the Way | 4.098 | 3.996 | 3.85 | 3.682 | 3.562 | 3.436 | 3.249 | 1.631 | 0.341 | -0.628 | -0.658 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Leading the Way | 2.461 | 2.396 | 2.291 | 2.166 | 2.084 | 1.998 | 1.85 | 0.435 | -0.637 | -1.401 | -1.272 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Leading the Way | 14.978 | 14.625 | 14.094 | 13.463 | 13.015 | 12.524 | 11.786 | 5.332 | 0.424 | -3.032 | -3.091 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Leading the Way | 1.969 | 1.805 | 1.504 | 1.121 | 0.83 | 0.512 | -0.05 | -6.092 | -10.69 | -14.08 | -13.64 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Leading the Way | 14.835 | 14.755 | 14.604 | 14.41 | 14.349 | 14.276 | 14.095 | 11.52 | 9.496 | 8.09 | 8.463 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Leading the Way | 4.719 | 4.617 | 4.477 | 4.317 | 4.183 | 4.042 | 3.85 | 2.294 | 1.081 | 0.168 | 0.095 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Leading the Way | 6.931 | 6.478 | 5.823 | 5.069 | 4.501 | 3.898 | 3.077 | -3.151 | -7.663 | -10.777 | -10.855 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Leading the Way | 12.641 | 12.298 | 11.804 | 11.246 | 10.865 | 10.466 | 9.897 | 5.406 | 2.055 | -0.341 | -0.389 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Leading the Way | 12.887 | 11.212 | 11.079 | 10.863 | 10.677 | 10.411 | 9.993 | 5.899 | 2.984 | 1.528 | 1.88 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Leading the Way | 2.953 | 2.689 | 2.387 | 2.161 | 1.976 | 1.785 | 1.533 | 0.092 | -0.831 | -1.353 | -1.267 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Leading the Way | 7.988 | 7.267 | 6.3 | 5.235 | 4.501 | 3.739 | 2.67 | -4.954 | -10.57 | -14.343 | -14.522 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Leading the Way | 8.538 | 8.536 | 8.527 | 8.512 | 8.499 | 8.482 | 8.458 | 8.269 | 8.085 | 7.908 | 7.775 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Leading the Way | 1.978 | 1.755 | 1.407 | 0.945 | 0.436 | -0.195 | -1.043 | -7.119 | -11.344 | -13.452 | -13.649 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Leading the Way | 11.798 | 11.422 | 10.928 | 10.453 | 10.151 | 9.827 | 9.279 | 4.034 | -0.054 | -2.988 | -2.702 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Leading the Way | 9.322 | 8.926 | 8.316 | 7.575 | 7.087 | 6.554 | 5.738 | -0.778 | -5.561 | -8.7 | -8.558 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Leading the Way | 0.877 | 0.762 | 0.594 | 0.381 | 0.171 | -0.079 | -0.404 | -2.719 | -4.376 | -5.298 | -5.511 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Leading the Way | 7.431 | 7.084 | 6.555 | 5.932 | 5.494 | 5.038 | 4.321 | -2.032 | -6.989 | -10.691 | -10.547 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Leading the Way | 0.906 | 0.866 | 0.76 | 0.617 | 0.565 | 0.498 | 0.335 | -2.292 | -4.331 | -5.736 | -5.257 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Leading the Way | 1.488 | 1.487 | 1.487 | 1.486 | 1.485 | 1.484 | 1.482 | 1.465 | 1.449 | 1.434 | 1.427 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 10.495 | 10.523 | 10.506 | 10.459 | 10.475 | 10.484 | 10.432 | 8.623 | 7.196 | 6.128 | 6.595 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 7.128 | 7.09 | 7.02 | 6.935 | 6.89 | 6.84 | 6.751 | 5.603 | 4.753 | 4.149 | 4.285 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 8.505 | 8.423 | 8.301 | 8.157 | 8.031 | 7.901 | 7.728 | 6.619 | 5.83 | 5.287 | 5.254 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 3.92 | 3.714 | 3.42 | 3.089 | 2.852 | 2.588 | 2.195 | -0.864 | -3.168 | -4.684 | -4.754 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Leading the Way | 14.573 | 14.266 | 13.847 | 14.369 | 13.941 | 13.5 | 12.909 | 8.743 | 5.585 | 3.356 | 3.228 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Leading the Way | 10.105 | 9.024 | 8.613 | 8.115 | 7.814 | 7.497 | 6.982 | 2.322 | -1.2 | -3.735 | -3.545 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Leading the Way | 3.254 | 3.063 | 2.801 | 2.491 | 2.189 | 1.849 | 1.392 | -2.134 | -4.799 | -6.623 | -6.931 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Leading the Way | 10.759 | 10.075 | 9.318 | 8.81 | 8.5 | 8.172 | 7.619 | 2.614 | -1.257 | -4.003 | -3.647 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Leading the Way | 10.774 | 10.718 | 10.639 | 10.544 | 10.489 | 10.43 | 10.331 | 8.865 | 7.502 | 6.302 | 6.093 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Leading the Way | -2.973 | -3.665 | -4.651 | -5.784 | -6.631 | -7.515 | -8.791 | -18.659 | -26.208 | -31.638 | -31.863 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Leading the Way | 7.079 | 6.423 | 5.559 | 4.711 | 4.153 | 3.574 | 2.727 | -3.235 | -7.42 | -10.011 | -9.558 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Leading the Way | 5.265 | 5.27 | 5.179 | 5.02 | 5.063 | 5.089 | 4.944 | 1.677 | -1.049 | -3.131 | -2.607 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 17.266 | 14.222 | 14.027 | 13.806 | 13.636 | 13.461 | 13.232 | 10.881 | 8.891 | 7.232 | 6.99 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Leading the Way | 13.888 | 13.847 | 13.779 | 13.686 | 13.593 | 13.479 | 13.329 | 11.706 | 10.377 | 9.424 | 9.285 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Leading the Way | 9.605 | 9.388 | 9.108 | 8.764 | 8.403 | 7.976 | 7.45 | 3.214 | -0.172 | -2.49 | -3.25 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Leading the Way | 12.758 | 12.736 | 12.658 | 12.545 | 12.525 | 12.499 | 12.397 | 10.096 | 8.219 | 6.785 | 7.168 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Leading the Way | 11.525 | 11.567 | 11.571 | 11.55 | 11.573 | 11.59 | 11.558 | 10.654 | 9.967 | 9.518 | 9.84 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 4.17 | 3.988 | 3.763 | 3.49 | 3.184 | 2.822 | 2.389 | -0.944 | -3.618 | -5.438 | -6.214 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Leading the Way | 16.338 | 16.265 | 16.147 | 15.998 | 15.926 | 15.84 | 15.677 | 13.737 | 12.156 | 11.028 | 11.072 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Leading the Way | 10.815 | 10.523 | 10.062 | 9.514 | 9.22 | 8.906 | 8.377 | 3.299 | -0.523 | -3.157 | -2.744 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Leading the Way | 10.327 | 10.21 | 9.985 | 9.694 | 9.584 | 9.452 | 9.161 | 5.33 | 2.331 | 0.269 | 0.753 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Leading the Way | 7.106 | 6.752 | 6.184 | 5.491 | 5.022 | 4.503 | 3.704 | -2.757 | -7.343 | -10.252 | -9.817 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Leading the Way | 4.536 | 4.159 | 3.62 | 3.009 | 2.542 | 2.028 | 1.3 | -4.581 | -8.992 | -11.909 | -11.909 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Leading the Way | 11.73 | 11.716 | 11.655 | 11.562 | 11.448 | 11.287 | 11.053 | 9.269 | 8.138 | 7.717 | 7.846 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Leading the Way | 15.422 | 15.104 | 14.606 | 14 | 13.677 | 13.34 | 12.768 | 7.69 | 3.858 | 1.162 | 1.468 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Leading the Way | 9.264 | 8.792 | 8.089 | 7.235 | 6.56 | 5.801 | 4.718 | -3.595 | -9.592 | -13.401 | -13.53 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Leading the Way | 3.295 | 3.179 | 3.016 | 3.328 | 3.182 | 3.029 | 2.815 | 1.16 | -0.093 | -1.013 | -1.109 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Leading the Way | 8.04 | 7.822 | 7.457 | 7.025 | 6.695 | 6.349 | 5.753 | 0.279 | -3.964 | -7.079 | -6.608 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Leading the Way | 4.144 | 3.944 | 3.642 | 3.297 | 3.094 | 2.883 | 2.543 | -0.186 | -2.219 | -3.632 | -3.526 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 12.3 | 12.284 | 12.241 | 12.179 | 12.15 | 12.113 | 12.037 | 10.855 | 9.851 | 9.05 | 9.052 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 25.328 | 25.285 | 25.219 | 25.136 | 25.086 | 25.032 | 24.944 | 23.568 | 22.404 | 21.472 | 21.507 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Leading the Way | 14.657 | 14.514 | 14.307 | 14.056 | 13.826 | 13.572 | 13.239 | 11.127 | 9.667 | 8.794 | 8.706 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Leading the Way | 12.697 | 12.748 | 12.776 | 12.787 | 12.814 | 12.837 | 12.83 | 11.699 | 10.799 | 10.117 | 10.455 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Leading the Way | 19.833 | 19.813 | 19.782 | 19.745 | 19.721 | 19.696 | 19.66 | 18.923 | 18.243 | 17.641 | 17.589 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Leading the Way | 6.817 | 6.553 | 6.139 | 5.645 | 5.349 | 5.037 | 4.55 | 0.502 | -2.391 | -4.275 | -3.938 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 22.491 | 22.482 | 22.396 | 22.26 | 22.223 | 22.168 | 22.003 | 19.233 | 17.082 | 15.546 | 16.03 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Leading the Way | 14.575 | 14.501 | 14.367 | 14.208 | 14.182 | 14.151 | 14.016 | 11.361 | 9.203 | 7.604 | 8.048 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Leading the Way | 4.735 | 4.649 | 4.513 | 4.352 | 4.258 | 4.155 | 3.985 | 2.53 | 1.469 | 0.755 | 0.845 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Leading the Way | 4.522 | 4.502 | 4.475 | 4.444 | 4.415 | 4.38 | 4.338 | 4.032 | 3.785 | 3.609 | 3.519 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Leading the Way | 15.691 | 15.609 | 15.471 | 15.292 | 15.167 | 15.018 | 14.789 | 11.883 | 9.484 | 7.701 | 7.702 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 9.661 | 9.523 | 9.306 | 9.045 | 8.845 | 8.633 | 8.298 | 5.618 | 3.673 | 2.358 | 2.553 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 11.537 | 11.442 | 11.291 | 11.109 | 10.996 | 10.879 | 10.669 | 8.661 | 7.131 | 6.044 | 6.229 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Leading the Way | 2.327 | 2.18 | 1.985 | 1.769 | 1.571 | 1.365 | 1.078 | -1.014 | -2.661 | -3.951 | -4.179 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Leading the Way | 3.473 | 3.261 | 2.962 | 2.605 | 2.398 | 2.16 | 1.779 | -2.986 | -6.882 | -9.836 | -9.899 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Leading the Way | 18.929 | 18.909 | 18.869 | 18.813 | 18.768 | 18.709 | 18.619 | 17.815 | 17.217 | 16.869 | 16.867 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Leading the Way | 4.845 | 4.763 | 4.639 | 4.494 | 4.395 | 4.292 | 4.114 | 2.526 | 1.315 | 0.437 | 0.541 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Leading the Way | 14.798 | 14.783 | 14.747 | 14.712 | 14.696 | 14.669 | 14.593 | 13.373 | 12.4 | 11.703 | 11.868 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Leading the Way | 12.646 | 12.738 | 12.812 | 12.872 | 12.939 | 12.994 | 13.026 | 12.681 | 12.419 | 12.289 | 12.568 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Leading the Way | 2.222 | 1.913 | 1.471 | 0.949 | 0.532 | 0.087 | -0.513 | -4.39 | -7.086 | -8.761 | -8.863 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 5.917 | 5.885 | 5.824 | 5.746 | 5.704 | 5.655 | 5.566 | 4.371 | 3.389 | 2.66 | 2.728 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 5.275 | 5.229 | 5.149 | 5.044 | 4.968 | 4.874 | 4.726 | 3.318 | 2.239 | 1.554 | 1.56 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Leading the Way | 5.25 | 4.92 | 4.449 | 3.899 | 3.477 | 3.025 | 2.372 | -2.797 | -6.72 | -9.502 | -9.642 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Leading the Way | 15.341 | 15.259 | 15.136 | 14.984 | 14.899 | 14.804 | 14.645 | 12.595 | 10.903 | 9.632 | 9.697 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Leading the Way | 8.194 | 7.634 | 6.894 | 6.17 | 5.592 | 4.989 | 4.074 | -2.878 | -7.948 | -11.522 | -11.294 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Leading the Way | 4.891 | 4.807 | 4.658 | 4.488 | 4.389 | 4.262 | 3.993 | 0.196 | -2.819 | -4.975 | -4.54 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Leading the Way | 10.393 | 10.084 | 9.578 | 8.951 | 8.56 | 8.153 | 7.441 | 0.584 | -4.907 | -9.04 | -8.757 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Leading the Way | 0.257 | 0.171 | 0.057 | -0.078 | -0.168 | -0.268 | -0.422 | -2.204 | -3.665 | -4.779 | -4.834 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Leading the Way | 13.443 | 13.138 | 12.676 | 12.15 | 11.778 | 11.38 | 10.759 | 5.789 | 2.123 | -0.374 | -0.162 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Leading the Way | 18.437 | 18.429 | 18.405 | 18.367 | 18.345 | 18.314 | 18.259 | 17.22 | 16.41 | 15.818 | 15.972 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Leading the Way | 12.619 | 12.391 | 12.083 | 11.735 | 11.566 | 11.387 | 11.089 | 7.841 | 5.138 | 3.038 | 2.856 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Leading the Way | 7.167 | 7.047 | 6.866 | 6.64 | 6.463 | 6.266 | 5.945 | 2.747 | 0.086 | -1.943 | -2.04 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Leading the Way | 8.24 | 8.092 | 7.84 | 7.5 | 7.262 | 6.969 | 6.467 | 1.264 | -2.948 | -5.914 | -5.993 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Leading the Way | 16.349 | 16.336 | 16.32 | 16.303 | 16.284 | 16.263 | 16.24 | 16.085 | 15.908 | 15.716 | 15.54 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Leading the Way | 16.966 | 16.875 | 16.721 | 16.531 | 16.38 | 16.216 | 15.962 | 13.595 | 11.864 | 10.63 | 10.792 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Leading the Way | 18.994 | 18.95 | 18.882 | 18.801 | 18.746 | 18.689 | 18.591 | 17.472 | 16.543 | 15.811 | 15.849 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Leading the Way | 9.137 | 8.606 | 7.96 | 7.421 | 7.113 | 6.79 | 6.261 | 1.379 | -2.317 | -4.89 | -4.512 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Leading the Way | 10.46 | 10.023 | 9.41 | 8.766 | 8.342 | 7.896 | 7.191 | 1.37 | -2.802 | -5.634 | -5.286 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Leading the Way | -6.478 | -6.363 | -6.275 | -6.206 | -6.137 | -6.085 | -6.068 | -6.568 | -6.912 | -7.051 | -6.684 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Leading the Way | 10.156 | 9.488 | 8.683 | 8.006 | 7.545 | 7.066 | 6.287 | -0.489 | -5.681 | -9.432 | -9.074 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Leading the Way | 11.42 | 11.295 | 11.1 | 10.847 | 10.669 | 10.457 | 10.123 | 6.17 | 3.023 | 0.768 | 0.805 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Leading the Way | 5.23 | 4.925 | 4.494 | 3.996 | 3.63 | 3.253 | 2.718 | -1.678 | -5.07 | -7.607 | -7.707 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Leading the Way | 24.507 | 24.478 | 24.379 | 24.233 | 24.205 | 24.168 | 24.025 | 20.879 | 18.343 | 16.461 | 17.019 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Leading the Way | 6.495 | 6.3 | 6.03 | 5.721 | 5.489 | 5.237 | 4.892 | 1.915 | -0.462 | -2.211 | -2.496 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Leading the Way | 6.769 | 6.76 | 6.743 | 6.723 | 6.711 | 6.699 | 6.677 | 6.447 | 6.288 | 6.186 | 6.218 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Leading the Way | 11.676 | 11.098 | 10.236 | 9.219 | 8.602 | 7.954 | 6.948 | -1.516 | -7.99 | -12.589 | -12.54 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Leading the Way | 21.981 | 21.991 | 21.96 | 21.879 | 21.756 | 21.57 | 21.31 | 19.322 | 18.019 | 17.601 | 17.67 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Leading the Way | 11.277 | 11.027 | 10.637 | 10.183 | 9.912 | 9.62 | 9.135 | 4.486 | 0.986 | -1.438 | -1.063 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Leading the Way | 12.095 | 11.941 | 11.695 | 11.353 | 10.962 | 10.464 | 9.768 | 4.003 | -0.294 | -2.768 | -2.959 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Leading the Way | 0.762 | 0.67 | 0.534 | 0.368 | 0.221 | 0.055 | -0.176 | -2.215 | -3.776 | -4.902 | -5.016 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Leading the Way | 7.086 | 1.348 | 0.999 | 0.592 | 0.286 | -0.039 | -0.493 | -3.817 | -6.276 | -7.943 | -8.008 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Leading the Way | 5.072 | 4.812 | 4.446 | 4.025 | 3.734 | 3.429 | 2.994 | -0.61 | -3.392 | -5.461 | -5.67 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Leading the Way | 12.913 | 12.693 | 12.351 | 11.922 | 11.5 | 10.967 | 10.217 | 4.148 | -0.098 | -2.281 | -2.161 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Leading the Way | 2.328 | 2.094 | 1.731 | 1.334 | 1.096 | 0.828 | 0.391 | -3.494 | -6.297 | -8.042 | -7.643 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Leading the Way | 2.274 | 2.087 | 1.846 | 1.639 | 1.513 | 1.382 | 1.18 | -0.349 | -1.454 | -2.164 | -2.032 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Leading the Way | 12.99 | 12.843 | 12.586 | 12.266 | 12.11 | 11.94 | 11.613 | 8.223 | 5.733 | 4.064 | 4.463 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Leading the Way | 7.908 | 7.95 | 7.975 | 8.002 | 8.038 | 8.068 | 8.073 | 6.703 | 5.626 | 4.815 | 5.279 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Leading the Way | 13.583 | 13.499 | 13.347 | 13.154 | 13.096 | 13.028 | 12.85 | 10.07 | 7.877 | 6.317 | 6.698 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Leading the Way | 7.128 | 6.739 | 6.194 | 5.566 | 5.04 | 4.486 | 3.735 | -1.667 | -5.638 | -8.5 | -8.926 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Leading the Way | 12.781 | 12.733 | 12.612 | 12.426 | 12.281 | 12.074 | 11.742 | 8.631 | 6.404 | 5.263 | 5.439 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Leading the Way | 13.777 | 13.82 | 13.857 | 13.889 | 13.923 | 13.955 | 13.98 | 13.825 | 13.7 | 13.61 | 13.748 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Leading the Way | 5.913 | 5.896 | 5.864 | 5.827 | 5.809 | 5.788 | 5.748 | 5.403 | 5.175 | 5.029 | 5.062 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Leading the Way | 14.203 | 14.23 | 14.233 | 14.22 | 14.227 | 14.229 | 14.207 | 12.926 | 11.923 | 11.183 | 11.536 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Leading the Way | -4.029 | -4.318 | -4.775 | -5.333 | -5.659 | -6.005 | -6.567 | -11.351 | -14.857 | -17.176 | -16.826 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Leading the Way | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Leading the Way | 8.957 | 7.842 | 7.183 | 6.416 | 5.894 | 5.351 | 4.506 | -2.694 | -8.244 | -12.296 | -12.121 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Leading the Way | 8.937 | 8.338 | 7.483 | 6.562 | 12.011 | 11.434 | 10.519 | 3.11 | -2.241 | -5.84 | -5.453 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Leading the Way | 4.048 | 4.123 | 4.17 | 4.189 | 4.209 | 4.22 | 4.163 | 2.283 | 0.697 | -0.542 | -0.143 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Leading the Way | 2.296 | 1.979 | 1.527 | 0.992 | 0.475 | -0.06 | -0.83 | -6.9 | -11.653 | -15.374 | -15.561 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Leading the Way | 14.388 | 14.197 | 13.905 | 13.572 | 13.337 | 13.091 | 12.679 | 8.839 | 5.857 | 3.665 | 3.898 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Leading the Way | 5.6 | 5.073 | 4.273 | 3.323 | 2.72 | 2.075 | 1.111 | -6.78 | -12.621 | -16.611 | -16.573 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Leading the Way | 5.187 | 4.19 | 3.819 | 3.425 | 3.173 | 2.885 | 2.378 | -2.239 | -5.707 | -8.048 | -7.684 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Leading the Way | 15.096 | 14.932 | 14.679 | 14.393 | 14.238 | 14.073 | 13.786 | 11.119 | 9.095 | 7.649 | 7.817 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Leading the Way | 4.171 | 3.871 | 3.405 | 2.858 | 2.516 | 2.144 | 1.545 | -3.777 | -7.655 | -10.235 | -9.94 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Leading the Way | 7.892 | 7.625 | 7.258 | 6.824 | 6.521 | 6.181 | 5.697 | 0.993 | -2.757 | -5.431 | -5.625 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Leading the Way | 8.919 | 8.449 | 7.777 | 7.016 | 6.529 | 6.017 | 5.258 | -0.602 | -4.742 | -7.377 | -7.052 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Leading the Way | 6.852 | 6.53 | 6.065 | 5.525 | 5.072 | 4.601 | 3.963 | -0.061 | -2.923 | -4.785 | -4.853 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Leading the Way | 2.334 | 1.61 | 0.703 | -0.099 | -0.715 | -1.359 | -2.405 | -10.975 | -17.299 | -21.681 | -21.004 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Leading the Way | 9.699 | 9.173 | 8.457 | 7.739 | 7.338 | 6.919 | 6.215 | 0.023 | -4.582 | -7.74 | -7.287 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Leading the Way | 10.623 | 10.113 | 9.423 | 8.731 | 8.212 | 7.637 | 6.774 | 0.134 | -4.618 | -7.597 | -7.357 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Leading the Way | 13.411 | 13.399 | 13.334 | 13.219 | 13.123 | 12.987 | 12.765 | 10.02 | 8.022 | 6.892 | 7.234 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Leading the Way | 8.819 | 8.697 | 8.503 | 8.276 | 8.118 | 7.951 | 7.669 | 4.876 | 2.816 | 1.355 | 1.572 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Leading the Way | 3.584 | 3.513 | 3.373 | 3.186 | 3.069 | 2.915 | 2.663 | 0.212 | -1.568 | -2.556 | -2.354 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Leading the Way | 12.908 | 12.684 | 12.327 | 11.903 | 11.641 | 11.365 | 10.91 | 6.83 | 3.785 | 1.645 | 1.934 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Leading the Way | 17.6 | 17.499 | 17.315 | 17.077 | 16.896 | 16.704 | 16.392 | 13.921 | 12.096 | 10.808 | 10.931 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Leading the Way | 15.454 | 15.34 | 15.165 | 14.952 | 14.858 | 14.758 | 14.568 | 12.085 | 9.992 | 8.397 | 8.479 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Leading the Way | 4.15 | 3.963 | 3.681 | 3.308 | 2.955 | 2.511 | 1.893 | -3.53 | -7.594 | -10.027 | -10.222 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Leading the Way | 10.148 | 10.183 | 10.186 | 10.163 | 10.169 | 10.159 | 10.104 | 8.331 | 6.948 | 5.99 | 6.409 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Leading the Way | -1.198 | -1.299 | -1.451 | -1.637 | -1.758 | -1.902 | -2.129 | -4.528 | -6.412 | -7.703 | -7.7 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Leading the Way | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Leading the Way | 6.782 | 6.269 | 5.579 | 4.867 | 4.415 | 3.924 | 3.181 | -2.839 | -7.122 | -9.928 | -9.739 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Leading the Way | 14.34 | 14.016 | 13.53 | 12.943 | 12.622 | 12.283 | 11.71 | 6.66 | 2.853 | 0.148 | 0.356 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Leading the Way | 3.463 | 3.319 | 3.117 | 2.889 | 2.728 | 2.56 | 2.32 | 0.255 | -1.327 | -2.525 | -2.598 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Leading the Way | 8.802 | 8.447 | 7.931 | 7.257 | 6.609 | 5.798 | 4.713 | -4.502 | -11.372 | -15.371 | -15.871 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Leading the Way | 13.065 | 12.57 | 11.945 | 11.364 | 10.968 | 10.553 | 9.924 | 4.534 | 0.627 | -2.093 | -1.85 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Leading the Way | 5.066 | 4.976 | 4.848 | 4.7 | 4.588 | 4.474 | 4.298 | 2.87 | 1.743 | 0.894 | 0.863 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Leading the Way | 6.741 | 6.302 | 5.674 | 4.948 | 4.451 | 3.934 | 3.169 | -3.822 | -9.288 | -13.441 | -13.475 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Leading the Way | 10.171 | 9.894 | 9.444 | 8.902 | 8.56 | 8.201 | 7.587 | 1.967 | -2.309 | -5.327 | -4.859 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Leading the Way | 14.854 | 14.519 | 14.076 | 13.64 | 13.32 | 12.99 | 12.483 | 8.608 | 5.67 | 3.575 | 3.759 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Leading the Way | 6.448 | 6.244 | 5.889 | 5.445 | 5.205 | 4.942 | 4.481 | -0.331 | -3.937 | -6.401 | -5.925 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Leading the Way | 14.02 | 13.636 | 13.12 | 12.534 | 11.983 | 11.391 | 10.602 | 4.662 | 0.141 | -3.15 | -3.618 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Leading the Way | 13.131 | 13.08 | 12.996 | 12.888 | 12.845 | 12.797 | 12.699 | 11.112 | 9.813 | 8.831 | 8.978 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Leading the Way | 9.277 | 8.933 | 8.435 | 7.874 | 7.49 | 7.069 | 6.464 | 1.878 | -1.456 | -3.575 | -3.598 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Leading the Way | 12.448 | 12.455 | 12.41 | 12.32 | 12.246 | 12.136 | 11.951 | 9.875 | 8.383 | 7.57 | 7.815 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Leading the Way | 6.949 | 6.868 | 6.694 | 6.451 | 6.307 | 6.114 | 5.779 | 2.005 | -0.776 | -2.429 | -2.046 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Leading the Way | 25.646 | 25.534 | 25.35 | 25.11 | 24.91 | 24.67 | 24.335 | 21.53 | 19.431 | 18.115 | 18.002 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Leading the Way | 4.553 | 4.352 | 4.095 | 3.796 | 3.578 | 3.344 | 2.982 | -0.842 | -4.264 | -7.135 | -7.757 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Leading the Way | 1.872 | 1.834 | 1.773 | 1.699 | 1.641 | 1.579 | 1.496 | 0.935 | 0.518 | 0.209 | 0.136 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Leading the Way | 12.504 | 12.206 | 11.797 | 11.341 | 11.033 | 10.706 | 10.229 | 5.837 | 2.448 | -0.049 | -0.077 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Leading the Way | 10.199 | 10.198 | 10.157 | 10.089 | 10.072 | 10.044 | 9.951 | 8.193 | 6.838 | 5.891 | 6.182 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Leading the Way | 10.31 | 10.221 | 10.034 | 9.776 | 9.651 | 9.514 | 9.16 | 3.673 | -0.951 | -4.579 | -4.059 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Leading the Way | 0.733 | 0.665 | 0.566 | 0.442 | 0.342 | 0.224 | 0.062 | -1.635 | -3.01 | -4.002 | -4.103 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Leading the Way | 9.425 | 9.406 | 9.305 | 9.11 | 8.836 | 8.447 | 7.897 | 2.736 | -0.929 | -2.73 | -2.457 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Leading the Way | 16.453 | 16.409 | 16.334 | 16.257 | 16.211 | 16.155 | 16.049 | 14.727 | 13.753 | 13.109 | 13.289 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Leading the Way | 8.979 | 7.819 | 7.27 | 6.633 | 6.157 | 5.658 | 4.932 | -1.541 | -6.625 | -10.461 | -10.626 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Leading the Way | 12.242 | 12.14 | 11.951 | 11.717 | 11.567 | 11.406 | 11.108 | 8.508 | 6.573 | 5.236 | 5.533 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Leading the Way | 18.115 | 18.143 | 18.064 | 17.87 | 17.585 | 17.162 | 16.554 | 11.739 | 8.567 | 7.418 | 7.683 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Leading the Way | 10.218 | 9.854 | 9.272 | 8.576 | 8.201 | 7.793 | 7.075 | 0.413 | -4.526 | -7.843 | -7.275 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Leading the Way | 4.306 | 4.248 | 4.16 | 4.056 | 3.985 | 3.91 | 3.796 | 2.884 | 2.195 | 1.695 | 1.664 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Leading the Way | 9.479 | 9.147 | 8.682 | 8.204 | 7.952 | 7.683 | 7.201 | 2.398 | -1.119 | -3.458 | -2.894 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 15.296 | 15.139 | 14.888 | 14.573 | 14.367 | 14.133 | 13.775 | 9.685 | 6.319 | 3.761 | 3.654 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 13.704 | 13.564 | 13.335 | 13.036 | 12.832 | 12.601 | 12.241 | 7.213 | 2.925 | -0.475 | -0.579 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Leading the Way | 13.404 | 13.405 | 13.372 | 13.318 | 13.291 | 13.249 | 13.161 | 11.479 | 10.244 | 9.456 | 9.831 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Leading the Way | 8.174 | 8.204 | 8.192 | 8.149 | 8.181 | 8.208 | 8.166 | 6.734 | 5.545 | 4.653 | 5.011 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Leading the Way | 17.586 | 17.456 | 17.25 | 17.004 | 16.851 | 16.687 | 16.438 | 14.473 | 13.055 | 12.151 | 12.271 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Leading the Way | 5.824 | 5.82 | 5.8 | 5.763 | 5.717 | 5.652 | 5.563 | 4.673 | 3.879 | 3.255 | 2.987 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Leading the Way | 2.195 | 1.709 | 1.056 | 0.413 | 0.03 | -0.372 | -1.042 | -6.968 | -11.356 | -14.359 | -13.864 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Leading the Way | 12.746 | 12.386 | 11.9 | 11.408 | 11.073 | 10.725 | 10.168 | 5.486 | 1.985 | -0.443 | -0.112 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Leading the Way | 10.023 | 9.507 | 8.772 | 7.98 | 7.479 | 6.922 | 6.043 | -1.236 | -6.46 | -9.636 | -9.093 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 11.648 | 11.659 | 11.619 | 11.531 | 11.437 | 11.295 | 11.081 | 8.847 | 7.289 | 6.534 | 6.801 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Leading the Way | 16.046 | 15.833 | 15.494 | 15.085 | 14.845 | 14.593 | 14.176 | 10.782 | 8.341 | 6.725 | 6.986 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Leading the Way | 12.903 | 12.797 | 12.601 | 12.349 | 12.152 | 11.941 | 11.574 | 7.808 | 5.019 | 3.05 | 3.479 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Leading the Way | 9.423 | 9.162 | 8.739 | 8.229 | 7.894 | 7.516 | 6.921 | 1.762 | -1.951 | -4.285 | -3.93 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Leading the Way | 11.545 | 9.796 | 9.588 | 9.319 | 9.171 | 9.014 | 8.71 | 5.629 | 3.201 | 1.414 | 1.687 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Leading the Way | 5.212 | 5.125 | 5.001 | 4.866 | 4.757 | 4.642 | 4.48 | 3.249 | 2.347 | 1.705 | 1.698 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Leading the Way | 14.304 | 13.869 | 13.23 | 12.507 | 12.011 | 11.489 | 10.7 | 4.565 | 0.14 | -2.916 | -2.833 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Leading the Way | 3.151 | 2.817 | 2.267 | 1.607 | 1.141 | 0.649 | -0.179 | -7.521 | -13.09 | -17.045 | -16.465 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Leading the Way | 14.857 | 14.582 | 14.17 | 13.712 | 13.41 | 13.086 | 12.583 | 8.64 | 5.768 | 3.838 | 4 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Leading the Way | 7.105 | 6.638 | 5.952 | 5.187 | 4.727 | 4.241 | 3.469 | -3.63 | -8.977 | -12.788 | -12.432 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Leading the Way | 19.374 | 19.411 | 19.365 | 19.25 | 19.211 | 19.147 | 18.928 | 14.896 | 11.616 | 9.178 | 9.793 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Leading the Way | 12.578 | 12.435 | 12.221 | 11.98 | 11.784 | 11.57 | 11.266 | 8.873 | 7.18 | 6.133 | 6.346 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Leading the Way | 4.588 | 4.268 | 3.792 | 3.228 | 2.831 | 2.404 | 1.772 | -3.682 | -7.762 | -10.657 | -10.697 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Leading the Way | 8.803 | 8.085 | 7.127 | 6.051 | 5.007 | 3.912 | 2.45 | -7.001 | -14.063 | -19.133 | -19.964 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Leading the Way | 4.588 | 4.251 | 3.772 | 3.271 | 2.907 | 2.523 | 1.876 | -4.119 | -8.822 | -12.3 | -12.004 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Leading the Way | 12.965 | 12.476 | 11.799 | 11.033 | 10.538 | 10.027 | 9.277 | 3.595 | -0.695 | -3.77 | -3.909 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Leading the Way | 20.883 | 17.791 | 17.822 | 17.85 | 17.876 | 17.901 | 17.925 | 17.692 | 17.489 | 17.327 | 17.466 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Leading the Way | 3.483 | 3.244 | 2.902 | 2.477 | 2.086 | 1.603 | 0.968 | -4.462 | -8.626 | -11.172 | -11.635 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Leading the Way | 13.88 | 13.762 | 13.562 | 13.325 | 13.269 | 13.206 | 13.003 | 9.775 | 7.132 | 5.144 | 5.492 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Leading the Way | 14.305 | 14.363 | 14.402 | 14.433 | 14.487 | 14.537 | 14.566 | 14.265 | 14.026 | 13.869 | 14.1 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Leading the Way | 15.69 | 15.723 | 15.735 | 15.731 | 15.752 | 15.768 | 15.757 | 14.909 | 14.241 | 13.744 | 13.993 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Leading the Way | 9.648 | 9.097 | 8.285 | 7.337 | 6.702 | 6.035 | 5.052 | -2.199 | -7.546 | -11.194 | -11.181 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Leading the Way | 14.757 | 14.647 | 14.481 | 14.276 | 14.18 | 14.071 | 13.864 | 10.879 | 8.359 | 6.392 | 6.431 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Leading the Way | 6.036 | 5.948 | 5.776 | 5.551 | 5.471 | 5.38 | 5.152 | 1.272 | -1.834 | -4.132 | -3.598 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Leading the Way | 14.014 | 13.832 | 13.542 | 13.199 | 12.956 | 12.695 | 12.303 | 8.876 | 6.418 | 4.789 | 5.041 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Leading the Way | 17.538 | 13.977 | 13.926 | 13.867 | 13.827 | 13.781 | 13.703 | 13.171 | 12.836 | 12.67 | 12.788 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Leading the Way | 10.957 | 10.7 | 10.339 | 9.941 | 9.681 | 9.403 | 8.992 | 5.702 | 3.232 | 1.532 | 1.483 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Leading the Way | 2.701 | 2.494 | 2.191 | 1.827 | 1.546 | 1.224 | 0.773 | -2.666 | -5.178 | -6.689 | -6.753 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Leading the Way | 11.155 | 10.787 | 10.26 | 9.696 | 9.369 | 9.025 | 8.489 | 4.419 | 1.47 | -0.496 | -0.321 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Leading the Way | 12.612 | 12.401 | 12.064 | 11.665 | 11.433 | 11.184 | 10.767 | 7.044 | 4.319 | 2.489 | 2.781 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Leading the Way | 5.593 | 5.406 | 5.125 | 4.753 | 4.406 | 3.987 | 3.376 | -2.553 | -7.303 | -10.581 | -10.907 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Leading the Way | 16.529 | 16.386 | 16.182 | 15.941 | 15.747 | 15.542 | 15.248 | 12.918 | 11.085 | 9.715 | 9.561 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Leading the Way | 11.713 | 9.916 | 9.556 | 9.105 | 8.771 | 8.379 | 7.759 | 1.67 | -3.2 | -6.561 | -6.699 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Leading the Way | 4.704 | 4.585 | 4.42 | 4.23 | 4.083 | 3.93 | 3.722 | 2.203 | 1.091 | 0.288 | 0.206 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Leading the Way | 14.814 | 14.532 | 14.098 | 13.583 | 13.231 | 12.861 | 12.317 | 8.243 | 5.374 | 3.547 | 3.79 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Leading the Way | 0.032 | -0.15 | -0.408 | -0.705 | -0.952 | -1.217 | -1.6 | -4.96 | -7.514 | -9.353 | -9.368 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Leading the Way | 9.327 | 8.98 | 8.473 | 7.886 | 7.459 | 7.007 | 6.344 | 0.545 | -3.99 | -7.35 | -7.427 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Leading the Way | 8.442 | 8.14 | 7.657 | 7.078 | 6.714 | 6.321 | 5.686 | -0.113 | -4.327 | -7.174 | -6.754 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Leading the Way | 5.55 | 5.096 | 4.443 | 3.685 | 3.154 | 2.593 | 1.782 | -5.981 | -12.057 | -16.667 | -16.777 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Leading the Way | 16.065 | 15.766 | 15.309 | 14.772 | 14.402 | 14 | 13.403 | 8.402 | 4.901 | 2.65 | 2.935 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Leading the Way | 8.272 | 8.302 | 8.281 | 8.22 | 8.209 | 8.176 | 8.072 | 5.968 | 4.355 | 3.309 | 3.768 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Leading the Way | 16.418 | 17.201 | 16.902 | 8.36 | 8.064 | 7.757 | 7.294 | 3.369 | 0.239 | -2.216 | -2.315 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Leading the Way | 10.992 | 10.541 | 9.897 | 9.142 | 8.543 | 7.912 | 7.021 | 0.507 | -4.345 | -7.702 | -7.878 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Leading the Way | 8.804 | 8.805 | 8.766 | 8.698 | 8.687 | 8.667 | 8.584 | 6.707 | 5.218 | 4.132 | 4.462 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Leading the Way | 10.821 | 10.374 | 9.711 | 8.944 | 8.462 | 7.958 | 7.171 | 0.847 | -3.69 | -6.775 | -6.434 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Leading the Way | 5.074 | 4.531 | 3.78 | 2.89 | 2.141 | 1.32 | 0.222 | -8.885 | -15.951 | -21.104 | -21.974 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Leading the Way | 13.01 | 13.077 | 13.139 | 13.196 | 13.249 | 13.3 | 13.348 | 13.287 | 13.232 | 13.196 | 13.386 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Leading the Way | 13.755 | 13.835 | 13.894 | 13.927 | 13.938 | 13.921 | 13.874 | 12.995 | 12.421 | 12.215 | 12.469 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Leading the Way | 2.768 | 2.849 | 2.918 | 2.979 | 3.038 | 3.092 | 3.134 | 2.888 | 2.707 | 2.61 | 2.88 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Leading the Way | 6.36 | 6.206 | 5.981 | 5.745 | 5.602 | 5.448 | 5.195 | 2.822 | 1.147 | 0.099 | 0.452 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Leading the Way | 1.873 | 1.717 | 1.509 | 1.282 | 1.087 | 0.879 | 0.595 | -1.408 | -2.89 | -3.906 | -4.03 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Leading the Way | 12.653 | 12.387 | 11.991 | 11.518 | 11.151 | 10.75 | 10.184 | 5.559 | 2.219 | 0.101 | 0.379 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Leading the Way | 12.617 | 10.626 | 10.616 | 10.589 | 10.557 | 10.511 | 10.427 | 8.698 | 7.353 | 6.421 | 6.719 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Leading the Way | 9.207 | 8.84 | 15.338 | 14.837 | 14.5 | 14.143 | 13.573 | 8.832 | 5.358 | 2.957 | 3.248 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Leading the Way | 11.486 | 11.365 | 11.186 | 10.959 | 10.816 | 10.644 | 10.359 | 7.071 | 4.337 | 2.332 | 2.214 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Leading the Way | 3.164 | 1.514 | 0.965 | 0.529 | 0.231 | -0.089 | -0.653 | -6.273 | -10.722 | -14.006 | -13.65 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Leading the Way | 12.955 | 12.93 | 12.881 | 12.815 | 12.793 | 12.766 | 12.703 | 11.595 | 10.619 | 9.808 | 9.782 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Leading the Way | 8.531 | 8.369 | 15.07 | 14.696 | 14.515 | 14.314 | 13.926 | 9.606 | 6.386 | 4.227 | 4.783 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Leading the Way | 5.203 | 3.983 | 3.351 | 2.833 | 2.424 | 1.975 | 1.327 | -4.333 | -8.661 | -11.708 | -11.721 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Leading the Way | 10.195 | 9.73 | 9.025 | 8.202 | 7.741 | 7.259 | 6.461 | -0.263 | -5.271 | -8.724 | -8.335 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Leading the Way | 12.809 | 12.655 | 10.324 | 9.99 | 9.658 | 9.227 | 8.644 | 4.073 | 0.766 | -0.96 | -1.227 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Leading the Way | 9.472 | 9.057 | 8.456 | 7.761 | 7.282 | 6.766 | 6.019 | 0.517 | -3.438 | -6.056 | -6.119 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Leading the Way | 7.805 | 5.838 | 5.361 | 4.846 | 4.528 | 4.187 | 3.613 | -1.728 | -5.811 | -8.668 | -8.319 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Leading the Way | 8.554 | 7.862 | 7.903 | 7.903 | 7.877 | 7.816 | 7.71 | 5.437 | 3.74 | 2.728 | 3.188 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Leading the Way | 18.874 | 18.834 | 18.751 | 18.622 | 18.467 | 18.257 | 17.975 | 15.527 | 13.825 | 13.028 | 13.109 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Leading the Way | 8.644 | 8.525 | 8.288 | 7.986 | 7.837 | 7.676 | 7.347 | 4.01 | 1.429 | -0.428 | -0.076 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Leading the Way | 10.536 | 10.344 | 10.054 | 9.709 | 9.387 | 9.038 | 8.524 | 4.374 | 1.273 | -0.906 | -0.814 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Leading the Way | 12.44 | 12.194 | 11.805 | 11.336 | 11.072 | 10.795 | 10.328 | 5.455 | 1.798 | -0.784 | -0.332 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Leading the Way | 12.364 | 12.337 | 12.259 | 12.149 | 12.111 | 12.056 | 11.931 | 9.999 | 8.498 | 7.512 | 7.825 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Leading the Way | 8.409 | 8.531 | 8.639 | 8.753 | 8.865 | 8.968 | 9.051 | 8.701 | 8.431 | 8.25 | 8.692 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Leading the Way | 8.261 | 6.391 | 6.202 | 5.968 | 5.898 | 5.801 | 5.54 | 2.033 | -0.711 | -2.556 | -2.09 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Leading the Way | 10.385 | 9.206 | 9.269 | 9.316 | 9.369 | 9.417 | 9.445 | 8.58 | 7.909 | 7.415 | 7.814 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Leading the Way | 1.705 | 1.522 | 1.268 | 0.978 | 0.764 | 0.539 | 0.216 | -2.568 | -4.698 | -6.303 | -6.431 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 3.43 | 3.39 | 3.326 | 3.258 | 3.248 | 3.236 | 3.189 | 2.269 | 1.503 | 0.928 | 1.041 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Leading the Way | 13.861 | 13.765 | 13.604 | 13.389 | 13.2 | 12.963 | 12.637 | 9.802 | 7.686 | 6.447 | 6.388 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Leading the Way | 24.617 | 24.645 | 24.669 | 24.685 | 24.697 | 24.707 | 24.715 | 24.103 | 23.504 | 22.95 | 22.979 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Leading the Way | 14.971 | 14.995 | 14.988 | 14.961 | 14.968 | 14.971 | 14.93 | 13.981 | 13.203 | 12.615 | 12.855 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Leading the Way | -0.825 | -0.936 | -1.1 | -1.302 | -1.464 | -1.647 | -1.902 | -4.41 | -6.517 | -8.146 | -8.472 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Leading the Way | 3.728 | 3.46 | 3.073 | 2.575 | 2.122 | 1.567 | 0.809 | -6.654 | -12.521 | -16.457 | -16.884 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Leading the Way | 11.093 | 10.912 | 10.595 | 10.204 | 9.976 | 9.734 | 9.315 | 5.454 | 2.565 | 0.569 | 0.962 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Leading the Way | 11.73 | 11.834 | 11.92 | 11.988 | 12.038 | 12.067 | 12.073 | 11.723 | 11.542 | 11.574 | 11.835 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Leading the Way | 8.617 | 8.216 | 7.611 | 6.893 | 6.392 | 5.845 | 5.006 | -2.257 | -7.753 | -11.514 | -11.336 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Leading the Way | 17.103 | 16.427 | 16.343 | 16.242 | 16.187 | 16.129 | 16.018 | 14.358 | 12.903 | 11.685 | 11.685 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Leading the Way | 4.951 | 4.652 | 4.254 | 3.865 | 3.571 | 3.268 | 2.788 | -0.932 | -3.789 | -5.854 | -5.691 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Leading the Way | 8.605 | 8.377 | 7.97 | 7.447 | 7.093 | 6.72 | 6.068 | 0.075 | -4.59 | -8.043 | -7.741 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Leading the Way | -1.167 | -1.371 | -1.67 | -2.012 | -2.227 | -2.452 | -2.824 | -6.498 | -9.352 | -11.451 | -11.259 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Leading the Way | 15.39 | 15.328 | 15.225 | 15.081 | 14.935 | 14.756 | 14.503 | 11.599 | 9.281 | 7.673 | 7.675 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Leading the Way | 15.823 | 15.266 | 14.664 | 14.266 | 13.949 | 13.608 | 13.094 | 8.819 | 5.638 | 3.468 | 3.632 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Leading the Way | 10.786 | 10.417 | 9.845 | 9.173 | 8.783 | 8.367 | 7.721 | 2.514 | -1.238 | -3.698 | -3.448 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Leading the Way | 24.274 | 24.316 | 24.353 | 24.392 | 24.431 | 24.467 | 24.495 | 24.297 | 24.136 | 24.017 | 24.184 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Leading the Way | 8.485 | 8.507 | 8.523 | 8.543 | 8.562 | 8.579 | 8.586 | 7.543 | 6.68 | 5.998 | 6.3 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Leading the Way | 11.275 | 10.974 | 10.493 | 9.913 | 9.585 | 9.241 | 8.68 | 3.999 | 0.542 | -1.847 | -1.591 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Leading the Way | -0.701 | -0.725 | -0.768 | -0.825 | -0.846 | -0.872 | -0.928 | -1.664 | -2.341 | -2.91 | -3.024 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Leading the Way | 9.307 | 9.199 | 9.044 | 8.856 | 8.731 | 8.592 | 8.388 | 6.059 | 4.067 | 2.478 | 2.293 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Leading the Way | 13.427 | 13.133 | 12.676 | 12.141 | 11.826 | 11.494 | 10.927 | 5.963 | 2.16 | -0.599 | -0.413 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Leading the Way | 11.6 | 11.35 | 11.001 | 10.602 | 10.32 | 10.022 | 9.578 | 5.802 | 2.887 | 0.852 | 0.874 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Leading the Way | 8.368 | 8.035 | 7.544 | 6.957 | 6.443 | 5.893 | 5.138 | -0.276 | -4.311 | -7.118 | -7.33 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Leading the Way | 13.55 | 13.327 | 13.044 | 12.713 | 12.408 | 12.065 | 11.615 | 7.461 | 3.964 | 1.282 | 0.627 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Leading the Way | 7.698 | 7.656 | 7.524 | 7.316 | 7.166 | 6.971 | 6.585 | 1.858 | -1.868 | -4.413 | -3.954 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Leading the Way | 14.056 | 13.801 | 13.403 | 12.934 | 12.672 | 12.395 | 11.941 | 8.036 | 5.124 | 3.113 | 3.323 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Leading the Way | 7.429 | 7.03 | 6.486 | 5.944 | 5.579 | 5.193 | 4.552 | -1.37 | -5.905 | -9.193 | -8.837 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Leading the Way | 8.092 | 7.922 | 7.687 | 7.403 | 7.198 | 6.967 | 6.645 | 2.508 | -0.983 | -3.747 | -3.993 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - System Transformation | 12.919 | 12.626 | 12.418 | 12.358 | 12.3 | 12.235 | 12.163 | 11.724 | 10.841 | 9.474 | 7.38 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - System Transformation | 12.526 | 10.88 | 10.814 | 10.714 | 10.603 | 10.458 | 10.273 | 8.895 | 6.763 | 4.868 | 2.544 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - System Transformation | 11.443 | 11.174 | 10.839 | 10.442 | 9.958 | 9.449 | 8.917 | 6.243 | 3.149 | -0.322 | -4.708 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - System Transformation | 5.854 | 4.434 | 4.434 | 4.408 | 4.365 | 4.303 | 4.209 | 3.546 | 1.559 | -0.063 | -1.817 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 5.271 | 4.944 | 4.592 | 4.27 | 3.953 | 3.63 | 3.298 | 1.778 | 0.063 | -2.023 | -5.111 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 5.317 | 5.304 | 5.283 | 5.261 | 5.236 | 5.205 | 5.171 | 4.971 | 4.64 | 4.224 | 3.622 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - System Transformation | 9.889 | 9.42 | 8.858 | 8.247 | 7.639 | 7.01 | 6.354 | 3.177 | -0.121 | -4.136 | -9.653 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - System Transformation | 17.073 | 17.084 | 17.081 | 17.069 | 17.058 | 17.041 | 17.011 | 16.828 | 15.741 | 14.616 | 13.172 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - System Transformation | 1.322 | 1.119 | 0.86 | 0.558 | 0.233 | -0.11 | -0.471 | -2.279 | -5.075 | -8.114 | -12.105 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - System Transformation | 2.868 | 2.298 | 2.375 | 2.433 | 2.481 | 2.516 | 2.534 | 2.504 | 1.71 | 0.911 | -0.062 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - System Transformation | 12.037 | 11.828 | 11.546 | 11.219 | 10.895 | 10.557 | 10.197 | 8.474 | 6.332 | 3.953 | 0.72 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - System Transformation | 2.436 | 2.127 | 1.8 | 1.495 | 1.157 | 0.782 | 0.354 | -1.934 | -5.114 | -7.856 | -10.974 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - System Transformation | 3.064 | 3.048 | 3.026 | 2.998 | 2.966 | 2.93 | 2.889 | 2.648 | 2.278 | 1.941 | 1.591 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - System Transformation | 15.736 | 15.563 | 15.328 | 15.064 | 14.823 | 14.574 | 14.309 | 13.058 | 11.166 | 8.899 | 5.61 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - System Transformation | 12.878 | 12.387 | 12.339 | 12.28 | 12.226 | 12.165 | 12.096 | 11.695 | 10.917 | 10.004 | 8.841 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - System Transformation | 10.508 | 10.502 | 10.469 | 10.412 | 10.346 | 10.264 | 10.158 | 9.515 | 7.87 | 6.37 | 4.639 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - System Transformation | 15.476 | 15.17 | 14.773 | 14.324 | 13.851 | 13.354 | 12.831 | 10.215 | 7.723 | 5.019 | 1.43 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - System Transformation | 8.41 | 8.421 | 8.415 | 8.394 | 8.367 | 8.328 | 8.275 | 7.858 | 6.809 | 5.791 | 4.502 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - System Transformation | 6.55 | 6.411 | 6.237 | 6.031 | 5.818 | 5.592 | 5.346 | 3.992 | 1.364 | -1.661 | -5.607 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - System Transformation | 21.762 | 21.707 | 21.61 | 21.483 | 21.359 | 21.229 | 21.091 | 20.428 | 19.611 | 18.616 | 17.147 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - System Transformation | 3.724 | 3.576 | 3.409 | 3.233 | 3.069 | 2.898 | 2.716 | 1.726 | 0.18 | -1.638 | -4.03 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - System Transformation | 11.325 | 10.874 | 10.314 | 9.686 | 9.042 | 8.363 | 7.634 | 3.868 | -0.175 | -4.711 | -10.734 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - System Transformation | 9.445 | 9.075 | 8.644 | 8.21 | 7.786 | 7.344 | 6.88 | 4.638 | 1.852 | -1.215 | -5.536 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - System Transformation | 14.761 | 14.522 | 14.239 | 13.959 | 13.655 | 13.342 | 13.021 | 11.55 | 10.3 | 8.727 | 6.46 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - System Transformation | 2.384 | 2.339 | 2.225 | 2.059 | 1.884 | 1.67 | 1.409 | -0.268 | -2.905 | -5.644 | -9.272 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - System Transformation | 5.806 | 5.589 | 5.315 | 5.001 | 4.68 | 4.338 | 3.972 | 2.067 | -0.006 | -2.034 | -4.468 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 15.106 | 15.081 | 15.05 | 15.012 | 14.969 | 14.917 | 14.853 | 14.461 | 13.465 | 12.448 | 11.166 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 4.166 | 1.08 | 1.034 | 0.953 | 0.835 | 0.674 | 0.462 | -1.091 | -4.423 | -7.472 | -11.093 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - System Transformation | 8.152 | 8.04 | 7.872 | 7.656 | 7.415 | 7.134 | 6.805 | 4.761 | 1.728 | -1.107 | -4.498 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - System Transformation | 11.657 | 11.372 | 10.995 | 10.561 | 10.15 | 9.723 | 9.277 | 7.08 | 4.251 | 0.669 | -4.691 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - System Transformation | 6.001 | 5.554 | 4.97 | 4.305 | 3.652 | 2.962 | 2.225 | -1.573 | -6.436 | -11.474 | -18.24 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - System Transformation | 6.832 | 6.812 | 6.789 | 6.762 | 6.735 | 6.709 | 6.679 | 6.535 | 6.226 | 5.912 | 5.544 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - System Transformation | 4.307 | 4.267 | 4.218 | 4.162 | 4.1 | 4.032 | 3.957 | 3.548 | 2.943 | 2.407 | 1.819 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - System Transformation | 13.647 | 13.359 | 12.991 | 12.577 | 12.181 | 11.77 | 11.334 | 9.222 | 6.796 | 3.893 | -0.272 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 13.864 | 13.732 | 13.596 | 13.45 | 13.297 | 13.141 | 12.975 | 12.094 | 10.51 | 8.913 | 7.244 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - System Transformation | 5.517 | 5.439 | 5.342 | 5.234 | 5.128 | 5.02 | 4.907 | 4.376 | 3.838 | 3.268 | 2.515 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 10.473 | 10.181 | 9.799 | 9.372 | 8.963 | 8.535 | 8.078 | 5.864 | 2.945 | -0.328 | -4.944 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - System Transformation | 11.456 | 11.171 | 10.796 | 10.375 | 9.96 | 9.52 | 9.052 | 6.711 | 3.705 | 0.701 | -3.372 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - System Transformation | 9.209 | 9.221 | 9.207 | 9.173 | 9.138 | 9.087 | 9.012 | 8.455 | 7.15 | 5.699 | 3.737 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - System Transformation | 10.282 | 10.25 | 10.181 | 10.088 | 9.99 | 9.88 | 9.75 | 9.077 | 7.958 | 7.021 | 5.923 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - System Transformation | 17.389 | 17.222 | 17.015 | 16.78 | 16.534 | 16.272 | 15.991 | 14.546 | 13.226 | 11.973 | 10.455 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - System Transformation | 7.845 | 22.353 | 22.113 | 21.85 | 21.589 | 21.316 | 21.03 | 19.626 | 17.38 | 14.924 | 11.516 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - System Transformation | 10.63 | 10.19 | 9.62 | 8.971 | 8.341 | 7.699 | 7.042 | 3.964 | -0.055 | -4.728 | -11.289 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - System Transformation | 3.804 | 3.697 | 3.576 | 3.464 | 3.352 | 3.237 | 3.117 | 2.591 | 2.095 | 1.482 | 0.587 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - System Transformation | 6.074 | 5.439 | 4.761 | 4.117 | 3.439 | 2.729 | 1.994 | -1.617 | -4.933 | -8.804 | -14.174 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - System Transformation | 4.504 | 4.083 | 3.551 | 2.932 | 2.237 | 1.501 | 0.721 | -3.195 | -8.873 | -14.33 | -20.968 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - System Transformation | 5.829 | 5.265 | 4.544 | 3.725 | 2.921 | 2.093 | 1.233 | -2.937 | -8.298 | -14.253 | -22.334 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - System Transformation | 4.271 | 4.311 | 4.342 | 4.364 | 4.379 | 4.386 | 4.384 | 4.28 | 3.935 | 3.662 | 3.399 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - System Transformation | 7.758 | 7.33 | 6.745 | 6.052 | 5.339 | 4.563 | 3.716 | -0.91 | -6.058 | -10.95 | -17.216 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - System Transformation | 12.973 | 13.032 | 13.079 | 13.112 | 13.134 | 13.144 | 13.139 | 13.012 | 12.125 | 11.42 | 10.737 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - System Transformation | 10.222 | 10.314 | 10.396 | 10.468 | 10.532 | 10.588 | 10.635 | 10.783 | 10.605 | 10.439 | 10.277 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - System Transformation | 10.905 | 10.939 | 10.967 | 11.004 | 11.027 | 11.033 | 11.011 | 10.754 | 9.048 | 7.41 | 5.456 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - System Transformation | 11.678 | 11.71 | 11.729 | 11.74 | 11.744 | 11.74 | 11.724 | 11.6 | 11.012 | 10.482 | 9.883 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - System Transformation | 10.802 | 10.53 | 10.171 | 9.765 | 9.348 | 8.894 | 8.395 | 5.701 | 3.002 | 0.385 | -3.041 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - System Transformation | 4.251 | 4.157 | 4.035 | 3.898 | 3.753 | 3.603 | 3.449 | 2.757 | 2.247 | 1.9 | 1.621 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - System Transformation | 5.128 | 5.051 | 4.953 | 4.841 | 4.714 | 4.577 | 4.427 | 3.603 | 2.581 | 1.518 | 0.401 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - System Transformation | 13.595 | 13.12 | 12.599 | 12.108 | 11.624 | 11.122 | 10.597 | 8.077 | 4.954 | 1.571 | -3.162 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - System Transformation | -0.039 | -0.059 | -0.088 | -0.126 | -0.17 | -0.22 | -0.277 | -0.612 | -1.11 | -1.567 | -2.031 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - System Transformation | 3.256 | 3.057 | 2.825 | 2.575 | 2.32 | 2.056 | 1.78 | 0.497 | -0.84 | -2.208 | -3.886 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 9.467 | 9.305 | 9.064 | 8.764 | 8.424 | 8.052 | 7.643 | 5.468 | 3.385 | 0.996 | -2.234 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - System Transformation | 9.075 | 8.914 | 8.751 | 8.622 | 8.491 | 8.348 | 8.182 | 7.334 | 5.532 | 3.757 | 1.476 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - System Transformation | 5.259 | 4.953 | 4.592 | 4.203 | 3.819 | 3.418 | 2.987 | 0.802 | -2.254 | -5.512 | -9.706 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - System Transformation | 4.778 | 4.793 | 4.803 | 4.808 | 4.809 | 4.805 | 4.796 | 4.695 | 4.451 | 4.242 | 4.003 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - System Transformation | 21.888 | 21.697 | 21.477 | 21.26 | 21.061 | 20.853 | 20.633 | 19.576 | 17.908 | 15.904 | 13.009 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - System Transformation | 7.843 | 7.857 | 7.863 | 7.87 | 7.876 | 7.872 | 7.85 | 7.664 | 6.604 | 5.548 | 4.228 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - System Transformation | 13.373 | 13.017 | 12.65 | 12.331 | 12.014 | 11.685 | 11.341 | 9.732 | 7.72 | 5.455 | 2.237 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - System Transformation | 7.189 | 7.13 | 7.014 | 6.857 | 6.697 | 6.517 | 6.307 | 5.164 | 2.845 | 0.681 | -2.079 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - System Transformation | 4.53 | 3.859 | 3.076 | 2.293 | 1.56 | 0.8 | 0.001 | -3.796 | -8.111 | -13.113 | -20.361 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - System Transformation | 0.94 | 0.897 | 0.848 | 0.794 | 0.736 | 0.674 | 0.606 | 0.24 | -0.42 | -1.026 | -1.686 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - System Transformation | 3.083 | 2.934 | 2.752 | 2.538 | 2.303 | 2.041 | 1.745 | 0.016 | -2.57 | -4.842 | -7.201 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - System Transformation | 12.929 | 12.859 | 12.742 | 12.59 | 12.434 | 12.267 | 12.089 | 11.235 | 9.979 | 8.667 | 6.898 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - System Transformation | 14.736 | 14.547 | 15.274 | 14.947 | 14.63 | 14.301 | 13.953 | 12.275 | 10.011 | 7.39 | 3.569 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - System Transformation | 22.244 | 22.213 | 22.118 | 21.95 | 21.729 | 21.432 | 21.045 | 18.193 | 13.49 | 10.19 | 7.002 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - System Transformation | 9.687 | 9.38 | 9.001 | 8.575 | 8.135 | 7.675 | 7.19 | 4.757 | 1.559 | -1.89 | -6.33 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - System Transformation | 2.34 | 2.118 | 1.867 | 1.59 | 1.31 | 1.018 | 0.707 | -0.833 | -2.452 | -4.31 | -6.847 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - System Transformation | 7.943 | 7.603 | 7.111 | 6.534 | 6.004 | 5.459 | 4.889 | 2.149 | -1.488 | -6.402 | -14.016 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - System Transformation | 6.058 | 3.758 | 3.739 | 3.706 | 3.662 | 3.607 | 3.538 | 3.065 | 2.042 | 1.077 | -0.114 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - System Transformation | 7.315 | 6.85 | 6.262 | 5.618 | 4.988 | 4.339 | 3.656 | 0.469 | -3.047 | -6.948 | -12.483 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - System Transformation | 3.826 | 3.549 | 17.887 | 17.48 | 17.065 | 16.627 | 16.161 | 13.792 | 10.451 | 6.952 | 2.196 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - System Transformation | -0.217 | -0.369 | -0.56 | -0.775 | -0.985 | -1.201 | -1.426 | -2.502 | -4.118 | -5.815 | -8.027 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - System Transformation | 2.818 | 2.819 | 2.809 | 2.788 | 2.765 | 2.736 | 2.696 | 2.433 | 1.789 | 1.199 | 0.508 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - System Transformation | 10.303 | 10.026 | 9.64 | 9.191 | 8.738 | 8.27 | 7.788 | 5.551 | 3.014 | -0.149 | -4.781 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - System Transformation | 8.375 | 8.062 | 7.649 | 7.186 | 6.735 | 6.259 | 5.745 | 3.161 | 0.147 | -3.351 | -8.354 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - System Transformation | 12.365 | 12.237 | 12.062 | 11.857 | 11.64 | 11.406 | 11.152 | 9.83 | 8.413 | 6.997 | 5.257 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - System Transformation | 3.706 | 2.727 | 2.712 | 2.661 | 2.598 | 2.505 | 2.377 | 1.402 | -0.628 | -2.573 | -5.039 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - System Transformation | 15.204 | 15.102 | 14.978 | 14.828 | 14.658 | 14.464 | 14.237 | 12.846 | 10.584 | 8.657 | 6.677 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - System Transformation | 4.047 | 3.948 | 3.822 | 3.681 | 3.539 | 3.393 | 3.24 | 2.506 | 1.546 | 0.435 | -1.071 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - System Transformation | 2.427 | 2.359 | 2.268 | 2.165 | 2.066 | 1.963 | 1.855 | 1.338 | 0.557 | -0.332 | -1.589 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - System Transformation | 14.826 | 14.465 | 14.008 | 13.491 | 12.988 | 12.452 | 11.871 | 8.817 | 4.892 | 0.868 | -4.416 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - System Transformation | 1.841 | 1.669 | 1.411 | 1.092 | 0.746 | 0.373 | -0.036 | -2.167 | -5.734 | -9.457 | -14.48 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - System Transformation | 14.738 | 14.677 | 14.58 | 14.463 | 14.361 | 14.247 | 14.116 | 13.358 | 11.968 | 10.181 | 7.566 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - System Transformation | 4.68 | 4.579 | 4.456 | 4.317 | 4.169 | 4.015 | 3.855 | 3.089 | 2.105 | 1.079 | -0.214 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - System Transformation | 6.73 | 6.282 | 5.713 | 5.077 | 4.432 | 3.761 | 3.05 | -0.296 | -4.036 | -7.794 | -12.564 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - System Transformation | 12.457 | 12.134 | 11.725 | 11.276 | 10.824 | 10.36 | 9.873 | 7.638 | 5.193 | 2.416 | -1.378 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - System Transformation | 12.789 | 11.128 | 11.05 | 10.921 | 10.754 | 10.528 | 10.234 | 8.055 | 5.063 | 2.866 | 0.645 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - System Transformation | 2.855 | 2.566 | 2.296 | 2.093 | 1.886 | 1.673 | 1.454 | 0.509 | -0.23 | -0.969 | -1.897 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - System Transformation | 7.713 | 7.07 | 6.307 | 5.48 | 4.636 | 3.766 | 2.867 | -1.439 | -4.795 | -9.363 | -15.91 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - System Transformation | 8.467 | 8.43 | 8.383 | 8.33 | 8.271 | 8.207 | 8.139 | 7.733 | 7.242 | 6.737 | 6.216 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - System Transformation | 1.973 | 1.772 | 1.495 | 1.146 | 0.736 | 0.244 | -0.335 | -4.167 | -8.57 | -11.338 | -13.749 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - System Transformation | 11.648 | 11.267 | 10.865 | 10.506 | 10.163 | 9.8 | 9.414 | 7.457 | 4.622 | 1.314 | -3.425 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - System Transformation | 9.156 | 8.776 | 8.273 | 7.693 | 7.139 | 6.553 | 5.926 | 2.723 | -0.825 | -4.693 | -10.057 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - System Transformation | 0.814 | 0.694 | 0.539 | 0.353 | 0.143 | -0.097 | -0.371 | -2.051 | -3.915 | -5.29 | -6.572 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - System Transformation | 7.28 | 6.919 | 6.45 | 5.922 | 5.408 | 4.878 | 4.325 | 1.725 | -1.903 | -6.063 | -11.881 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - System Transformation | 0.797 | 0.75 | 0.666 | 0.563 | 0.466 | 0.356 | 0.222 | -0.555 | -2.319 | -4.178 | -6.602 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - System Transformation | 1.484 | 1.482 | 1.48 | 1.478 | 1.475 | 1.471 | 1.467 | 1.446 | 1.415 | 1.386 | 1.356 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 10.356 | 10.376 | 10.371 | 10.342 | 10.301 | 10.251 | 10.182 | 9.791 | 8.524 | 7.114 | 5.269 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 7.076 | 7.041 | 6.989 | 6.926 | 6.861 | 6.79 | 6.71 | 6.31 | 5.61 | 4.893 | 3.957 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 8.477 | 8.387 | 8.27 | 8.135 | 7.993 | 7.847 | 7.697 | 7.033 | 6.399 | 5.834 | 5.205 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 3.815 | 3.611 | 3.364 | 3.1 | 2.83 | 2.541 | 2.229 | 0.555 | -1.266 | -3.174 | -5.693 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - System Transformation | 14.431 | 14.164 | 13.821 | 14.417 | 13.95 | 13.467 | 12.975 | 10.651 | 8.656 | 6.158 | 2.823 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - System Transformation | 9.969 | 8.906 | 8.577 | 8.194 | 7.826 | 7.445 | 7.041 | 5.127 | 2.718 | -0.164 | -4.353 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - System Transformation | 3.206 | 3.005 | 2.762 | 2.486 | 2.186 | 1.857 | 1.497 | -0.534 | -3.109 | -5.261 | -7.637 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - System Transformation | 10.487 | 9.744 | 9.108 | 8.715 | 8.349 | 7.97 | 7.572 | 5.672 | 3.124 | -0.024 | -4.661 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - System Transformation | 10.662 | 10.567 | 10.457 | 10.337 | 10.217 | 10.09 | 9.952 | 9.156 | 7.685 | 6.003 | 3.937 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - System Transformation | -3.21 | -3.912 | -4.787 | -5.751 | -6.703 | -7.685 | -8.706 | -13.568 | -19.216 | -25.447 | -33.88 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - System Transformation | 6.788 | 6.16 | 5.471 | 4.822 | 4.166 | 3.495 | 2.807 | -0.287 | -2.662 | -6.081 | -11.205 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - System Transformation | 5.102 | 5.1 | 5.051 | 4.972 | 4.923 | 4.857 | 4.764 | 4.043 | 2.294 | -0.261 | -4.326 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 17.193 | 14.136 | 13.947 | 13.74 | 13.536 | 13.325 | 13.102 | 12.011 | 10.15 | 8.226 | 5.924 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - System Transformation | 13.796 | 13.736 | 13.658 | 13.56 | 13.44 | 13.301 | 13.141 | 12.135 | 10.568 | 9.208 | 7.841 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - System Transformation | 9.497 | 9.248 | 8.96 | 8.627 | 8.253 | 7.831 | 7.353 | 4.404 | 0.515 | -2.517 | -5.3 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - System Transformation | 12.656 | 12.642 | 12.596 | 12.528 | 12.464 | 12.391 | 12.299 | 11.811 | 10.323 | 8.62 | 6.289 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - System Transformation | 11.471 | 11.503 | 11.512 | 11.503 | 11.49 | 11.466 | 11.432 | 11.214 | 10.683 | 10.113 | 9.382 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 4.047 | 3.819 | 3.561 | 3.269 | 2.939 | 2.566 | 2.145 | -0.506 | -3.953 | -6.651 | -9.086 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - System Transformation | 16.261 | 16.184 | 16.084 | 15.97 | 15.865 | 15.747 | 15.613 | 14.776 | 13.447 | 11.929 | 9.905 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - System Transformation | 10.654 | 10.404 | 10.059 | 9.667 | 9.302 | 8.924 | 8.52 | 6.585 | 4.042 | 0.917 | -3.678 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - System Transformation | 10.204 | 10.109 | 9.959 | 9.777 | 9.618 | 9.441 | 9.236 | 8.035 | 5.91 | 3.324 | -0.402 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - System Transformation | 6.934 | 6.58 | 6.106 | 5.556 | 5.021 | 4.453 | 3.841 | 0.73 | -2.836 | -6.608 | -11.778 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - System Transformation | 4.369 | 3.985 | 3.519 | 3.016 | 2.506 | 1.961 | 1.374 | -1.719 | -5.414 | -9.098 | -13.68 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - System Transformation | 11.687 | 11.661 | 11.609 | 11.535 | 11.43 | 11.291 | 11.116 | 9.893 | 8.528 | 7.811 | 7.37 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - System Transformation | 15.275 | 14.996 | 14.613 | 14.171 | 13.77 | 13.362 | 12.935 | 10.935 | 8.66 | 5.527 | 0.65 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - System Transformation | 9.117 | 8.663 | 8.072 | 7.388 | 6.693 | 5.938 | 5.112 | 0.627 | -4.489 | -9.085 | -14.736 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - System Transformation | 3.249 | 3.124 | 2.969 | 3.298 | 3.128 | 2.953 | 2.769 | 1.874 | 0.794 | -0.301 | -1.696 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - System Transformation | 7.927 | 7.679 | 7.342 | 6.96 | 6.574 | 6.174 | 5.755 | 3.779 | 0.653 | -2.889 | -7.884 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - System Transformation | 4.012 | 3.839 | 3.608 | 3.351 | 3.097 | 2.837 | 2.568 | 1.318 | 0.139 | -1.507 | -4.047 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 12.206 | 12.163 | 12.104 | 12.029 | 11.951 | 11.862 | 11.761 | 11.163 | 10.068 | 8.894 | 7.469 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 25.283 | 25.241 | 25.187 | 25.121 | 25.055 | 24.983 | 24.901 | 24.466 | 23.439 | 22.366 | 21.039 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - System Transformation | 14.505 | 14.37 | 14.196 | 13.985 | 13.724 | 13.446 | 13.153 | 11.656 | 10.468 | 9.276 | 7.902 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - System Transformation | 12.633 | 12.667 | 12.686 | 12.689 | 12.686 | 12.675 | 12.65 | 12.475 | 11.517 | 10.624 | 9.58 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - System Transformation | 19.789 | 19.758 | 19.72 | 19.676 | 19.63 | 19.582 | 19.527 | 19.234 | 18.502 | 17.74 | 16.86 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - System Transformation | 6.594 | 6.38 | 6.08 | 5.724 | 5.345 | 4.95 | 4.539 | 2.606 | 0.906 | -1.502 | -5.079 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 22.359 | 22.331 | 22.259 | 22.153 | 22.053 | 21.935 | 21.79 | 20.945 | 19.052 | 17.023 | 14.319 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - System Transformation | 14.489 | 14.42 | 14.331 | 14.237 | 14.171 | 14.098 | 14.008 | 13.481 | 11.974 | 10.057 | 7.26 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - System Transformation | 4.696 | 4.612 | 4.501 | 4.377 | 4.263 | 4.143 | 4.016 | 3.387 | 2.665 | 1.817 | 0.565 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - System Transformation | 4.496 | 4.464 | 4.427 | 4.387 | 4.343 | 4.296 | 4.243 | 3.93 | 3.574 | 3.255 | 2.947 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - System Transformation | 15.577 | 15.484 | 15.358 | 15.205 | 15.042 | 14.859 | 14.646 | 13.382 | 11.06 | 8.8 | 6.137 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 9.615 | 9.472 | 9.279 | 9.055 | 8.833 | 8.602 | 8.36 | 7.214 | 5.774 | 4.22 | 2.06 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 11.493 | 11.401 | 11.278 | 11.135 | 11 | 10.861 | 10.715 | 10.011 | 8.973 | 7.706 | 5.845 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - System Transformation | 2.276 | 2.111 | 1.917 | 1.707 | 1.482 | 1.249 | 1.01 | -0.152 | -1.535 | -3.007 | -4.894 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - System Transformation | 3.33 | 3.138 | 2.911 | 2.655 | 2.403 | 2.127 | 1.81 | -0.057 | -3.319 | -6.79 | -11.232 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - System Transformation | 18.899 | 18.875 | 18.84 | 18.796 | 18.746 | 18.684 | 18.611 | 18.122 | 17.495 | 16.977 | 16.416 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - System Transformation | 4.817 | 4.734 | 4.627 | 4.509 | 4.394 | 4.277 | 4.154 | 3.565 | 2.725 | 1.731 | 0.277 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - System Transformation | 14.757 | 14.729 | 14.7 | 14.673 | 14.644 | 14.606 | 14.555 | 14.196 | 13.363 | 12.515 | 11.393 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - System Transformation | 12.581 | 12.649 | 12.703 | 12.744 | 12.778 | 12.8 | 12.809 | 12.721 | 12.291 | 11.883 | 11.398 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - System Transformation | 2.121 | 1.821 | 1.435 | 0.993 | 0.54 | 0.067 | -0.428 | -2.82 | -4.92 | -7.009 | -9.665 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 5.867 | 5.833 | 5.783 | 5.723 | 5.663 | 5.596 | 5.519 | 5.071 | 4.254 | 3.338 | 2.139 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 5.22 | 5.171 | 5.103 | 5.021 | 4.931 | 4.826 | 4.704 | 3.935 | 2.92 | 1.96 | 0.807 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - System Transformation | 5.142 | 4.812 | 4.397 | 3.933 | 3.47 | 2.985 | 2.474 | -0.087 | -3.198 | -6.421 | -10.657 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - System Transformation | 15.278 | 15.192 | 15.084 | 14.963 | 14.851 | 14.731 | 14.595 | 13.84 | 12.386 | 10.792 | 8.751 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - System Transformation | 8.024 | 7.428 | 6.771 | 6.147 | 5.509 | 4.851 | 4.169 | 1.023 | -2.615 | -6.566 | -12.083 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - System Transformation | 4.771 | 4.684 | 4.577 | 4.464 | 4.333 | 4.177 | 3.988 | 2.791 | 0.304 | -2.293 | -5.679 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - System Transformation | 10.252 | 9.943 | 9.516 | 9.017 | 8.548 | 8.064 | 7.561 | 5.11 | 1.411 | -3.152 | -9.874 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - System Transformation | 0.19 | 0.104 | 0.004 | -0.112 | -0.232 | -0.361 | -0.505 | -1.337 | -2.628 | -4.041 | -5.807 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - System Transformation | 13.326 | 13.031 | 12.648 | 12.229 | 11.81 | 11.374 | 10.913 | 8.693 | 6.091 | 3.241 | -0.784 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - System Transformation | 18.398 | 18.389 | 18.372 | 18.346 | 18.312 | 18.273 | 18.224 | 17.936 | 17.17 | 16.467 | 15.651 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - System Transformation | 12.448 | 12.263 | 12.046 | 11.811 | 11.571 | 11.32 | 11.051 | 9.618 | 7.903 | 5.421 | 1.802 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - System Transformation | 7.097 | 6.969 | 6.808 | 6.618 | 6.415 | 6.195 | 5.959 | 4.611 | 2.572 | 0.245 | -2.88 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - System Transformation | 8.124 | 7.969 | 7.758 | 7.498 | 7.232 | 6.925 | 6.569 | 4.218 | 0.602 | -3.044 | -7.744 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - System Transformation | 16.293 | 16.249 | 16.201 | 16.148 | 16.093 | 16.034 | 15.971 | 15.602 | 15.146 | 14.674 | 14.201 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - System Transformation | 16.915 | 16.821 | 16.684 | 16.518 | 16.343 | 16.157 | 15.957 | 14.987 | 13.563 | 12.172 | 10.374 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - System Transformation | 18.977 | 18.934 | 18.878 | 18.814 | 18.75 | 18.685 | 18.615 | 18.285 | 17.678 | 17.039 | 16.225 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - System Transformation | 8.901 | 8.36 | 7.843 | 7.446 | 7.071 | 6.684 | 6.274 | 4.363 | 1.949 | -1.071 | -5.492 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - System Transformation | 10.295 | 9.858 | 9.347 | 8.835 | 8.342 | 7.831 | 7.294 | 4.758 | 1.834 | -1.443 | -6.142 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - System Transformation | -6.559 | -6.478 | -6.418 | -6.376 | -6.35 | -6.339 | -6.345 | -6.539 | -7.097 | -7.539 | -7.98 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - System Transformation | 9.932 | 9.231 | 8.553 | 8.018 | 7.498 | 6.963 | 6.407 | 3.809 | 0.324 | -3.818 | -9.838 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - System Transformation | 11.324 | 11.204 | 11.048 | 10.857 | 10.66 | 10.435 | 10.171 | 8.538 | 5.679 | 2.972 | -0.285 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - System Transformation | 5.127 | 4.826 | 4.45 | 4.03 | 3.617 | 3.194 | 2.758 | 0.734 | -1.804 | -4.62 | -8.402 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - System Transformation | 24.4 | 24.373 | 24.309 | 24.219 | 24.143 | 24.055 | 23.945 | 23.293 | 21.266 | 19.002 | 15.931 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - System Transformation | 6.314 | 6.089 | 5.818 | 5.515 | 5.198 | 4.86 | 4.495 | 2.545 | 0.152 | -2.362 | -5.335 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - System Transformation | 6.763 | 6.753 | 6.739 | 6.723 | 6.708 | 6.692 | 6.674 | 6.584 | 6.455 | 6.324 | 6.142 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - System Transformation | 11.402 | 10.898 | 10.228 | 9.464 | 8.728 | 7.968 | 7.169 | 3.336 | -0.877 | -6.148 | -13.869 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - System Transformation | 21.959 | 21.969 | 21.952 | 21.904 | 21.819 | 21.69 | 21.516 | 20.085 | 18.401 | 17.56 | 17.1 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - System Transformation | 11.151 | 10.907 | 10.591 | 10.243 | 9.917 | 9.574 | 9.206 | 7.39 | 4.934 | 2.103 | -1.93 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - System Transformation | 12.056 | 11.922 | 11.735 | 11.485 | 11.165 | 10.771 | 10.298 | 6.998 | 2.675 | -0.502 | -3.646 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - System Transformation | 0.704 | 0.595 | 0.454 | 0.293 | 0.123 | -0.06 | -0.264 | -1.378 | -2.975 | -4.371 | -5.941 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - System Transformation | 6.933 | 1.206 | 0.913 | 0.578 | 0.219 | -0.155 | -0.541 | -2.426 | -4.16 | -6.191 | -8.914 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - System Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - System Transformation | 4.926 | 4.667 | 4.344 | 3.986 | 3.626 | 3.254 | 2.861 | 0.953 | -1.298 | -3.813 | -7.124 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - System Transformation | 12.854 | 12.655 | 12.4 | 12.097 | 11.747 | 11.318 | 10.802 | 7.352 | 3.138 | 0.238 | -2.568 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - System Transformation | 2.142 | 1.914 | 1.627 | 1.329 | 1.026 | 0.7 | 0.343 | -1.492 | -3.541 | -5.893 | -9.157 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - System Transformation | 2.165 | 1.978 | 1.785 | 1.626 | 1.466 | 1.3 | 1.129 | 0.362 | -0.34 | -1.291 | -2.716 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - System Transformation | 12.894 | 12.75 | 12.545 | 12.309 | 12.1 | 11.878 | 11.637 | 10.39 | 8.636 | 6.541 | 3.467 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - System Transformation | 7.82 | 7.834 | 7.843 | 7.852 | 7.853 | 7.844 | 7.817 | 7.638 | 6.371 | 5.276 | 4.106 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - System Transformation | 13.481 | 13.424 | 13.335 | 13.222 | 13.121 | 13.008 | 12.874 | 12.073 | 10.616 | 8.709 | 5.928 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - System Transformation | 6.96 | 6.52 | 5.978 | 5.374 | 4.759 | 4.121 | 3.452 | 0.177 | -3.512 | -7.064 | -11.371 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - System Transformation | 12.721 | 12.687 | 12.612 | 12.502 | 12.372 | 12.199 | 11.977 | 10.313 | 8.162 | 6.515 | 4.712 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - System Transformation | 13.744 | 13.773 | 13.796 | 13.814 | 13.829 | 13.841 | 13.847 | 13.84 | 13.602 | 13.382 | 13.142 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - System Transformation | 5.891 | 5.872 | 5.846 | 5.816 | 5.787 | 5.754 | 5.719 | 5.538 | 5.367 | 5.169 | 4.876 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - System Transformation | 14.141 | 14.16 | 14.164 | 14.154 | 14.137 | 14.114 | 14.076 | 13.866 | 12.838 | 11.902 | 10.855 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - System Transformation | -4.167 | -4.428 | -4.786 | -5.202 | -5.593 | -5.999 | -6.425 | -8.488 | -10.708 | -13.563 | -17.823 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - System Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - System Transformation | 8.804 | 7.695 | 7.136 | 6.513 | 5.914 | 5.297 | 4.659 | 1.641 | -2.164 | -6.767 | -13.357 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - System Transformation | 8.659 | 8.11 | 7.439 | 6.746 | 12.081 | 11.399 | 10.684 | 7.365 | 4.004 | -0.215 | -6.579 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - System Transformation | 3.972 | 4.026 | 4.058 | 4.067 | 4.056 | 4.03 | 3.988 | 3.64 | 2.178 | 0.668 | -1.247 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - System Transformation | 2.215 | 1.885 | 1.457 | 0.956 | 0.404 | -0.165 | -0.746 | -3.42 | -7.006 | -10.913 | -16.092 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - System Transformation | 14.309 | 14.113 | 13.864 | 13.593 | 13.324 | 13.045 | 12.753 | 11.358 | 9.221 | 6.802 | 3.377 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - System Transformation | 5.315 | 4.865 | 4.247 | 3.528 | 2.809 | 2.056 | 1.253 | -2.673 | -6.748 | -11.498 | -18.163 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - System Transformation | 5.022 | 3.999 | 3.684 | 3.371 | 3.059 | 2.719 | 2.347 | 0.348 | -2.182 | -5.075 | -9.185 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - System Transformation | 15.006 | 14.849 | 14.647 | 14.431 | 14.233 | 14.028 | 13.81 | 12.778 | 11.464 | 9.799 | 7.28 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - System Transformation | 4.028 | 3.756 | 3.391 | 2.981 | 2.585 | 2.165 | 1.712 | -0.59 | -3.396 | -6.425 | -10.688 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - System Transformation | 7.72 | 7.479 | 7.189 | 6.855 | 6.499 | 6.113 | 5.688 | 3.279 | 0.187 | -3.167 | -7.359 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - System Transformation | 8.699 | 8.311 | 7.815 | 7.254 | 6.679 | 6.081 | 5.454 | 2.464 | 0.071 | -3.19 | -8.018 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - System Transformation | 6.656 | 6.357 | 5.964 | 5.512 | 5.006 | 4.486 | 3.959 | 1.529 | -0.345 | -2.547 | -5.494 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - System Transformation | 2.088 | 1.293 | 0.483 | -0.21 | -0.9 | -1.614 | -2.351 | -5.837 | -10.351 | -15.456 | -22.686 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - System Transformation | 9.476 | 8.962 | 8.393 | 7.859 | 7.37 | 6.867 | 6.34 | 3.86 | 1.002 | -2.719 | -8.372 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - System Transformation | 10.433 | 9.922 | 9.352 | 8.808 | 8.255 | 7.663 | 7.025 | 3.726 | 0.13 | -3.407 | -8.117 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - System Transformation | 13.35 | 13.343 | 13.305 | 13.233 | 13.144 | 13.024 | 12.863 | 11.685 | 9.614 | 8.045 | 6.447 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - System Transformation | 8.763 | 8.637 | 8.471 | 8.283 | 8.099 | 7.906 | 7.697 | 6.663 | 5.052 | 3.389 | 1.134 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - System Transformation | 3.499 | 3.455 | 3.374 | 3.262 | 3.133 | 2.978 | 2.79 | 1.557 | 0.075 | -1.318 | -3.035 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - System Transformation | 12.811 | 12.586 | 12.286 | 11.948 | 11.636 | 11.313 | 10.973 | 9.376 | 7.263 | 4.791 | 1.202 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - System Transformation | 17.56 | 17.449 | 17.28 | 17.072 | 16.865 | 16.649 | 16.423 | 15.347 | 14.036 | 12.601 | 10.537 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - System Transformation | 15.292 | 15.22 | 15.117 | 14.989 | 14.836 | 14.673 | 14.501 | 13.551 | 12.369 | 10.421 | 7.535 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - System Transformation | 4.048 | 3.892 | 3.688 | 3.428 | 3.114 | 2.735 | 2.283 | -0.759 | -4.696 | -7.788 | -10.997 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - System Transformation | 10.064 | 10.088 | 10.094 | 10.081 | 10.057 | 10.018 | 9.956 | 9.505 | 8.103 | 6.819 | 5.357 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - System Transformation | -1.273 | -1.378 | -1.508 | -1.657 | -1.803 | -1.967 | -2.155 | -3.308 | -5.053 | -6.784 | -8.906 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - System Transformation | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - System Transformation | 6.545 | 6.064 | 5.532 | 5.01 | 4.485 | 3.93 | 3.336 | 0.382 | -2.487 | -5.811 | -10.542 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - System Transformation | 14.224 | 13.925 | 13.546 | 13.114 | 12.726 | 12.325 | 11.901 | 9.813 | 7.52 | 4.459 | -0.297 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - System Transformation | 3.407 | 3.258 | 3.078 | 2.88 | 2.69 | 2.496 | 2.291 | 1.315 | 0.041 | -1.323 | -3.127 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - System Transformation | 8.678 | 8.383 | 8.009 | 7.539 | 6.986 | 6.317 | 5.516 | 0.11 | -6.805 | -11.94 | -16.956 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - System Transformation | 12.909 | 12.397 | 11.873 | 11.411 | 10.968 | 10.51 | 10.026 | 7.754 | 4.942 | 1.906 | -2.313 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - System Transformation | 5.036 | 4.938 | 4.816 | 4.683 | 4.554 | 4.423 | 4.288 | 3.644 | 2.802 | 1.836 | 0.489 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - System Transformation | 6.562 | 6.119 | 5.572 | 4.967 | 4.387 | 3.789 | 3.162 | 0.202 | -3.958 | -8.589 | -14.864 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - System Transformation | 10.061 | 9.779 | 9.398 | 8.965 | 8.564 | 8.15 | 7.715 | 5.636 | 2.668 | -0.841 | -5.941 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - System Transformation | 14.746 | 14.398 | 14.016 | 13.654 | 13.296 | 12.932 | 12.56 | 10.911 | 8.989 | 6.637 | 3.205 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - System Transformation | 6.299 | 6.116 | 5.847 | 5.525 | 5.22 | 4.895 | 4.539 | 2.738 | 0.157 | -2.813 | -7.015 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - System Transformation | 13.881 | 13.479 | 12.999 | 12.461 | 11.868 | 11.242 | 10.582 | 7.249 | 3.306 | -0.469 | -4.956 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - System Transformation | 13.057 | 13.009 | 12.948 | 12.872 | 12.796 | 12.714 | 12.622 | 12.103 | 11.084 | 9.837 | 8.165 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - System Transformation | 9.093 | 8.79 | 8.406 | 7.985 | 7.548 | 7.084 | 6.582 | 4.046 | 1.568 | -1.079 | -4.601 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - System Transformation | 12.38 | 12.382 | 12.352 | 12.29 | 12.21 | 12.101 | 11.958 | 10.937 | 9.362 | 8.158 | 6.903 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - System Transformation | 6.818 | 6.772 | 6.673 | 6.529 | 6.36 | 6.152 | 5.896 | 4.186 | 1.838 | -0.405 | -3.177 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - System Transformation | 25.577 | 25.46 | 25.301 | 25.103 | 24.881 | 24.628 | 24.342 | 22.651 | 20.606 | 18.967 | 17.342 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - System Transformation | 4.402 | 4.146 | 3.86 | 3.55 | 3.248 | 2.928 | 2.589 | 0.619 | -2.566 | -6.16 | -10.762 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - System Transformation | 1.829 | 1.772 | 1.698 | 1.614 | 1.526 | 1.434 | 1.337 | 0.863 | 0.365 | -0.114 | -0.625 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - System Transformation | 12.344 | 12.058 | 11.721 | 11.361 | 10.997 | 10.618 | 10.213 | 8.237 | 5.677 | 2.819 | -0.981 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - System Transformation | 10.136 | 10.129 | 10.1 | 10.056 | 10.014 | 9.96 | 9.886 | 9.385 | 8.186 | 6.991 | 5.446 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - System Transformation | 10.203 | 10.128 | 10.001 | 9.833 | 9.666 | 9.483 | 9.276 | 8.059 | 4.837 | 0.901 | -4.758 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - System Transformation | 0.671 | 0.599 | 0.508 | 0.401 | 0.285 | 0.154 | 0.004 | -0.892 | -2.305 | -3.598 | -5.027 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - System Transformation | 9.377 | 9.369 | 9.308 | 9.185 | 8.99 | 8.714 | 8.345 | 5.489 | 1.277 | -1.292 | -3.321 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - System Transformation | 16.392 | 16.336 | 16.27 | 16.209 | 16.143 | 16.067 | 15.977 | 15.455 | 14.55 | 13.712 | 12.683 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - System Transformation | 8.838 | 7.676 | 7.193 | 6.654 | 6.118 | 5.563 | 4.978 | 2.129 | -1.859 | -6.129 | -11.751 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - System Transformation | 12.164 | 12.042 | 11.867 | 11.664 | 11.467 | 11.26 | 11.043 | 9.994 | 8.61 | 6.915 | 4.423 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - System Transformation | 18.04 | 18.051 | 17.992 | 17.853 | 17.633 | 17.314 | 16.892 | 13.583 | 9.546 | 7.377 | 5.958 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - System Transformation | 10.021 | 9.679 | 9.221 | 8.707 | 8.238 | 7.746 | 7.218 | 4.538 | 1.221 | -2.811 | -8.807 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - System Transformation | 4.267 | 4.202 | 4.119 | 4.025 | 3.933 | 3.836 | 3.734 | 3.231 | 2.641 | 1.993 | 1.129 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - System Transformation | 9.326 | 8.989 | 8.616 | 8.26 | 7.943 | 7.611 | 7.254 | 5.461 | 3.05 | 0.102 | -4.201 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 15.059 | 14.883 | 14.655 | 14.381 | 14.08 | 13.754 | 13.393 | 11.367 | 8.344 | 4.992 | 0.831 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 13.482 | 13.307 | 13.078 | 12.799 | 12.505 | 12.182 | 11.815 | 9.704 | 5.559 | 1.312 | -3.755 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - System Transformation | 13.326 | 13.325 | 13.304 | 13.266 | 13.218 | 13.155 | 13.072 | 12.537 | 11.278 | 10.187 | 8.978 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - System Transformation | 8.09 | 8.107 | 8.099 | 8.072 | 8.057 | 8.034 | 7.998 | 7.726 | 6.822 | 5.614 | 3.814 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - System Transformation | 17.502 | 17.395 | 17.241 | 17.061 | 16.877 | 16.686 | 16.482 | 15.513 | 14.604 | 13.448 | 11.766 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - System Transformation | 5.688 | 5.614 | 5.526 | 5.42 | 5.297 | 5.157 | 4.998 | 3.972 | 2.531 | 1.203 | -0.108 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - System Transformation | 1.996 | 1.501 | 0.964 | 0.468 | 0.008 | -0.468 | -0.966 | -3.332 | -6.216 | -9.795 | -15.089 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - System Transformation | 12.606 | 12.247 | 11.845 | 11.457 | 11.071 | 10.673 | 10.262 | 8.342 | 6.067 | 3.222 | -0.927 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - System Transformation | 9.786 | 9.297 | 8.722 | 8.138 | 7.568 | 6.959 | 6.301 | 2.824 | -0.919 | -5.035 | -10.738 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 11.583 | 11.588 | 11.561 | 11.502 | 11.413 | 11.29 | 11.126 | 9.917 | 8.09 | 6.827 | 5.683 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - System Transformation | 15.96 | 15.753 | 15.472 | 15.153 | 14.862 | 14.563 | 14.25 | 12.782 | 11.209 | 9.243 | 6.265 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - System Transformation | 12.847 | 12.725 | 12.541 | 12.316 | 12.09 | 11.852 | 11.593 | 10.306 | 7.974 | 5.685 | 2.679 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - System Transformation | 9.284 | 9.033 | 8.693 | 8.304 | 7.924 | 7.513 | 7.058 | 4.662 | 1.699 | -1.241 | -5.14 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - System Transformation | 11.458 | 9.705 | 9.532 | 9.323 | 9.127 | 8.921 | 8.702 | 7.646 | 6.051 | 4.018 | 0.953 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - System Transformation | 5.178 | 5.087 | 4.975 | 4.856 | 4.735 | 4.608 | 4.476 | 3.86 | 3.126 | 2.402 | 1.474 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - System Transformation | 14.137 | 13.732 | 13.211 | 12.641 | 12.077 | 11.495 | 10.885 | 8.026 | 5.05 | 1.72 | -3.107 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - System Transformation | 2.987 | 2.642 | 2.165 | 1.615 | 1.069 | 0.502 | -0.095 | -2.93 | -6.951 | -11.548 | -18.081 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - System Transformation | 14.726 | 14.466 | 14.132 | 13.776 | 13.421 | 13.052 | 12.662 | 10.808 | 8.889 | 6.655 | 3.404 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - System Transformation | 6.872 | 6.439 | 5.898 | 5.321 | 4.766 | 4.191 | 3.581 | 0.73 | -2.869 | -7.14 | -13.298 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - System Transformation | 19.259 | 19.273 | 19.234 | 19.149 | 19.061 | 18.948 | 18.799 | 17.803 | 15.001 | 12.115 | 8.299 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - System Transformation | 12.459 | 12.317 | 12.137 | 11.939 | 11.719 | 11.485 | 11.234 | 10.013 | 8.636 | 7.231 | 5.462 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - System Transformation | 4.43 | 4.091 | 3.661 | 3.176 | 2.704 | 2.208 | 1.675 | -1.024 | -4.501 | -8.048 | -12.623 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - System Transformation | 8.598 | 7.85 | 6.956 | 5.964 | 4.846 | 3.682 | 2.496 | -3.23 | -8.589 | -14.306 | -21.563 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - System Transformation | 4.458 | 4.099 | 3.687 | 3.278 | 2.867 | 2.438 | 1.987 | -0.229 | -3.507 | -7.319 | -12.757 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - System Transformation | 12.78 | 12.332 | 11.785 | 11.19 | 10.61 | 10.019 | 9.411 | 6.592 | 4.004 | 0.528 | -4.645 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - System Transformation | 20.861 | 17.761 | 17.785 | 17.804 | 17.819 | 17.833 | 17.842 | 17.871 | 17.588 | 17.347 | 17.112 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - System Transformation | 3.311 | 3.096 | 2.823 | 2.495 | 2.106 | 1.649 | 1.114 | -2.337 | -6.716 | -10.216 | -13.704 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - System Transformation | 13.765 | 13.674 | 13.549 | 13.412 | 13.302 | 13.184 | 13.047 | 12.245 | 10.625 | 8.344 | 4.815 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - System Transformation | 14.242 | 14.285 | 14.315 | 14.338 | 14.357 | 14.371 | 14.376 | 14.337 | 14.054 | 13.677 | 13.133 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - System Transformation | 15.641 | 15.662 | 15.669 | 15.664 | 15.659 | 15.649 | 15.628 | 15.481 | 14.809 | 14.14 | 13.301 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - System Transformation | 9.413 | 8.906 | 8.249 | 7.508 | 6.775 | 6.02 | 5.236 | 1.56 | -1.832 | -6.09 | -12.3 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - System Transformation | 14.663 | 14.546 | 14.403 | 14.243 | 14.102 | 13.95 | 13.778 | 12.751 | 10.626 | 8.231 | 5.062 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - System Transformation | 5.915 | 5.844 | 5.733 | 5.594 | 5.464 | 5.321 | 5.152 | 4.195 | 1.902 | -0.788 | -4.524 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - System Transformation | 13.922 | 13.743 | 13.502 | 13.226 | 12.948 | 12.654 | 12.34 | 10.81 | 8.916 | 6.947 | 4.332 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - System Transformation | 17.505 | 13.933 | 13.884 | 13.831 | 13.773 | 13.709 | 13.64 | 13.32 | 13.046 | 12.808 | 12.529 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - System Transformation | 10.828 | 10.592 | 10.304 | 9.997 | 9.689 | 9.368 | 9.026 | 7.34 | 5.598 | 3.578 | 0.767 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - System Transformation | 2.634 | 2.457 | 2.225 | 1.957 | 1.677 | 1.368 | 1.027 | -0.905 | -2.932 | -4.779 | -7.041 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - System Transformation | 10.924 | 10.61 | 10.222 | 9.816 | 9.399 | 8.97 | 8.523 | 6.495 | 4.882 | 2.479 | -1.281 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - System Transformation | 12.502 | 12.3 | 12.031 | 11.729 | 11.447 | 11.151 | 10.835 | 9.276 | 7.414 | 5.223 | 2.025 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - System Transformation | 5.452 | 5.241 | 4.976 | 4.651 | 4.286 | 3.864 | 3.379 | 0.242 | -4.449 | -8.662 | -13.406 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - System Transformation | 16.481 | 16.322 | 16.126 | 15.905 | 15.686 | 15.459 | 15.221 | 14.026 | 12.483 | 10.885 | 8.823 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - System Transformation | 11.594 | 9.836 | 9.571 | 9.255 | 8.912 | 8.524 | 8.088 | 5.283 | 1.533 | -2.498 | -7.739 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - System Transformation | 4.664 | 4.54 | 4.388 | 4.22 | 4.052 | 3.88 | 3.701 | 2.866 | 1.963 | 1.034 | -0.169 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - System Transformation | 14.711 | 14.444 | 14.084 | 13.673 | 13.278 | 12.869 | 12.44 | 10.462 | 8.412 | 6.194 | 3.096 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - System Transformation | -0.027 | -0.22 | -0.457 | -0.721 | -0.987 | -1.269 | -1.571 | -3.109 | -5.301 | -7.397 | -9.992 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - System Transformation | 9.149 | 8.814 | 8.381 | 7.893 | 7.397 | 6.88 | 6.333 | 3.682 | 0.091 | -3.77 | -8.856 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - System Transformation | 8.296 | 8.001 | 7.603 | 7.149 | 6.72 | 6.268 | 5.779 | 3.367 | 0.171 | -3.207 | -7.88 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - System Transformation | 5.344 | 4.898 | 4.339 | 3.714 | 3.101 | 2.463 | 1.781 | -1.527 | -6.451 | -11.572 | -18.197 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - System Transformation | 15.926 | 15.65 | 15.286 | 14.869 | 14.449 | 14.004 | 13.525 | 11.147 | 8.523 | 5.839 | 2.256 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - System Transformation | 8.176 | 8.198 | 8.189 | 8.152 | 8.108 | 8.045 | 7.955 | 7.311 | 5.762 | 4.293 | 2.522 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - System Transformation | 16.358 | 17.134 | 16.865 | 8.36 | 8.042 | 7.714 | 7.376 | 5.772 | 3.497 | 0.959 | -2.499 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - System Transformation | 10.792 | 10.371 | 9.833 | 9.213 | 8.548 | 7.856 | 7.136 | 3.635 | 0.325 | -3.515 | -8.733 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - System Transformation | 8.738 | 8.735 | 8.709 | 8.664 | 8.625 | 8.576 | 8.509 | 8.071 | 6.759 | 5.432 | 3.716 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - System Transformation | 10.546 | 10.153 | 9.643 | 9.067 | 8.483 | 7.883 | 7.259 | 4.352 | 1.58 | -2.013 | -7.362 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - System Transformation | 4.851 | 4.295 | 3.606 | 2.822 | 2.006 | 1.134 | 0.187 | -4.857 | -11.471 | -17.563 | -24.633 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - System Transformation | 12.972 | 13.021 | 13.065 | 13.101 | 13.133 | 13.16 | 13.182 | 13.247 | 13.034 | 12.851 | 12.676 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - System Transformation | 13.7 | 13.759 | 13.801 | 13.822 | 13.821 | 13.797 | 13.748 | 13.246 | 12.3 | 11.764 | 11.424 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - System Transformation | 2.711 | 2.767 | 2.815 | 2.853 | 2.882 | 2.904 | 2.916 | 2.897 | 2.512 | 2.184 | 1.85 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - System Transformation | 6.267 | 6.102 | 5.911 | 5.723 | 5.543 | 5.354 | 5.149 | 4.151 | 2.852 | 1.409 | -0.551 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - System Transformation | 1.816 | 1.647 | 1.452 | 1.247 | 1.032 | 0.806 | 0.571 | -0.616 | -1.849 | -3.089 | -4.63 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - System Transformation | 12.6 | 12.346 | 12.012 | 11.626 | 11.241 | 10.83 | 10.384 | 8.096 | 5.321 | 2.789 | -0.356 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - System Transformation | 12.572 | 10.574 | 10.565 | 10.544 | 10.508 | 10.459 | 10.388 | 9.914 | 8.497 | 7.37 | 6.216 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - System Transformation | 9.057 | 8.668 | 15.236 | 14.828 | 14.432 | 14.021 | 13.587 | 11.54 | 9.08 | 6.27 | 2.247 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - System Transformation | 11.375 | 11.242 | 11.083 | 10.899 | 10.716 | 10.51 | 10.274 | 8.758 | 6.314 | 3.736 | 0.485 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - System Transformation | 2.928 | 1.21 | 0.718 | 0.342 | -0.03 | -0.423 | -0.843 | -2.961 | -6.341 | -10.198 | -15.556 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - System Transformation | 12.864 | 12.811 | 12.745 | 12.668 | 12.593 | 12.511 | 12.419 | 11.876 | 10.844 | 9.649 | 8.147 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - System Transformation | 8.383 | 8.231 | 15.003 | 14.733 | 14.485 | 14.217 | 13.92 | 12.368 | 10.003 | 7.27 | 3.386 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - System Transformation | 4.986 | 3.72 | 3.169 | 2.735 | 2.289 | 1.811 | 1.292 | -1.401 | -5.118 | -8.711 | -13.154 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - System Transformation | 9.988 | 9.571 | 9.025 | 8.419 | 7.857 | 7.279 | 6.679 | 3.876 | 0.949 | -3.087 | -9.36 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - System Transformation | 12.722 | 12.583 | 10.306 | 10.058 | 9.761 | 9.397 | 8.958 | 5.921 | 2.281 | -0.248 | -2.566 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - System Transformation | 9.242 | 8.86 | 8.376 | 7.833 | 7.273 | 6.688 | 6.07 | 3.02 | 0.234 | -2.951 | -7.35 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - System Transformation | 7.64 | 5.684 | 5.304 | 4.915 | 4.541 | 4.147 | 3.725 | 1.642 | -1.121 | -4.388 | -9.119 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - System Transformation | 8.482 | 7.778 | 7.814 | 7.816 | 7.789 | 7.732 | 7.634 | 6.829 | 4.74 | 3.314 | 2.119 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - System Transformation | 18.855 | 18.828 | 18.776 | 18.694 | 18.581 | 18.429 | 18.235 | 16.808 | 14.893 | 13.757 | 12.901 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - System Transformation | 8.516 | 8.391 | 8.195 | 7.961 | 7.743 | 7.514 | 7.269 | 6.06 | 4.394 | 2.187 | -1.216 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - System Transformation | 10.499 | 10.31 | 10.054 | 9.751 | 9.412 | 9.048 | 8.659 | 6.664 | 4.089 | 1.645 | -1.445 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - System Transformation | 12.328 | 12.103 | 11.797 | 11.446 | 11.129 | 10.801 | 10.449 | 8.78 | 6.182 | 3.226 | -0.964 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - System Transformation | 12.263 | 12.252 | 12.214 | 12.155 | 12.085 | 11.999 | 11.894 | 11.228 | 10.037 | 8.726 | 7 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - System Transformation | 8.307 | 8.381 | 8.449 | 8.518 | 8.576 | 8.622 | 8.652 | 8.69 | 8.084 | 7.548 | 6.962 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - System Transformation | 8.12 | 6.253 | 6.127 | 5.987 | 5.863 | 5.715 | 5.536 | 4.347 | 2.403 | -0.022 | -3.571 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - System Transformation | 10.289 | 9.089 | 9.135 | 9.164 | 9.177 | 9.182 | 9.17 | 9.065 | 8.21 | 7.452 | 6.643 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - System Transformation | 1.639 | 1.446 | 1.214 | 0.961 | 0.715 | 0.461 | 0.19 | -1.141 | -2.893 | -4.694 | -7.037 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 3.363 | 3.337 | 3.304 | 3.271 | 3.235 | 3.197 | 3.15 | 2.901 | 2.404 | 1.696 | 0.645 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - System Transformation | 13.769 | 13.679 | 13.551 | 13.388 | 13.197 | 12.97 | 12.704 | 10.996 | 8.827 | 7.055 | 5.213 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - System Transformation | 24.55 | 24.549 | 24.542 | 24.527 | 24.503 | 24.475 | 24.438 | 24.202 | 23.342 | 22.522 | 21.678 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - System Transformation | 14.926 | 14.939 | 14.932 | 14.911 | 14.888 | 14.86 | 14.824 | 14.634 | 14.064 | 13.456 | 12.663 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - System Transformation | -1.011 | -1.194 | -1.413 | -1.664 | -1.928 | -2.213 | -2.526 | -4.311 | -6.839 | -9.403 | -12.288 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - System Transformation | 3.574 | 3.308 | 2.982 | 2.588 | 2.149 | 1.633 | 1.026 | -2.93 | -8.869 | -13.782 | -18.969 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - System Transformation | 10.972 | 10.799 | 10.542 | 10.239 | 9.95 | 9.651 | 9.333 | 7.85 | 5.855 | 3.459 | -0.057 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - System Transformation | 11.668 | 11.742 | 11.8 | 11.842 | 11.866 | 11.872 | 11.858 | 11.582 | 11.032 | 10.741 | 10.584 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - System Transformation | 8.431 | 8.033 | 7.522 | 6.943 | 6.372 | 5.768 | 5.121 | 1.75 | -2.545 | -7.103 | -13.173 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - System Transformation | 17.057 | 16.385 | 16.32 | 16.245 | 16.17 | 16.091 | 16.005 | 15.538 | 14.472 | 13.142 | 11.301 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - System Transformation | 4.863 | 4.54 | 4.186 | 3.855 | 3.53 | 3.198 | 2.86 | 1.325 | -0.561 | -2.835 | -6.174 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - System Transformation | 8.517 | 8.274 | 7.917 | 7.487 | 7.077 | 6.649 | 6.2 | 4.024 | 0.866 | -2.862 | -8.374 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - System Transformation | -1.257 | -1.449 | -1.688 | -1.947 | -2.198 | -2.457 | -2.732 | -4.051 | -6.014 | -8.331 | -11.643 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - System Transformation | 15.344 | 15.28 | 15.192 | 15.076 | 14.941 | 14.779 | 14.584 | 13.317 | 10.973 | 9.044 | 7.017 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - System Transformation | 15.659 | 15.055 | 14.54 | 14.215 | 13.89 | 13.547 | 13.181 | 11.352 | 8.899 | 6.506 | 3.362 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - System Transformation | 10.549 | 10.266 | 9.858 | 9.385 | 8.901 | 8.398 | 7.865 | 5.349 | 3.173 | 0.249 | -4.172 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - System Transformation | 24.236 | 24.261 | 24.285 | 24.308 | 24.328 | 24.344 | 24.354 | 24.361 | 24.093 | 23.846 | 23.561 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - System Transformation | 8.439 | 8.45 | 8.461 | 8.473 | 8.478 | 8.478 | 8.467 | 8.397 | 7.441 | 6.636 | 5.811 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - System Transformation | 11.122 | 10.855 | 10.482 | 10.05 | 9.645 | 9.228 | 8.791 | 6.79 | 4.672 | 1.876 | -2.418 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - System Transformation | -0.798 | -0.86 | -0.935 | -1.019 | -1.101 | -1.19 | -1.287 | -1.87 | -2.721 | -3.744 | -5.025 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - System Transformation | 9.2 | 9.076 | 8.924 | 8.75 | 8.577 | 8.391 | 8.186 | 7.057 | 5.195 | 3.202 | 0.742 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - System Transformation | 13.29 | 13.015 | 12.651 | 12.246 | 11.862 | 11.466 | 11.05 | 9.068 | 6.679 | 3.61 | -1.082 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - System Transformation | 11.496 | 11.254 | 10.958 | 10.631 | 10.308 | 9.969 | 9.611 | 7.783 | 5.677 | 3.191 | -0.19 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - System Transformation | 8.156 | 7.841 | 7.421 | 6.925 | 6.359 | 5.764 | 5.149 | 2.122 | -0.798 | -4.017 | -8.215 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - System Transformation | 13.406 | 13.143 | 12.843 | 12.51 | 12.158 | 11.772 | 11.349 | 8.867 | 5.151 | 1.669 | -2.178 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - System Transformation | 7.6 | 7.563 | 7.472 | 7.332 | 7.168 | 6.968 | 6.724 | 5.076 | 1.988 | -1.081 | -5.047 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - System Transformation | 13.912 | 13.7 | 13.406 | 13.069 | 12.743 | 12.405 | 12.051 | 10.403 | 8.643 | 6.312 | 2.748 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - System Transformation | 7.26 | 6.85 | 6.396 | 5.964 | 5.54 | 5.098 | 4.631 | 2.397 | -0.74 | -4.413 | -9.675 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - System Transformation | 7.934 | 7.756 | 7.543 | 7.297 | 7.036 | 6.753 | 6.43 | 4.601 | 1.211 | -2.127 | -6.008 | Primary
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NPg Best View | 13.323 | 13.179 | 13.016 | 12.961 | 12.95 | 12.933 | 12.903 | 12.79 | 11.256 | 9.973 | 8.749 | Primary
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NPg Best View | 12.631 | 11.014 | 10.938 | 10.803 | 10.696 | 10.543 | 10.333 | 8.964 | 6.491 | 4.849 | 3.4 | Primary
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NPg Best View | 11.596 | 11.366 | 11.026 | 10.627 | 10.186 | 9.732 | 9.227 | 7.023 | 2.764 | -0.66 | -3.746 | Primary
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NPg Best View | 5.998 | 4.643 | 4.686 | 4.681 | 4.668 | 4.631 | 4.558 | 4.045 | 2.057 | 0.606 | -0.676 | Primary
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NPg Best View | 5.528 | 5.295 | 4.988 | 4.687 | 4.496 | 4.293 | 4.042 | 2.993 | 0.383 | -1.7 | -3.654 | Primary
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NPg Best View | 5.4 | 5.419 | 5.412 | 5.397 | 5.406 | 5.41 | 5.401 | 5.353 | 4.706 | 4.168 | 3.64 | Primary
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NPg Best View | 10.195 | 9.785 | 9.208 | 8.537 | 8.091 | 7.626 | 7.091 | 4.745 | -0.133 | -3.925 | -7.63 | Primary
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NPg Best View | 17.19 | 17.251 | 17.275 | 17.281 | 17.298 | 17.311 | 17.315 | 17.36 | 16.116 | 15.075 | 14.094 | Primary
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NPg Best View | 1.482 | 1.346 | 1.13 | 0.856 | 0.616 | 0.358 | 0.05 | -1.359 | -4.953 | -7.934 | -10.68 | Primary
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NPg Best View | 3.081 | 2.601 | 2.75 | 2.868 | 2.992 | 3.102 | 3.19 | 3.555 | 2.931 | 2.447 | 1.976 | Primary
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NPg Best View | 12.233 | 12.059 | 11.776 | 11.429 | 11.211 | 10.979 | 10.7 | 9.472 | 6.684 | 4.489 | 2.3 | Primary
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NPg Best View | 2.766 | 2.56 | 2.241 | 1.916 | 1.653 | 1.347 | 0.958 | -0.971 | -4.34 | -6.613 | -8.71 | Primary
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NPg Best View | 3.117 | 3.125 | 3.121 | 3.11 | 3.099 | 3.084 | 3.06 | 2.923 | 2.618 | 2.377 | 2.147 | Primary
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NPg Best View | 15.897 | 15.753 | 15.506 | 15.203 | 15.053 | 14.894 | 14.699 | 13.877 | 11.052 | 8.811 | 6.614 | Primary
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NPg Best View | 12.99 | 12.551 | 12.534 | 12.503 | 12.491 | 12.475 | 12.45 | 12.342 | 11.564 | 10.891 | 10.224 | Primary
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NPg Best View | 10.635 | 10.667 | 10.635 | 10.569 | 10.518 | 10.454 | 10.369 | 9.934 | 8.092 | 6.745 | 5.53 | Primary
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NPg Best View | 15.72 | 15.444 | 15.037 | 14.554 | 14.209 | 13.832 | 13.381 | 11.28 | 7.869 | 5.431 | 3.141 | Primary
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NPg Best View | 8.482 | 8.527 | 8.539 | 8.526 | 8.515 | 8.49 | 8.446 | 8.135 | 6.912 | 5.985 | 5.175 | Primary
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NPg Best View | 6.727 | 6.645 | 6.48 | 6.273 | 6.113 | 5.949 | 5.766 | 4.898 | 1.654 | -1.16 | -3.92 | Primary
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NPg Best View | 21.863 | 21.855 | 21.792 | 21.692 | 21.632 | 21.564 | 21.468 | 21.094 | 19.972 | 19.087 | 18.26 | Primary
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NPg Best View | 3.843 | 3.739 | 3.59 | 3.421 | 3.307 | 3.188 | 3.057 | 2.414 | 0.647 | -0.911 | -2.477 | Primary
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NPg Best View | 11.695 | 11.321 | 10.758 | 10.076 | 9.61 | 9.1 | 8.493 | 5.587 | 0.109 | -3.996 | -7.935 | Primary
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NPg Best View | 9.696 | 9.424 | 9.024 | 8.589 | 8.289 | 7.966 | 7.574 | 5.853 | 1.919 | -1.123 | -3.961 | Primary
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NPg Best View | 15.023 | 14.83 | 14.556 | 14.276 | 14.081 | 13.876 | 13.625 | 12.625 | 10.695 | 9.262 | 7.921 | Primary
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NPg Best View | 2.612 | 2.61 | 2.466 | 2.246 | 2.122 | 1.956 | 1.732 | 0.463 | -2.866 | -5.228 | -7.484 | Primary
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NPg Best View | 5.999 | 5.847 | 5.612 | 5.318 | 5.095 | 4.845 | 4.54 | 3.053 | 0.786 | -0.847 | -2.369 | Primary
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 15.16 | 15.155 | 15.122 | 15.076 | 15.032 | 14.981 | 14.92 | 14.597 | 13.326 | 12.319 | 11.405 | Primary
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 4.437 | 1.442 | 1.431 | 1.349 | 1.273 | 1.142 | 0.942 | -0.399 | -4.188 | -6.938 | -9.366 | Primary
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NPg Best View | 8.328 | 8.26 | 8.069 | 7.816 | 7.584 | 7.309 | 6.974 | 5.168 | 1.771 | -0.646 | -2.882 | Primary
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NPg Best View | 11.852 | 11.628 | 11.256 | 10.794 | 10.516 | 10.221 | 9.862 | 8.286 | 3.826 | 0.218 | -3.218 | Primary
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NPg Best View | 6.278 | 5.939 | 5.384 | 4.708 | 4.208 | 3.661 | 3.003 | -0.079 | -6.313 | -11.068 | -15.515 | Primary
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NPg Best View | 6.85 | 6.837 | 6.819 | 6.797 | 6.777 | 6.757 | 6.735 | 6.634 | 6.313 | 6.026 | 5.746 | Primary
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NPg Best View | 4.359 | 4.341 | 4.306 | 4.262 | 4.218 | 4.17 | 4.108 | 3.797 | 3.242 | 2.814 | 2.412 | Primary
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NPg Best View | 13.84 | 13.57 | 13.155 | 12.667 | 12.378 | 12.073 | 11.713 | 10.151 | 6.559 | 3.772 | 0.993 | Primary
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 14.031 | 13.979 | 13.919 | 13.845 | 13.765 | 13.678 | 13.584 | 13.086 | 11.913 | 10.76 | 9.6 | Primary
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NPg Best View | 5.557 | 5.493 | 5.401 | 5.293 | 5.217 | 5.139 | 5.048 | 4.652 | 3.955 | 3.43 | 2.93 | Primary
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 10.735 | 10.522 | 10.16 | 9.715 | 9.46 | 9.184 | 8.84 | 7.314 | 3.173 | -0.044 | -3.134 | Primary
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NPg Best View | 11.652 | 11.465 | 11.141 | 10.745 | 10.452 | 10.129 | 9.726 | 7.869 | 4.003 | 1.076 | -1.607 | Primary
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NPg Best View | 9.376 | 9.437 | 9.437 | 9.4 | 9.411 | 9.403 | 9.369 | 9.103 | 7.466 | 6.217 | 5.013 | Primary
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NPg Best View | 10.457 | 10.499 | 10.494 | 10.452 | 10.447 | 10.426 | 10.37 | 10.056 | 9.007 | 8.245 | 7.524 | Primary
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NPg Best View | 17.503 | 17.366 | 17.165 | 16.921 | 16.735 | 16.527 | 16.274 | 15.047 | 13.453 | 12.421 | 11.493 | Primary
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NPg Best View | 7.994 | 22.571 | 22.368 | 22.125 | 21.95 | 21.762 | 21.532 | 20.504 | 17.412 | 14.893 | 12.587 | Primary
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NPg Best View | 10.832 | 10.501 | 10 | 9.392 | 8.934 | 8.463 | 7.915 | 5.627 | 0.143 | -4.443 | -8.791 | Primary
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NPg Best View | 3.917 | 3.835 | 3.721 | 3.606 | 3.545 | 3.48 | 3.396 | 3.065 | 2.338 | 1.805 | 1.27 | Primary
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NPg Best View | 6.433 | 5.904 | 5.228 | 4.553 | 4.011 | 3.435 | 2.767 | -0.186 | -5.321 | -9.113 | -12.447 | Primary
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NPg Best View | 4.745 | 4.46 | 4.021 | 3.494 | 2.924 | 2.32 | 1.615 | -1.626 | -8.008 | -13.303 | -18.167 | Primary
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NPg Best View | 6.129 | 5.689 | 5.034 | 4.242 | 3.652 | 3.032 | 2.307 | -0.902 | -7.877 | -13.574 | -18.992 | Primary
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NPg Best View | 4.359 | 4.438 | 4.503 | 4.555 | 4.6 | 4.634 | 4.654 | 4.686 | 4.502 | 4.403 | 4.324 | Primary
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NPg Best View | 8.047 | 7.661 | 7.044 | 6.271 | 5.691 | 5.024 | 4.208 | 0.034 | -6.352 | -10.779 | -14.853 | Primary
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NPg Best View | 13.097 | 13.21 | 13.304 | 13.371 | 13.427 | 13.468 | 13.492 | 13.523 | 12.778 | 12.245 | 11.789 | Primary
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NPg Best View | 10.371 | 10.533 | 10.679 | 10.812 | 10.933 | 11.044 | 11.14 | 11.552 | 11.645 | 11.729 | 11.808 | Primary
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NPg Best View | 11.241 | 11.419 | 11.548 | 11.66 | 11.771 | 11.862 | 11.921 | 12.133 | 10.478 | 9.162 | 7.956 | Primary
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NPg Best View | 11.817 | 11.91 | 11.971 | 12.015 | 12.066 | 12.108 | 12.132 | 12.238 | 11.651 | 11.194 | 10.756 | Primary
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NPg Best View | 11.015 | 10.78 | 10.392 | 9.922 | 9.59 | 9.208 | 8.732 | 6.361 | 2.828 | 0.521 | -1.606 | Primary
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NPg Best View | 4.343 | 4.302 | 4.232 | 4.148 | 4.066 | 3.976 | 3.862 | 3.404 | 3.113 | 2.95 | 2.828 | Primary
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NPg Best View | 5.37 | 5.407 | 5.406 | 5.391 | 5.368 | 5.334 | 5.278 | 5.018 | 4.459 | 3.945 | 3.427 | Primary
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NPg Best View | 13.932 | 13.586 | 13.121 | 12.648 | 12.323 | 11.972 | 11.542 | 9.617 | 5.224 | 1.816 | -1.309 | Primary
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NPg Best View | 0.051 | 0.073 | 0.078 | 0.074 | 0.069 | 0.055 | 0.028 | -0.127 | -0.479 | -0.758 | -1.029 | Primary
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NPg Best View | 3.379 | 3.218 | 3 | 2.753 | 2.571 | 2.381 | 2.159 | 1.204 | -0.356 | -1.54 | -2.685 | Primary
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 9.708 | 9.531 | 9.209 | 8.807 | 8.539 | 8.238 | 7.872 | 6.139 | 3.039 | 0.926 | -1.132 | Primary
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NPg Best View | 9.333 | 9.278 | 9.171 | 9.079 | 9.031 | 8.968 | 8.869 | 8.408 | 6.312 | 4.643 | 3.099 | Primary
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NPg Best View | 5.482 | 5.244 | 4.889 | 4.483 | 4.187 | 3.871 | 3.504 | 1.823 | -1.886 | -4.865 | -7.782 | Primary
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NPg Best View | 4.815 | 4.847 | 4.87 | 4.885 | 4.897 | 4.903 | 4.901 | 4.851 | 4.638 | 4.494 | 4.371 | Primary
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NPg Best View | 22.064 | 21.935 | 21.732 | 21.506 | 21.388 | 21.261 | 21.101 | 20.425 | 17.965 | 15.999 | 14.137 | Primary
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NPg Best View | 8.036 | 8.13 | 8.186 | 8.227 | 8.288 | 8.338 | 8.369 | 8.479 | 7.396 | 6.528 | 5.694 | Primary
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NPg Best View | 13.705 | 13.479 | 13.181 | 12.907 | 12.731 | 12.539 | 12.291 | 11.219 | 8.4 | 6.171 | 4.13 | Primary
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NPg Best View | 7.384 | 7.419 | 7.369 | 7.258 | 7.188 | 7.095 | 6.953 | 6.227 | 3.609 | 1.558 | -0.339 | Primary
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NPg Best View | 5.038 | 4.521 | 3.785 | 2.968 | 2.509 | 2.008 | 1.385 | -1.375 | -7.749 | -12.584 | -17.224 | Primary
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NPg Best View | 0.971 | 0.943 | 0.904 | 0.856 | 0.809 | 0.757 | 0.697 | 0.385 | -0.253 | -0.795 | -1.322 | Primary
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NPg Best View | 3.283 | 3.217 | 3.09 | 2.912 | 2.744 | 2.539 | 2.287 | 0.855 | -1.726 | -3.727 | -5.595 | Primary
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NPg Best View | 13.036 | 13.019 | 12.942 | 12.821 | 12.729 | 12.625 | 12.487 | 11.911 | 10.31 | 9.078 | 7.985 | Primary
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NPg Best View | 14.893 | 14.746 | 15.482 | 15.142 | 14.937 | 14.719 | 14.448 | 13.264 | 9.942 | 7.283 | 4.744 | Primary
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NPg Best View | 22.385 | 22.403 | 22.305 | 22.086 | 21.819 | 21.445 | 20.951 | 17.745 | 13.077 | 10.241 | 7.942 | Primary
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NPg Best View | 9.893 | 9.653 | 9.292 | 8.869 | 8.524 | 8.161 | 7.742 | 5.863 | 1.974 | -1.186 | -4.214 | Primary
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NPg Best View | 2.488 | 2.286 | 2.01 | 1.687 | 1.486 | 1.269 | 1.011 | -0.175 | -2.427 | -4.165 | -5.934 | Primary
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NPg Best View | 8.285 | 7.991 | 7.467 | 6.806 | 6.494 | 6.162 | 5.751 | 4.031 | -2.009 | -6.917 | -11.784 | Primary
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NPg Best View | 6.126 | 3.855 | 3.853 | 3.828 | 3.8 | 3.761 | 3.7 | 3.318 | 2.143 | 1.244 | 0.438 | Primary
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NPg Best View | 7.664 | 7.311 | 6.779 | 6.146 | 5.756 | 5.336 | 4.814 | 2.528 | -2.424 | -6.212 | -9.796 | Primary
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NPg Best View | 4.024 | 3.838 | 18.222 | 17.834 | 17.533 | 17.204 | 16.798 | 14.9 | 10.378 | 6.863 | 3.711 | Primary
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NPg Best View | -0.135 | -0.243 | -0.401 | -0.594 | -0.745 | -0.902 | -1.084 | -1.893 | -3.815 | -5.45 | -7.018 | Primary
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NPg Best View | 2.865 | 2.883 | 2.875 | 2.851 | 2.835 | 2.814 | 2.782 | 2.598 | 1.884 | 1.373 | 0.908 | Primary
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NPg Best View | 10.528 | 10.307 | 9.932 | 9.477 | 9.172 | 8.851 | 8.459 | 6.871 | 3.116 | 0.191 | -2.543 | Primary
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NPg Best View | 8.659 | 8.373 | 7.912 | 7.356 | 7.048 | 6.709 | 6.292 | 4.349 | -0.153 | -3.517 | -6.815 | Primary
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NPg Best View | 12.575 | 12.512 | 12.383 | 12.209 | 12.1 | 11.969 | 11.793 | 10.906 | 9.394 | 8.331 | 7.324 | Primary
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NPg Best View | 3.897 | 3.011 | 3.042 | 3.023 | 3.001 | 2.944 | 2.84 | 2.177 | -0.041 | -1.648 | -3.103 | Primary
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NPg Best View | 15.324 | 15.264 | 15.158 | 15.009 | 14.854 | 14.668 | 14.445 | 13.156 | 11.004 | 9.422 | 7.959 | Primary
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NPg Best View | 4.13 | 4.052 | 3.935 | 3.795 | 3.698 | 3.596 | 3.475 | 2.953 | 1.666 | 0.613 | -0.402 | Primary
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NPg Best View | 2.488 | 2.443 | 2.361 | 2.259 | 2.195 | 2.127 | 2.043 | 1.692 | 0.587 | -0.293 | -1.117 | Primary
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NPg Best View | 15.085 | 14.807 | 14.367 | 13.823 | 13.452 | 13.039 | 12.536 | 10.047 | 5.145 | 1.412 | -2.175 | Primary
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NPg Best View | 2.047 | 1.959 | 1.728 | 1.422 | 1.169 | 0.895 | 0.55 | -1.036 | -5.705 | -9.457 | -12.914 | Primary
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NPg Best View | 14.834 | 14.781 | 14.634 | 14.457 | 14.371 | 14.279 | 14.175 | 13.72 | 11.572 | 9.894 | 8.236 | Primary
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NPg Best View | 4.747 | 4.668 | 4.557 | 4.425 | 4.314 | 4.197 | 4.061 | 3.462 | 2.268 | 1.304 | 0.397 | Primary
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NPg Best View | 7.025 | 6.656 | 6.102 | 5.454 | 4.977 | 4.47 | 3.868 | 1.259 | -3.144 | -6.431 | -9.619 | Primary
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NPg Best View | 12.704 | 12.415 | 11.992 | 11.509 | 11.19 | 10.86 | 10.472 | 8.857 | 5.552 | 2.961 | 0.385 | Primary
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NPg Best View | 12.946 | 11.314 | 11.207 | 11.017 | 10.829 | 10.559 | 10.199 | 7.909 | 4.889 | 3.226 | 1.87 | Primary
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NPg Best View | 3.076 | 2.877 | 2.644 | 2.468 | 2.33 | 2.184 | 2.007 | 1.338 | 0.461 | -0.103 | -0.598 | Primary
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NPg Best View | 8.135 | 7.546 | 6.731 | 5.804 | 5.192 | 4.554 | 3.819 | 0.675 | -4.946 | -9.161 | -13.29 | Primary
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NPg Best View | 8.588 | 8.604 | 8.605 | 8.596 | 8.586 | 8.566 | 8.533 | 8.355 | 8.15 | 7.963 | 7.776 | Primary
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NPg Best View | 2.019 | 1.825 | 1.516 | 1.094 | 0.619 | 0.023 | -0.716 | -5.119 | -9.342 | -11.586 | -13.261 | Primary
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NPg Best View | 11.952 | 11.665 | 11.272 | 10.879 | 10.639 | 10.375 | 10.051 | 8.564 | 4.395 | 1.095 | -2.03 | Primary
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NPg Best View | 9.409 | 9.082 | 8.56 | 7.919 | 7.519 | 7.076 | 6.536 | 3.981 | -0.843 | -4.379 | -7.787 | Primary
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NPg Best View | 0.928 | 0.841 | 0.701 | 0.516 | 0.329 | 0.099 | -0.186 | -1.819 | -3.46 | -4.42 | -5.223 | Primary
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NPg Best View | 7.544 | 7.283 | 6.858 | 6.342 | 5.991 | 5.624 | 5.184 | 3.35 | -1.614 | -5.668 | -9.548 | Primary
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NPg Best View | 0.977 | 0.988 | 0.922 | 0.812 | 0.774 | 0.719 | 0.635 | 0.207 | -1.974 | -3.644 | -5.22 | Primary
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NPg Best View | 1.491 | 1.492 | 1.493 | 1.493 | 1.493 | 1.492 | 1.491 | 1.483 | 1.467 | 1.452 | 1.437 | Primary
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 10.537 | 10.606 | 10.612 | 10.588 | 10.596 | 10.598 | 10.584 | 10.584 | 9.067 | 7.844 | 6.651 | Primary
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 7.15 | 7.13 | 7.077 | 7.007 | 6.968 | 6.926 | 6.87 | 6.625 | 5.754 | 5.081 | 4.423 | Primary
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 8.545 | 8.489 | 8.402 | 8.293 | 8.205 | 8.112 | 7.998 | 7.526 | 6.776 | 6.207 | 5.686 | Primary
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 3.99 | 3.825 | 3.581 | 3.299 | 3.103 | 2.879 | 2.606 | 1.237 | -1.059 | -2.722 | -4.297 | Primary
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NPg Best View | 14.635 | 14.408 | 14.085 | 14.693 | 14.347 | 13.99 | 13.582 | 11.866 | 8.737 | 6.327 | 4.156 | Primary
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NPg Best View | 10.174 | 9.151 | 8.81 | 8.387 | 8.148 | 7.894 | 7.585 | 6.275 | 2.751 | -0.054 | -2.838 | Primary
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NPg Best View | 3.303 | 3.151 | 2.934 | 2.67 | 2.401 | 2.093 | 1.725 | -0.218 | -2.841 | -4.741 | -6.437 | Primary
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NPg Best View | 11.084 | 10.553 | 9.955 | 9.545 | 9.313 | 9.062 | 8.75 | 7.445 | 3.513 | 0.408 | -2.564 | Primary
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NPg Best View | 10.843 | 10.825 | 10.774 | 10.702 | 10.655 | 10.601 | 10.535 | 10.179 | 8.772 | 7.48 | 6.188 | Primary
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NPg Best View | -2.757 | -3.3 | -4.083 | -5.014 | -5.665 | -6.357 | -7.176 | -10.804 | -18.27 | -24.178 | -29.813 | Primary
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NPg Best View | 7.314 | 6.794 | 6.103 | 5.397 | 4.989 | 4.557 | 4.036 | 1.94 | -2.31 | -5.38 | -8.327 | Primary
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NPg Best View | 5.35 | 5.407 | 5.354 | 5.235 | 5.288 | 5.324 | 5.328 | 5.212 | 2.375 | -0.01 | -2.496 | Primary
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NPg Best View | 17.308 | 14.297 | 14.136 | 13.943 | 13.794 | 13.641 | 13.47 | 12.687 | 10.701 | 8.962 | 7.227 | Primary
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NPg Best View | 13.938 | 13.926 | 13.88 | 13.805 | 13.718 | 13.609 | 13.47 | 12.659 | 11.314 | 10.325 | 9.414 | Primary
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NPg Best View | 9.699 | 9.532 | 9.298 | 8.994 | 8.66 | 8.256 | 7.772 | 4.939 | 1.57 | -0.786 | -2.894 | Primary
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NPg Best View | 12.786 | 12.801 | 12.744 | 12.654 | 12.623 | 12.589 | 12.542 | 12.374 | 10.425 | 8.824 | 7.24 | Primary
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NPg Best View | 11.581 | 11.658 | 11.687 | 11.691 | 11.722 | 11.745 | 11.75 | 11.79 | 11.056 | 10.499 | 9.946 | Primary
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 4.263 | 4.126 | 3.94 | 3.697 | 3.415 | 3.07 | 2.656 | 0.177 | -2.487 | -4.313 | -5.923 | Primary
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NPg Best View | 16.368 | 16.319 | 16.217 | 16.084 | 16.012 | 15.926 | 15.821 | 15.223 | 13.557 | 12.248 | 10.975 | Primary
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NPg Best View | 10.886 | 10.651 | 10.26 | 9.782 | 9.547 | 9.294 | 8.984 | 7.649 | 3.72 | 0.686 | -2.322 | Primary
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NPg Best View | 10.322 | 10.237 | 10.021 | 9.753 | 9.615 | 9.465 | 9.289 | 8.454 | 5.285 | 2.844 | 0.464 | Primary
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NPg Best View | 7.182 | 6.895 | 6.416 | 5.82 | 5.433 | 5.003 | 4.467 | 1.952 | -2.722 | -6.055 | -9.163 | Primary
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NPg Best View | 4.655 | 4.354 | 3.904 | 3.374 | 2.98 | 2.535 | 2 | -0.622 | -5.08 | -8.291 | -11.266 | Primary
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NPg Best View | 11.821 | 11.848 | 11.826 | 11.765 | 11.679 | 11.543 | 11.342 | 10.052 | 8.914 | 8.445 | 8.153 | Primary
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NPg Best View | 15.473 | 15.201 | 14.769 | 14.24 | 13.983 | 13.716 | 13.395 | 12.065 | 8.166 | 5.077 | 1.971 | Primary
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NPg Best View | 9.369 | 8.978 | 8.378 | 7.636 | 7.059 | 6.4 | 5.598 | 1.487 | -4.47 | -8.599 | -12.406 | Primary
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NPg Best View | 3.328 | 3.234 | 3.099 | 3.441 | 3.32 | 3.193 | 3.044 | 2.37 | 1.134 | 0.147 | -0.799 | Primary
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NPg Best View | 8.188 | 8.066 | 7.824 | 7.513 | 7.289 | 7.047 | 6.735 | 5.446 | 1.146 | -2.383 | -5.587 | Primary
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NPg Best View | 4.186 | 4.018 | 3.761 | 3.463 | 3.303 | 3.135 | 2.932 | 2.111 | 0.084 | -1.5 | -3.092 | Primary
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 12.359 | 12.378 | 12.36 | 12.322 | 12.301 | 12.27 | 12.223 | 11.962 | 10.936 | 10.073 | 9.212 | Primary
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 25.344 | 25.32 | 25.266 | 25.194 | 25.144 | 25.09 | 25.028 | 24.73 | 23.539 | 22.538 | 21.556 | Primary
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NPg Best View | 14.658 | 14.529 | 14.348 | 14.131 | 13.93 | 13.709 | 13.447 | 12.218 | 10.751 | 9.771 | 8.94 | Primary
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NPg Best View | 12.755 | 12.841 | 12.896 | 12.927 | 12.964 | 12.994 | 13.009 | 13.052 | 12.087 | 11.314 | 10.593 | Primary
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NPg Best View | 19.862 | 19.859 | 19.842 | 19.815 | 19.796 | 19.775 | 19.749 | 19.614 | 18.922 | 18.294 | 17.663 | Primary
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NPg Best View | 6.878 | 6.668 | 6.321 | 5.897 | 5.663 | 5.414 | 5.109 | 3.857 | 0.9 | -1.294 | -3.455 | Primary
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 22.521 | 22.56 | 22.491 | 22.385 | 22.319 | 22.243 | 22.141 | 21.731 | 19.483 | 17.719 | 16.011 | Primary
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NPg Best View | 14.626 | 14.589 | 14.485 | 14.348 | 14.324 | 14.296 | 14.256 | 14.035 | 11.69 | 9.763 | 7.875 | Primary
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NPg Best View | 4.759 | 4.69 | 4.576 | 4.439 | 4.363 | 4.282 | 4.18 | 3.724 | 2.65 | 1.835 | 1.035 | Primary
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NPg Best View | 4.52 | 4.495 | 4.452 | 4.4 | 4.345 | 4.284 | 4.209 | 3.838 | 3.52 | 3.312 | 3.132 | Primary
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NPg Best View | 15.749 | 15.712 | 15.607 | 15.456 | 15.336 | 15.192 | 15.015 | 14.046 | 11.596 | 9.679 | 7.845 | Primary
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NPg Best View | 9.716 | 9.615 | 9.451 | 9.246 | 9.104 | 8.95 | 8.758 | 7.909 | 5.919 | 4.366 | 2.968 | Primary
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NPg Best View | 11.566 | 11.493 | 11.37 | 11.218 | 11.131 | 11.039 | 10.926 | 10.442 | 8.845 | 7.555 | 6.345 | Primary
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NPg Best View | 2.373 | 2.259 | 2.103 | 1.931 | 1.767 | 1.595 | 1.395 | 0.512 | -1.095 | -2.449 | -3.697 | Primary
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NPg Best View | 3.519 | 3.352 | 3.086 | 2.756 | 2.549 | 2.313 | 2.036 | 0.486 | -3.511 | -6.718 | -9.904 | Primary
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NPg Best View | 18.951 | 18.941 | 18.911 | 18.865 | 18.824 | 18.767 | 18.694 | 18.242 | 17.636 | 17.257 | 16.923 | Primary
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NPg Best View | 4.87 | 4.808 | 4.708 | 4.591 | 4.511 | 4.429 | 4.329 | 3.909 | 2.668 | 1.653 | 0.708 | Primary
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NPg Best View | 14.853 | 14.864 | 14.854 | 14.835 | 14.827 | 14.808 | 14.772 | 14.506 | 13.481 | 12.679 | 11.945 | Primary
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NPg Best View | 12.716 | 12.838 | 12.938 | 13.017 | 13.096 | 13.159 | 13.204 | 13.328 | 13.033 | 12.856 | 12.696 | Primary
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NPg Best View | 2.315 | 2.068 | 1.718 | 1.289 | 0.977 | 0.637 | 0.224 | -1.688 | -4.322 | -6.157 | -7.846 | Primary
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NPg Best View | 5.923 | 5.904 | 5.848 | 5.778 | 5.724 | 5.667 | 5.602 | 5.294 | 4.292 | 3.501 | 2.73 | Primary
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NPg Best View | 5.291 | 5.262 | 5.19 | 5.096 | 5.019 | 4.923 | 4.804 | 4.142 | 3.052 | 2.306 | 1.61 | Primary
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NPg Best View | 5.32 | 5.046 | 4.646 | 4.172 | 3.817 | 3.437 | 2.986 | 0.884 | -3.03 | -6.075 | -8.956 | Primary
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NPg Best View | 15.359 | 15.3 | 15.191 | 15.054 | 14.964 | 14.869 | 14.76 | 14.22 | 12.439 | 10.986 | 9.58 | Primary
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NPg Best View | 8.468 | 8.063 | 7.523 | 6.977 | 6.569 | 6.133 | 5.594 | 3.296 | -1.716 | -5.69 | -9.321 | Primary
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NPg Best View | 4.973 | 4.958 | 4.852 | 4.722 | 4.608 | 4.47 | 4.295 | 3.377 | 0.237 | -2.192 | -4.431 | Primary
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NPg Best View | 10.498 | 10.272 | 9.872 | 9.359 | 9.056 | 8.735 | 8.346 | 6.67 | 1.127 | -3.466 | -7.883 | Primary
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NPg Best View | 0.294 | 0.24 | 0.15 | 0.031 | -0.05 | -0.144 | -0.253 | -0.857 | -2.375 | -3.609 | -4.805 | Primary
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NPg Best View | 13.544 | 13.311 | 12.943 | 12.515 | 12.222 | 11.907 | 11.52 | 9.826 | 6.173 | 3.382 | 0.758 | Primary
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NPg Best View | 18.454 | 18.461 | 18.448 | 18.421 | 18.396 | 18.365 | 18.326 | 18.116 | 17.263 | 16.602 | 15.999 | Primary
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NPg Best View | 12.653 | 12.461 | 12.18 | 11.862 | 11.698 | 11.524 | 11.332 | 10.41 | 7.684 | 5.397 | 2.994 | Primary
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NPg Best View | 7.199 | 7.11 | 6.957 | 6.764 | 6.594 | 6.409 | 6.191 | 5.09 | 2.373 | 0.145 | -1.921 | Primary
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NPg Best View | 8.315 | 8.219 | 8.016 | 7.73 | 7.511 | 7.235 | 6.89 | 4.783 | 0.486 | -2.774 | -5.812 | Primary
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NPg Best View | 16.398 | 16.405 | 16.406 | 16.404 | 16.396 | 16.383 | 16.363 | 16.235 | 16.061 | 15.873 | 15.684 | Primary
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NPg Best View | 17.021 | 16.971 | 16.866 | 16.722 | 16.607 | 16.482 | 16.322 | 15.616 | 13.879 | 12.527 | 11.29 | Primary
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NPg Best View | 19.011 | 18.983 | 18.932 | 18.867 | 18.822 | 18.775 | 18.721 | 18.485 | 17.537 | 16.726 | 15.953 | Primary
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NPg Best View | 9.355 | 8.939 | 8.414 | 7.96 | 7.721 | 7.465 | 7.151 | 5.875 | 2.12 | -0.786 | -3.643 | Primary
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NPg Best View | 10.639 | 10.31 | 9.838 | 9.323 | 9.023 | 8.701 | 8.299 | 6.522 | 2.331 | -0.908 | -4.013 | Primary
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NPg Best View | -6.381 | -6.22 | -6.095 | -5.995 | -5.908 | -5.842 | -5.805 | -5.728 | -6.108 | -6.312 | -6.473 | Primary
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NPg Best View | 10.452 | 9.946 | 9.322 | 8.79 | 8.439 | 8.07 | 7.624 | 5.76 | 0.528 | -3.694 | -7.667 | Primary
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NPg Best View | 11.458 | 11.373 | 11.204 | 10.977 | 10.798 | 10.586 | 10.329 | 8.857 | 5.625 | 3.174 | 0.85 | Primary
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NPg Best View | 5.286 | 5.035 | 4.671 | 4.247 | 3.94 | 3.626 | 3.265 | 1.756 | -1.602 | -4.336 | -6.996 | Primary
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NPg Best View | 24.545 | 24.56 | 24.486 | 24.363 | 24.327 | 24.285 | 24.224 | 23.926 | 21.214 | 19.024 | 16.91 | Primary
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NPg Best View | 6.616 | 6.496 | 6.294 | 6.04 | 5.849 | 5.632 | 5.368 | 4.075 | 1.68 | -0.198 | -2.023 | Primary
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NPg Best View | 6.771 | 6.766 | 6.752 | 6.734 | 6.725 | 6.715 | 6.701 | 6.641 | 6.473 | 6.346 | 6.226 | Primary
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NPg Best View | 11.781 | 11.293 | 10.548 | 9.656 | 9.148 | 8.611 | 7.975 | 5.207 | -1.253 | -6.322 | -11.407 | Primary
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NPg Best View | 22.024 | 22.052 | 22.035 | 21.966 | 21.85 | 21.669 | 21.42 | 19.719 | 18.398 | 17.949 | 17.743 | Primary
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NPg Best View | 11.36 | 11.18 | 10.861 | 10.476 | 10.252 | 10.012 | 9.718 | 8.446 | 4.877 | 2.139 | -0.5 | Primary
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NPg Best View | 12.122 | 12.005 | 11.783 | 11.473 | 11.075 | 10.575 | 9.96 | 6.252 | 1.894 | -0.767 | -2.893 | Primary
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NPg Best View | 0.812 | 0.753 | 0.65 | 0.515 | 0.391 | 0.249 | 0.073 | -0.842 | -2.386 | -3.564 | -4.658 | Primary
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NPg Best View | 7.15 | 1.462 | 1.177 | 0.837 | 0.592 | 0.33 | 0.018 | -1.358 | -3.784 | -5.6 | -7.318 | Primary
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NPg Best View | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NPg Best View | 5.149 | 4.942 | 4.638 | 4.279 | 4.042 | 3.791 | 3.493 | 2.157 | -0.594 | -2.816 | -5.036 | Primary
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NPg Best View | 12.975 | 12.801 | 12.5 | 12.105 | 11.697 | 11.18 | 10.53 | 6.674 | 2.35 | -0.042 | -1.929 | Primary
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NPg Best View | 2.43 | 2.265 | 1.968 | 1.631 | 1.431 | 1.203 | 0.912 | -0.399 | -3.286 | -5.326 | -7.27 | Primary
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NPg Best View | 2.36 | 2.216 | 2.026 | 1.858 | 1.767 | 1.669 | 1.545 | 1.078 | -0.005 | -0.796 | -1.587 | Primary
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NPg Best View | 13.041 | 12.933 | 12.717 | 12.441 | 12.315 | 12.176 | 11.997 | 11.172 | 8.54 | 6.513 | 4.542 | Primary
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NPg Best View | 8.012 | 8.111 | 8.181 | 8.235 | 8.285 | 8.325 | 8.347 | 8.425 | 7.25 | 6.326 | 5.491 | Primary
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NPg Best View | 13.619 | 13.576 | 13.454 | 13.283 | 13.228 | 13.164 | 13.079 | 12.619 | 10.27 | 8.417 | 6.585 | Primary
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NPg Best View | 7.295 | 7.006 | 6.592 | 6.095 | 5.703 | 5.28 | 4.769 | 2.378 | -1.477 | -4.516 | -7.389 | Primary
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NPg Best View | 12.827 | 12.806 | 12.706 | 12.54 | 12.404 | 12.206 | 11.938 | 10.156 | 7.852 | 6.544 | 5.436 | Primary
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NPg Best View | 13.811 | 13.87 | 13.921 | 13.962 | 14.002 | 14.037 | 14.066 | 14.18 | 14.033 | 13.918 | 13.81 | Primary
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NPg Best View | 5.932 | 5.925 | 5.905 | 5.88 | 5.872 | 5.861 | 5.842 | 5.755 | 5.54 | 5.38 | 5.208 | Primary
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NPg Best View | 14.239 | 14.294 | 14.318 | 14.319 | 14.325 | 14.327 | 14.319 | 14.282 | 13.19 | 12.337 | 11.562 | Primary
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NPg Best View | -3.98 | -4.222 | -4.621 | -5.112 | -5.385 | -5.674 | -6.022 | -7.514 | -11.147 | -13.892 | -16.563 | Primary
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NPg Best View | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NPg Best View | 9.064 | 8.04 | 7.494 | 6.848 | 6.427 | 5.988 | 5.473 | 3.297 | -2.329 | -6.878 | -11.214 | Primary
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NPg Best View | 9.131 | 8.651 | 7.957 | 7.187 | 12.787 | 12.362 | 11.84 | 9.599 | 4.247 | 0.138 | -3.965 | Primary
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NPg Best View | 4.119 | 4.242 | 4.324 | 4.376 | 4.406 | 4.423 | 4.418 | 4.346 | 2.686 | 1.305 | 0.063 | Primary
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NPg Best View | 2.366 | 2.122 | 1.763 | 1.334 | 0.903 | 0.459 | -0.056 | -2.172 | -6.861 | -10.827 | -14.402 | Primary
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NPg Best View | 14.475 | 14.345 | 14.127 | 13.869 | 13.692 | 13.503 | 13.27 | 12.28 | 9.269 | 6.821 | 4.54 | Primary
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NPg Best View | 5.721 | 5.294 | 4.618 | 3.793 | 3.299 | 2.766 | 2.124 | -0.772 | -6.567 | -10.932 | -15.31 | Primary
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NPg Best View | 5.304 | 4.385 | 4.082 | 3.758 | 3.533 | 3.277 | 2.951 | 1.468 | -2.06 | -4.716 | -7.203 | Primary
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NPg Best View | 15.155 | 15.029 | 14.823 | 14.583 | 14.466 | 14.341 | 14.184 | 13.525 | 11.484 | 9.856 | 8.229 | Primary
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NPg Best View | 4.258 | 4.023 | 3.636 | 3.167 | 2.895 | 2.593 | 2.218 | 0.438 | -3.485 | -6.407 | -9.24 | Primary
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NPg Best View | 7.94 | 7.737 | 7.412 | 7.021 | 6.716 | 6.381 | 5.997 | 4.059 | 0.255 | -2.636 | -5.447 | Primary
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NPg Best View | 9.036 | 8.678 | 8.131 | 7.477 | 7.087 | 6.674 | 6.182 | 4.103 | -0.069 | -3.076 | -6.048 | Primary
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NPg Best View | 6.912 | 6.643 | 6.266 | 5.825 | 5.475 | 5.108 | 4.676 | 2.867 | 0.068 | -1.99 | -3.842 | Primary
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NPg Best View | 2.732 | 2.213 | 1.555 | 0.951 | 0.536 | 0.088 | -0.474 | -2.93 | -9.41 | -14.582 | -19.23 | Primary
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NPg Best View | 9.873 | 9.452 | 8.859 | 8.247 | 7.94 | 7.616 | 7.22 | 5.57 | 0.862 | -2.811 | -6.443 | Primary
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NPg Best View | 10.839 | 10.448 | 9.902 | 9.333 | 8.929 | 8.471 | 7.901 | 5.119 | 0.396 | -2.927 | -5.978 | Primary
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NPg Best View | 13.452 | 13.474 | 13.431 | 13.331 | 13.237 | 13.101 | 12.915 | 11.71 | 9.592 | 8.286 | 7.189 | Primary
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NPg Best View | 8.851 | 8.76 | 8.598 | 8.406 | 8.269 | 8.124 | 7.949 | 7.178 | 5.057 | 3.374 | 1.803 | Primary
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NPg Best View | 3.595 | 3.551 | 3.421 | 3.25 | 3.116 | 2.952 | 2.747 | 1.61 | -0.22 | -1.357 | -2.399 | Primary
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NPg Best View | 12.966 | 12.79 | 12.493 | 12.132 | 11.921 | 11.7 | 11.43 | 10.312 | 7.2 | 4.752 | 2.397 | Primary
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NPg Best View | 17.652 | 17.589 | 17.459 | 17.283 | 17.156 | 17.018 | 16.842 | 16.086 | 14.292 | 12.866 | 11.548 | Primary
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NPg Best View | 15.479 | 15.397 | 15.245 | 15.056 | 14.964 | 14.869 | 14.76 | 14.252 | 12.101 | 10.329 | 8.527 | Primary
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NPg Best View | 4.175 | 4.019 | 3.76 | 3.41 | 3.058 | 2.618 | 2.078 | -1.19 | -5.309 | -7.908 | -10.156 | Primary
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NPg Best View | 10.21 | 10.289 | 10.321 | 10.318 | 10.324 | 10.314 | 10.281 | 10.044 | 8.562 | 7.47 | 6.477 | Primary
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NPg Best View | -1.162 | -1.235 | -1.365 | -1.532 | -1.647 | -1.784 | -1.953 | -2.921 | -4.895 | -6.369 | -7.765 | Primary
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NPg Best View | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NPg Best View | 6.951 | 6.542 | 5.973 | 5.368 | 5.01 | 4.615 | 4.128 | 1.893 | -2.344 | -5.426 | -8.49 | Primary
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NPg Best View | 14.402 | 14.127 | 13.703 | 13.187 | 12.926 | 12.648 | 12.314 | 10.847 | 7.014 | 3.99 | 0.953 | Primary
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NPg Best View | 3.504 | 3.389 | 3.224 | 3.03 | 2.901 | 2.767 | 2.609 | 1.909 | 0.347 | -0.935 | -2.206 | Primary
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NPg Best View | 8.857 | 8.555 | 8.079 | 7.441 | 6.8 | 5.996 | 5.013 | -0.96 | -7.866 | -12.042 | -15.651 | Primary
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NPg Best View | 13.237 | 12.845 | 12.338 | 11.851 | 11.537 | 11.207 | 10.811 | 9.098 | 5.183 | 2.164 | -0.733 | Primary
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NPg Best View | 5.085 | 5.011 | 4.902 | 4.776 | 4.68 | 4.582 | 4.468 | 3.988 | 2.854 | 1.914 | 1.029 | Primary
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NPg Best View | 6.862 | 6.516 | 5.999 | 5.379 | 4.976 | 4.554 | 4.058 | 1.926 | -3.504 | -7.94 | -12.32 | Primary
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NPg Best View | 10.267 | 10.061 | 9.706 | 9.261 | 9 | 8.721 | 8.379 | 6.926 | 2.52 | -0.989 | -4.288 | Primary
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NPg Best View | 15.023 | 14.78 | 14.459 | 14.127 | 13.916 | 13.691 | 13.411 | 12.28 | 9.349 | 7 | 4.822 | Primary
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NPg Best View | 6.499 | 6.351 | 6.046 | 5.656 | 5.439 | 5.202 | 4.913 | 3.65 | -0.078 | -2.916 | -5.678 | Primary
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NPg Best View | 14.137 | 13.84 | 13.428 | 12.946 | 12.48 | 11.977 | 11.383 | 8.592 | 4.165 | 0.729 | -2.391 | Primary
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NPg Best View | 13.149 | 13.123 | 13.051 | 12.958 | 12.907 | 12.853 | 12.791 | 12.516 | 11.147 | 10.027 | 8.921 | Primary
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NPg Best View | 9.366 | 9.084 | 8.659 | 8.169 | 7.845 | 7.482 | 7.043 | 4.987 | 1.695 | -0.607 | -2.861 | Primary
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NPg Best View | 12.483 | 12.52 | 12.491 | 12.418 | 12.338 | 12.221 | 12.061 | 11.086 | 9.55 | 8.642 | 7.874 | Primary
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NPg Best View | 7.004 | 6.979 | 6.841 | 6.63 | 6.486 | 6.295 | 6.043 | 4.54 | 1.651 | -0.241 | -1.99 | Primary
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NPg Best View | 25.712 | 25.645 | 25.498 | 25.299 | 25.117 | 24.896 | 24.62 | 23.101 | 20.993 | 19.579 | 18.293 | Primary
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NPg Best View | 4.647 | 4.499 | 4.293 | 4.043 | 3.85 | 3.638 | 3.395 | 2.029 | -1.448 | -4.528 | -7.523 | Primary
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NPg Best View | 1.917 | 1.903 | 1.866 | 1.818 | 1.779 | 1.735 | 1.677 | 1.427 | 1.029 | 0.707 | 0.389 | Primary
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NPg Best View | 12.58 | 12.342 | 12.001 | 11.61 | 11.354 | 11.084 | 10.763 | 9.309 | 5.901 | 3.183 | 0.513 | Primary
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NPg Best View | 10.245 | 10.273 | 10.256 | 10.204 | 10.195 | 10.172 | 10.125 | 9.795 | 8.352 | 7.256 | 6.21 | Primary
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NPg Best View | 10.347 | 10.314 | 10.171 | 9.962 | 9.838 | 9.705 | 9.546 | 8.761 | 3.943 | -0.153 | -4.02 | Primary
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NPg Best View | 0.762 | 0.717 | 0.635 | 0.526 | 0.428 | 0.312 | 0.174 | -0.59 | -1.979 | -3.021 | -4.012 | Primary
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NPg Best View | 9.52 | 9.555 | 9.499 | 9.335 | 9.076 | 8.697 | 8.19 | 4.837 | 1.07 | -0.882 | -2.267 | Primary
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NPg Best View | 16.516 | 16.504 | 16.46 | 16.407 | 16.38 | 16.339 | 16.274 | 15.921 | 14.924 | 14.208 | 13.542 | Primary
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NPg Best View | 9.078 | 7.997 | 7.545 | 7.004 | 6.609 | 6.193 | 5.706 | 3.498 | -1.593 | -5.749 | -9.74 | Primary
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NPg Best View | 12.307 | 12.249 | 12.111 | 11.93 | 11.822 | 11.703 | 11.545 | 10.911 | 8.903 | 7.3 | 5.82 | Primary
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NPg Best View | 18.236 | 18.321 | 18.289 | 18.137 | 17.881 | 17.481 | 16.92 | 13.174 | 9.961 | 8.707 | 8.015 | Primary
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NPg Best View | 10.343 | 10.063 | 9.582 | 8.987 | 8.701 | 8.381 | 7.976 | 6.102 | 1.019 | -2.851 | -6.649 | Primary
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NPg Best View | 4.331 | 4.288 | 4.219 | 4.134 | 4.079 | 4.019 | 3.945 | 3.611 | 2.93 | 2.386 | 1.851 | Primary
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NPg Best View | 9.586 | 9.327 | 8.935 | 8.517 | 8.308 | 8.084 | 7.808 | 6.574 | 2.828 | -0.039 | -2.787 | Primary
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 15.33 | 15.229 | 15.003 | 14.728 | 14.496 | 14.248 | 13.963 | 12.613 | 9.178 | 6.401 | 3.691 | Primary
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 13.798 | 13.736 | 13.56 | 13.31 | 13.108 | 12.877 | 12.604 | 11.17 | 6.783 | 3.148 | -0.385 | Primary
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NPg Best View | 13.431 | 13.464 | 13.447 | 13.405 | 13.364 | 13.312 | 13.239 | 12.855 | 11.516 | 10.583 | 9.757 | Primary
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NPg Best View | 8.21 | 8.273 | 8.276 | 8.251 | 8.275 | 8.294 | 8.301 | 8.357 | 7.082 | 6.018 | 4.953 | Primary
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NPg Best View | 17.608 | 17.499 | 17.322 | 17.105 | 16.976 | 16.837 | 16.67 | 15.954 | 14.528 | 13.507 | 12.503 | Primary
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NPg Best View | 5.941 | 5.988 | 6.011 | 6.009 | 5.987 | 5.941 | 5.863 | 5.329 | 4.528 | 3.888 | 3.296 | Primary
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NPg Best View | 2.383 | 2.008 | 1.484 | 0.949 | 0.658 | 0.349 | -0.03 | -1.632 | -6.148 | -9.664 | -13.046 | Primary
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NPg Best View | 12.875 | 12.599 | 12.212 | 11.808 | 11.545 | 11.27 | 10.94 | 9.58 | 5.997 | 3.182 | 0.548 | Primary
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NPg Best View | 10.209 | 9.807 | 9.203 | 8.527 | 8.128 | 7.674 | 7.107 | 4.33 | -1.065 | -4.844 | -8.386 | Primary
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 11.662 | 11.696 | 11.66 | 11.581 | 11.466 | 11.307 | 11.097 | 9.82 | 8.211 | 7.376 | 6.75 | Primary
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NPg Best View | 16.117 | 15.95 | 15.679 | 15.341 | 15.177 | 15.001 | 14.779 | 13.81 | 11.316 | 9.398 | 7.522 | Primary
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NPg Best View | 12.95 | 12.889 | 12.739 | 12.538 | 12.371 | 12.194 | 11.973 | 11.006 | 8.086 | 5.764 | 3.693 | Primary
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NPg Best View | 9.514 | 9.319 | 8.97 | 8.532 | 8.256 | 7.939 | 7.538 | 5.575 | 1.801 | -0.848 | -3.348 | Primary
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NPg Best View | 11.609 | 9.906 | 9.751 | 9.537 | 9.429 | 9.312 | 9.158 | 8.536 | 6.086 | 4.09 | 2.147 | Primary
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NPg Best View | 5.239 | 5.171 | 5.073 | 4.963 | 4.875 | 4.784 | 4.673 | 4.2 | 3.322 | 2.64 | 1.999 | Primary
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NPg Best View | 14.435 | 14.086 | 13.579 | 12.988 | 12.629 | 12.246 | 11.776 | 9.678 | 5.361 | 2.022 | -1.246 | Primary
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NPg Best View | 3.279 | 3.043 | 2.613 | 2.082 | 1.716 | 1.327 | 0.844 | -1.159 | -6.858 | -11.416 | -15.624 | Primary
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NPg Best View | 14.971 | 14.766 | 14.447 | 14.08 | 13.864 | 13.627 | 13.33 | 12.019 | 9.202 | 7.074 | 5.001 | Primary
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NPg Best View | 7.26 | 6.901 | 6.344 | 5.702 | 5.347 | 4.971 | 4.514 | 2.578 | -2.753 | -6.939 | -11.087 | Primary
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NPg Best View | 19.442 | 19.543 | 19.54 | 19.473 | 19.429 | 19.365 | 19.26 | 18.659 | 15.245 | 12.506 | 9.955 | Primary
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NPg Best View | 12.558 | 12.438 | 12.234 | 12.014 | 11.804 | 11.585 | 11.334 | 10.323 | 8.578 | 7.378 | 6.341 | Primary
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NPg Best View | 4.661 | 4.407 | 3.994 | 3.5 | 3.146 | 2.767 | 2.316 | 0.253 | -3.854 | -7.036 | -10.116 | Primary
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NPg Best View | 9.06 | 8.521 | 7.809 | 6.99 | 6.189 | 5.337 | 4.332 | -0.155 | -6.928 | -12.226 | -16.872 | Primary
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NPg Best View | 4.751 | 4.518 | 4.162 | 3.774 | 3.494 | 3.191 | 2.817 | 1.183 | -3.573 | -7.448 | -11.031 | Primary
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NPg Best View | 13.05 | 12.635 | 12.052 | 11.385 | 10.979 | 10.562 | 10.078 | 8.077 | 3.848 | 0.5 | -2.871 | Primary
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NPg Best View | 20.91 | 17.831 | 17.874 | 17.909 | 17.94 | 17.968 | 17.992 | 18.097 | 17.868 | 17.683 | 17.521 | Primary
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NPg Best View | 3.581 | 3.399 | 3.105 | 2.721 | 2.351 | 1.885 | 1.312 | -2.128 | -6.303 | -8.957 | -11.332 | Primary
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NPg Best View | 13.928 | 13.85 | 13.682 | 13.471 | 13.422 | 13.366 | 13.291 | 12.872 | 10.091 | 7.792 | 5.453 | Primary
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NPg Best View | 14.349 | 14.43 | 14.486 | 14.529 | 14.588 | 14.641 | 14.683 | 14.864 | 14.599 | 14.392 | 14.165 | Primary
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NPg Best View | 15.728 | 15.784 | 15.813 | 15.823 | 15.847 | 15.866 | 15.875 | 15.899 | 15.185 | 14.616 | 14.067 | Primary
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NPg Best View | 9.762 | 9.303 | 8.623 | 7.819 | 7.322 | 6.796 | 6.171 | 3.506 | -1.755 | -5.767 | -9.718 | Primary
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NPg Best View | 14.799 | 14.722 | 14.579 | 14.393 | 14.299 | 14.193 | 14.067 | 13.348 | 10.697 | 8.478 | 6.284 | Primary
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NPg Best View | 6.07 | 6.031 | 5.889 | 5.695 | 5.604 | 5.506 | 5.386 | 4.818 | 1.519 | -1.146 | -3.721 | Primary
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NPg Best View | 14.075 | 13.942 | 13.71 | 13.422 | 13.225 | 13.012 | 12.75 | 11.591 | 9.096 | 7.263 | 5.553 | Primary
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NPg Best View | 17.575 | 14.035 | 14.001 | 13.962 | 13.931 | 13.893 | 13.839 | 13.651 | 13.321 | 13.124 | 12.949 | Primary
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NPg Best View | 11.027 | 10.817 | 10.512 | 10.167 | 9.953 | 9.722 | 9.445 | 8.183 | 5.738 | 3.885 | 2.043 | Primary
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NPg Best View | 2.735 | 2.555 | 2.286 | 1.957 | 1.707 | 1.417 | 1.068 | -0.778 | -3.284 | -4.924 | -6.421 | Primary
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NPg Best View | 11.292 | 11.004 | 10.585 | 10.121 | 9.892 | 9.645 | 9.336 | 8.084 | 5.203 | 3.018 | 0.751 | Primary
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NPg Best View | 12.677 | 12.515 | 12.236 | 11.899 | 11.714 | 11.513 | 11.264 | 10.174 | 7.406 | 5.309 | 3.258 | Primary
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NPg Best View | 5.688 | 5.565 | 5.337 | 5.015 | 4.687 | 4.283 | 3.788 | 0.836 | -4.029 | -7.591 | -10.782 | Primary
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NPg Best View | 16.57 | 16.456 | 16.289 | 16.088 | 15.927 | 15.756 | 15.555 | 14.613 | 12.798 | 11.328 | 9.941 | Primary
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NPg Best View | 11.742 | 9.987 | 9.656 | 9.239 | 8.906 | 8.518 | 8.063 | 5.408 | 0.351 | -3.44 | -6.935 | Primary
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NPg Best View | 4.73 | 4.632 | 4.494 | 4.335 | 4.214 | 4.09 | 3.945 | 3.317 | 2.232 | 1.375 | 0.547 | Primary
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NPg Best View | 14.885 | 14.659 | 14.302 | 13.871 | 13.604 | 13.319 | 12.971 | 11.5 | 8.634 | 6.559 | 4.583 | Primary
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NPg Best View | 0.092 | -0.045 | -0.251 | -0.501 | -0.704 | -0.925 | -1.189 | -2.461 | -5.029 | -7.035 | -8.897 | Primary
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NPg Best View | 9.44 | 9.176 | 8.767 | 8.277 | 7.931 | 7.559 | 7.116 | 5.136 | 0.637 | -2.974 | -6.467 | Primary
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NPg Best View | 8.539 | 8.313 | 7.918 | 7.428 | 7.139 | 6.823 | 6.429 | 4.634 | 0.346 | -2.89 | -6.001 | Primary
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NPg Best View | 5.686 | 5.335 | 4.803 | 4.155 | 3.723 | 3.262 | 2.715 | 0.225 | -5.797 | -10.676 | -15.498 | Primary
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NPg Best View | 16.148 | 15.92 | 15.545 | 15.087 | 14.785 | 14.455 | 14.049 | 12.195 | 8.671 | 6.146 | 3.742 | Primary
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NPg Best View | 8.317 | 8.385 | 8.385 | 8.345 | 8.326 | 8.287 | 8.22 | 7.806 | 6.079 | 4.848 | 3.726 | Primary
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NPg Best View | 16.486 | 17.323 | 17.095 | 8.626 | 8.388 | 8.141 | 7.851 | 6.603 | 3.516 | 0.899 | -1.5 | Primary
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NPg Best View | 11.087 | 10.722 | 10.196 | 9.564 | 9.085 | 8.575 | 7.975 | 5.291 | 0.518 | -3.12 | -6.524 | Primary
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NPg Best View | 8.845 | 8.877 | 8.858 | 8.806 | 8.797 | 8.776 | 8.739 | 8.495 | 6.912 | 5.668 | 4.475 | Primary
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NPg Best View | 10.911 | 10.541 | 9.986 | 9.337 | 8.959 | 8.564 | 8.087 | 6.111 | 1.539 | -1.986 | -5.43 | Primary
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NPg Best View | 5.179 | 4.731 | 4.077 | 3.291 | 2.609 | 1.862 | 0.987 | -3.392 | -10.341 | -15.699 | -20.836 | Primary
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NPg Best View | 13.056 | 13.142 | 13.221 | 13.29 | 13.353 | 13.409 | 13.457 | 13.663 | 13.587 | 13.531 | 13.485 | Primary
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NPg Best View | 13.82 | 13.93 | 14.013 | 14.065 | 14.088 | 14.079 | 14.034 | 13.589 | 12.982 | 12.744 | 12.614 | Primary
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NPg Best View | 2.836 | 2.948 | 3.044 | 3.124 | 3.199 | 3.262 | 3.312 | 3.495 | 3.283 | 3.148 | 3.037 | Primary
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NPg Best View | 6.442 | 6.34 | 6.169 | 5.977 | 5.874 | 5.758 | 5.607 | 4.953 | 3.172 | 1.874 | 0.675 | Primary
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NPg Best View | 1.935 | 1.814 | 1.654 | 1.472 | 1.323 | 1.16 | 0.966 | 0.032 | -1.424 | -2.527 | -3.53 | Primary
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NPg Best View | 12.737 | 12.53 | 12.205 | 11.802 | 11.495 | 11.156 | 10.753 | 8.834 | 5.46 | 3.1 | 1.033 | Primary
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NPg Best View | 12.673 | 10.718 | 10.738 | 10.731 | 10.711 | 10.674 | 10.614 | 10.212 | 8.791 | 7.76 | 6.876 | Primary
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NPg Best View | 9.351 | 9.074 | 15.673 | 15.265 | 14.999 | 14.715 | 14.365 | 12.901 | 9.404 | 6.693 | 4.122 | Primary
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NPg Best View | 11.42 | 11.261 | 10.996 | 10.676 | 10.41 | 10.112 | 9.755 | 7.962 | 4.88 | 2.587 | 0.445 | Primary
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NPg Best View | 3.449 | 1.95 | 1.549 | 1.224 | 1.001 | 0.753 | 0.438 | -0.942 | -5.472 | -9.169 | -12.621 | Primary
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NPg Best View | 13.016 | 13.023 | 12.999 | 12.954 | 12.944 | 12.925 | 12.894 | 12.702 | 11.676 | 10.77 | 9.858 | Primary
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NPg Best View | 8.611 | 8.508 | 15.268 | 14.949 | 14.807 | 14.644 | 14.428 | 13.416 | 10.027 | 7.452 | 4.959 | Primary
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NPg Best View | 5.456 | 4.368 | 3.874 | 3.453 | 3.122 | 2.746 | 2.288 | 0.059 | -4.25 | -7.506 | -10.546 | Primary
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NPg Best View | 10.288 | 9.9 | 9.297 | 8.584 | 8.219 | 7.839 | 7.381 | 5.496 | 0.423 | -3.535 | -7.502 | Primary
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NPg Best View | 12.87 | 12.747 | 10.445 | 10.136 | 9.819 | 9.401 | 8.875 | 5.577 | 2.246 | 0.419 | -1.072 | Primary
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NPg Best View | 9.533 | 9.182 | 8.657 | 8.054 | 7.642 | 7.2 | 6.677 | 4.355 | 0.46 | -2.404 | -5.207 | Primary
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NPg Best View | 7.934 | 6.047 | 5.662 | 5.227 | 4.979 | 4.707 | 4.368 | 2.855 | -1.285 | -4.495 | -7.583 | Primary
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NPg Best View | 8.642 | 8.002 | 8.083 | 8.107 | 8.097 | 8.046 | 7.947 | 7.18 | 5.379 | 4.267 | 3.382 | Primary
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NPg Best View | 18.896 | 18.873 | 18.802 | 18.681 | 18.525 | 18.315 | 18.047 | 16.353 | 14.609 | 13.749 | 13.14 | Primary
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NPg Best View | 8.732 | 8.669 | 8.492 | 8.253 | 8.153 | 8.04 | 7.882 | 7.246 | 4.644 | 2.553 | 0.473 | Primary
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NPg Best View | 10.629 | 10.506 | 10.296 | 10.035 | 9.769 | 9.477 | 9.125 | 7.481 | 4.386 | 2.016 | -0.014 | Primary
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NPg Best View | 12.502 | 12.311 | 11.988 | 11.581 | 11.372 | 11.152 | 10.885 | 9.725 | 5.926 | 2.94 | 0.049 | Primary
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NPg Best View | 12.415 | 12.426 | 12.376 | 12.29 | 12.257 | 12.207 | 12.133 | 11.711 | 10.146 | 9.017 | 7.926 | Primary
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NPg Best View | 8.535 | 8.713 | 8.869 | 9.013 | 9.145 | 9.262 | 9.357 | 9.739 | 9.424 | 9.186 | 8.967 | Primary
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NPg Best View | 8.317 | 6.493 | 6.329 | 6.124 | 6.038 | 5.93 | 5.786 | 4.982 | 2.09 | -0.092 | -2.232 | Primary
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NPg Best View | 10.431 | 9.288 | 9.371 | 9.434 | 9.482 | 9.523 | 9.553 | 9.707 | 8.974 | 8.408 | 7.889 | Primary
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NPg Best View | 1.755 | 1.608 | 1.397 | 1.148 | 0.974 | 0.789 | 0.57 | -0.446 | -2.546 | -4.248 | -5.923 | Primary
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 3.46 | 3.439 | 3.389 | 3.332 | 3.324 | 3.312 | 3.294 | 3.207 | 2.416 | 1.771 | 1.09 | Primary
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NPg Best View | 13.861 | 13.786 | 13.626 | 13.424 | 13.21 | 12.955 | 12.65 | 10.959 | 8.833 | 7.525 | 6.379 | Primary
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NPg Best View | 24.681 | 24.741 | 24.79 | 24.825 | 24.85 | 24.869 | 24.88 | 24.893 | 24.269 | 23.694 | 23.136 | Primary
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NPg Best View | 15.025 | 15.081 | 15.102 | 15.103 | 15.126 | 15.143 | 15.146 | 15.186 | 14.385 | 13.714 | 13.062 | Primary
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NPg Best View | -0.685 | -0.721 | -0.821 | -0.971 | -1.101 | -1.257 | -1.457 | -2.531 | -4.703 | -6.474 | -8.156 | Primary
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NPg Best View | 3.829 | 3.63 | 3.301 | 2.846 | 2.414 | 1.876 | 1.217 | -2.77 | -8.702 | -12.826 | -16.59 | Primary
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NPg Best View | 11.16 | 11.031 | 10.776 | 10.452 | 10.276 | 10.089 | 9.851 | 8.899 | 5.95 | 3.651 | 1.429 | Primary
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NPg Best View | 11.82 | 11.962 | 12.078 | 12.17 | 12.237 | 12.279 | 12.288 | 12.158 | 11.959 | 11.972 | 12.039 | Primary
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NPg Best View | 8.759 | 8.456 | 7.968 | 7.366 | 6.965 | 6.518 | 5.971 | 3.32 | -2.254 | -6.469 | -10.44 | Primary
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NPg Best View | 17.113 | 16.457 | 16.385 | 16.298 | 16.237 | 16.176 | 16.11 | 15.822 | 14.334 | 13.018 | 11.724 | Primary
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NPg Best View | 5.092 | 4.873 | 4.577 | 4.282 | 4.071 | 3.849 | 3.58 | 2.498 | -0.344 | -2.654 | -4.777 | Primary
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NPg Best View | 8.682 | 8.524 | 8.205 | 7.784 | 7.504 | 7.209 | 6.845 | 5.293 | 0.61 | -3.225 | -6.854 | Primary
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NPg Best View | -1.106 | -1.262 | -1.505 | -1.791 | -1.965 | -2.147 | -2.366 | -3.317 | -6.222 | -8.569 | -10.825 | Primary
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NPg Best View | 15.422 | 15.388 | 15.307 | 15.178 | 15.034 | 14.856 | 14.638 | 13.347 | 10.97 | 9.254 | 7.726 | Primary
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NPg Best View | 16.095 | 15.669 | 15.204 | 14.892 | 14.643 | 14.369 | 14.037 | 12.487 | 9.3 | 6.893 | 4.722 | Primary
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NPg Best View | 10.873 | 10.576 | 10.093 | 9.515 | 9.205 | 8.872 | 8.466 | 6.746 | 3.031 | 0.281 | -2.522 | Primary
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NPg Best View | 24.322 | 24.387 | 24.442 | 24.492 | 24.54 | 24.582 | 24.616 | 24.749 | 24.567 | 24.423 | 24.288 | Primary
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NPg Best View | 8.547 | 8.605 | 8.651 | 8.686 | 8.713 | 8.735 | 8.749 | 8.799 | 7.863 | 7.109 | 6.437 | Primary
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NPg Best View | 11.328 | 11.077 | 10.661 | 10.156 | 9.889 | 9.61 | 9.272 | 7.927 | 4.459 | 1.766 | -0.957 | Primary
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NPg Best View | -0.673 | -0.702 | -0.779 | -0.888 | -0.971 | -1.066 | -1.191 | -1.752 | -2.632 | -3.325 | -3.985 | Primary
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NPg Best View | 9.347 | 9.275 | 9.141 | 8.978 | 8.848 | 8.709 | 8.549 | 7.778 | 5.771 | 4.091 | 2.424 | Primary
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NPg Best View | 13.514 | 13.286 | 12.915 | 12.473 | 12.23 | 11.973 | 11.657 | 10.315 | 6.529 | 3.466 | 0.436 | Primary
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NPg Best View | 11.668 | 11.478 | 11.193 | 10.846 | 10.611 | 10.358 | 10.06 | 8.685 | 5.682 | 3.368 | 1.181 | Primary
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NPg Best View | 8.404 | 8.12 | 7.706 | 7.208 | 6.771 | 6.307 | 5.76 | 3.307 | -0.662 | -3.658 | -6.371 | Primary
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NPg Best View | 13.62 | 13.447 | 13.203 | 12.908 | 12.614 | 12.281 | 11.898 | 9.791 | 6.268 | 3.454 | 0.805 | Primary
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NPg Best View | 7.737 | 7.745 | 7.642 | 7.474 | 7.317 | 7.121 | 6.868 | 5.412 | 1.545 | -1.34 | -3.923 | Primary
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NPg Best View | 14.116 | 13.91 | 13.575 | 13.174 | 12.966 | 12.746 | 12.478 | 11.374 | 8.458 | 6.194 | 3.906 | Primary
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NPg Best View | 7.599 | 7.303 | 6.879 | 6.44 | 6.157 | 5.854 | 5.483 | 3.888 | -0.713 | -4.408 | -7.889 | Primary
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NPg Best View | 8.165 | 8.054 | 7.863 | 7.612 | 7.416 | 7.194 | 6.933 | 5.513 | 1.971 | -0.935 | -3.797 | Primary
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Falling Short | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - System Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NPg Best View | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 35.501 | 32.933 | 31.511 | 29.842 | 28.676 | 27.667 | 26.441 | 20.628 | 5.88 | -5.355 | -16.446 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Consumer Transformation | 47.508 | 47.454 | 46.071 | 45.994 | 46.101 | 46.256 | 46.319 | 46.239 | 40.242 | 35.63 | 31.012 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Consumer Transformation | 58.451 | 56.644 | 55.514 | 54.265 | 53.411 | 52.683 | 51.801 | 47.643 | 33.004 | 20.938 | 9.19 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Consumer Transformation | 35.994 | 34.061 | 31.681 | 29.081 | 27.012 | 25.098 | 22.812 | 11.82 | -13.322 | -33.431 | -52.817 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Consumer Transformation | 24.223 | 22.131 | 20.243 | 18.243 | 16.723 | 15.356 | 13.682 | 6.127 | -11.02 | -24.561 | -37.858 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Consumer Transformation | 15.605 | 14.766 | 13.561 | 12.438 | 11.518 | 10.653 | 9.536 | 4.53 | -3.966 | -9.77 | -15.104 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 33.701 | 33.035 | 32.359 | 31.591 | 31.023 | 30.486 | 29.782 | 26.134 | 15.584 | 7.549 | 0.274 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Consumer Transformation | 40.907 | 39.529 | 38.344 | 36.971 | 35.977 | 35.083 | 28.716 | -8.724 | -21.309 | -30.234 | -38.664 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 99.094 | 97.244 | 96.408 | 95.326 | 94.682 | 94.124 | 93.309 | 88.572 | 67.782 | 51.107 | 35.426 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Consumer Transformation | 38.573 | 37.956 | 37.472 | 36.91 | 36.428 | 35.953 | 35.365 | 32.401 | 24.165 | 17.38 | 11.127 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Consumer Transformation | 41.027 | 39.448 | 38.135 | 36.686 | 35.713 | 34.904 | 33.862 | 28.975 | 15.512 | 5.167 | -5.181 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Consumer Transformation | 68.863 | 66.988 | 65.537 | 62.376 | 61.296 | 60.333 | 59.136 | 53.974 | 43.939 | 36.411 | 28.953 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 21.826 | 20.611 | 20.29 | 19.912 | 19.61 | 19.314 | 18.954 | 16.904 | 11.717 | 7.469 | 3.439 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Consumer Transformation | 53.767 | 51.92 | 50.49 | 48.847 | 47.391 | 45.953 | 44.271 | 35.303 | 17.505 | 3.501 | -9.479 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Consumer Transformation | 24.831 | 20.732 | 18.909 | 17.094 | 15.46 | 13.855 | 11.837 | 3.019 | -10.58 | -20.215 | -28.892 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Consumer Transformation | 20.766 | 18.814 | 17.52 | 16.093 | 14.941 | 13.887 | 12.57 | 6.349 | -9.278 | -21.42 | -32.964 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 66.348 | 61.059 | 58.621 | 56.041 | 54.097 | 52.397 | 50.231 | 40.297 | 15.434 | -3.433 | -21.773 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 28.879 | 27.429 | 25.93 | 24.09 | 22.693 | 21.369 | 19.744 | 10.427 | -12.557 | -30.177 | -46.692 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.17 | 19.745 | 18.21 | 16.516 | 15.327 | 14.321 | 13.094 | 7.481 | -8.367 | -20.891 | -33.508 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Consumer Transformation | 35.123 | 34.351 | 34.18 | 33.809 | 33.498 | 33.12 | 32.096 | 26.108 | 17.56 | 12.538 | 8.854 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 32.239 | 31.101 | 29.789 | 28.212 | 26.916 | 25.677 | 24.077 | 16.605 | -2.725 | -17.83 | -31.863 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Consumer Transformation | 68.43 | 68.35 | 68.334 | 68.313 | 68.289 | 68.26 | 68.229 | 68.019 | 67.67 | 67.285 | 66.895 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | -1.429 | -1.444 | -1.468 | -1.495 | -1.517 | -1.539 | -1.57 | -1.713 | -1.988 | -2.185 | -2.367 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Consumer Transformation | 116.215 | 103.09 | 90.549 | 85.244 | 81.001 | 77.098 | 72.361 | 50.997 | 16.806 | -6.976 | -29.385 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 56.926 | 56.174 | 55.283 | 54.161 | 53.529 | 53.036 | 52.423 | 48.587 | 32.463 | 19.254 | 6.245 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 26.831 | 25.594 | 25.149 | 24.568 | 24.164 | 23.788 | 23.281 | 19.556 | 9.632 | 2.494 | -3.986 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 35.132 | 32.99 | 32.37 | 31.603 | 30.648 | 29.575 | 28.504 | 23.609 | 19.553 | 16.419 | 14.224 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Falling Short | 46.771 | 46.653 | 45.345 | 45.398 | 45.372 | 45.292 | 45.188 | 44.458 | 43.507 | 42.774 | 42.378 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Falling Short | 58.239 | 56.74 | 56.191 | 55.536 | 54.744 | 53.86 | 52.977 | 49.408 | 47.421 | 46.022 | 45.122 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Falling Short | 35.44 | 34.015 | 32.628 | 31.028 | 29.13 | 27.037 | 24.947 | 15.369 | 7.573 | 1.374 | -3.309 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Falling Short | 24.133 | 22.699 | 21.88 | 20.915 | 19.719 | 18.381 | 17.075 | 11.5 | 7.687 | 5.028 | 3.172 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Falling Short | 15.638 | 15.28 | 14.808 | 14.264 | 13.535 | 12.681 | 11.842 | 8.181 | 5.654 | 4.122 | 3.43 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 33.54 | 33.069 | 32.786 | 32.412 | 31.905 | 31.307 | 30.699 | 27.844 | 25.516 | 23.949 | 23.194 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Falling Short | 40.468 | 39.478 | 39.019 | 38.397 | 37.564 | 36.588 | 30.386 | -6.054 | -10.005 | -12.819 | -14.415 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 98.421 | 96.735 | 96.425 | 95.945 | 95.251 | 94.405 | 93.519 | 89.313 | 85.905 | 83.508 | 82.336 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Falling Short | 38.36 | 37.766 | 37.419 | 37.002 | 36.49 | 35.916 | 35.335 | 32.632 | 30.397 | 28.654 | 27.423 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Falling Short | 40.598 | 39.479 | 38.986 | 38.364 | 37.559 | 36.633 | 35.707 | 31.71 | 29.007 | 27.134 | 25.991 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Falling Short | 68.905 | 67.627 | 67.045 | 64.595 | 63.768 | 62.832 | 61.929 | 58.062 | 55.415 | 53.637 | 52.395 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 21.446 | 20.146 | 19.811 | 19.438 | 19.014 | 18.556 | 18.081 | 15.608 | 13.099 | 10.845 | 8.953 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Falling Short | 52.711 | 50.728 | 49.406 | 47.918 | 46.225 | 44.388 | 42.498 | 32.737 | 22.78 | 14.099 | 7.137 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Falling Short | 25.124 | 21.701 | 20.911 | 19.961 | 18.728 | 17.317 | 15.955 | 10.167 | 6.473 | 4.444 | 3.56 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Falling Short | 20.386 | 18.776 | 18.119 | 17.307 | 16.289 | 15.142 | 14.001 | 8.838 | 4.811 | 1.917 | 0.007 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 65.823 | 61.447 | 60.475 | 59.265 | 57.711 | 55.928 | 54.164 | 46.503 | 41.159 | 37.59 | 35.531 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 27.712 | 26.294 | 25.195 | 23.88 | 22.311 | 20.554 | 18.715 | 9.051 | -0.942 | -9.321 | -15.372 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 20.613 | 19.612 | 18.866 | 17.981 | 16.898 | 15.695 | 14.506 | 9.192 | 5.023 | 1.686 | -0.998 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Falling Short | 34.605 | 33.776 | 33.679 | 33.487 | 33.177 | 32.753 | 31.752 | 26.404 | 21.326 | 17.475 | 15.88 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 31.997 | 31.254 | 30.72 | 29.967 | 28.952 | 27.775 | 26.619 | 21.54 | 17.945 | 15.748 | 14.626 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Falling Short | 68.194 | 67.996 | 67.863 | 67.725 | 67.582 | 67.435 | 67.283 | 66.468 | 65.563 | 64.599 | 63.608 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | -1.433 | -1.436 | -1.444 | -1.455 | -1.47 | -1.489 | -1.507 | -1.591 | -1.66 | -1.7 | -1.719 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Falling Short | 116.415 | 105.216 | 95.628 | 93.126 | 89.988 | 86.429 | 82.939 | 67.686 | 56.655 | 49.43 | 45.589 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 56.291 | 55.724 | 55.295 | 54.768 | 54.139 | 53.435 | 52.692 | 48.944 | 45.368 | 42.371 | 40.211 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 26.255 | 25.077 | 24.846 | 24.536 | 24.127 | 23.631 | 23.067 | 19.548 | 15.253 | 11.851 | 9.938 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 35.369 | 32.495 | 30.677 | 28.65 | 27.358 | 26.367 | 24.642 | 7.134 | -5.883 | -14.63 | -13.576 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Leading the Way | 47.444 | 47.259 | 45.705 | 45.481 | 45.537 | 45.709 | 45.562 | 38.696 | 33.477 | 29.984 | 31.954 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Leading the Way | 58.359 | 56.328 | 54.873 | 53.299 | 52.316 | 51.591 | 50.064 | 32.815 | 19.67 | 10.164 | 11.633 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Leading the Way | 35.831 | 33.56 | 30.68 | 27.574 | 25.33 | 23.428 | 20.338 | -9.314 | -32.023 | -48.457 | -48.582 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Leading the Way | 24.119 | 21.803 | 19.572 | 17.227 | 15.641 | 14.369 | 12.135 | -8.872 | -24.306 | -35.071 | -34.379 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Leading the Way | 15.574 | 14.638 | 13.254 | 11.949 | 10.985 | 10.147 | 8.791 | -2.177 | -9.513 | -13.819 | -12.72 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 33.661 | 32.883 | 32.026 | 31.067 | 30.429 | 29.874 | 28.749 | 16.303 | 7.2 | 1.175 | 2.649 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Leading the Way | 40.802 | 39.212 | 37.72 | 36.044 | 34.937 | 34.042 | 27.274 | -19.757 | -30.53 | -37.138 | -35.627 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 98.98 | 96.854 | 95.608 | 94.106 | 93.293 | 92.702 | 90.929 | 66.917 | 48.613 | 35.782 | 38.899 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Leading the Way | 38.533 | 37.828 | 37.211 | 36.507 | 35.968 | 35.475 | 34.55 | 24.995 | 17.545 | 11.982 | 12.161 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Leading the Way | 40.909 | 39.102 | 37.451 | 35.661 | 34.585 | 33.831 | 32.296 | 15.963 | 4.095 | -3.764 | -2.252 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Leading the Way | 68.82 | 66.824 | 65.17 | 61.82 | 60.721 | 59.839 | 58.43 | 45.81 | 36.765 | 30.674 | 31.226 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 21.806 | 20.538 | 20.136 | 19.677 | 19.337 | 19.027 | 18.504 | 12.668 | 7.983 | 4.43 | 4.138 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Leading the Way | 53.679 | 51.627 | 49.913 | 48 | 46.392 | 44.857 | 42.706 | 22.682 | 6.696 | -5.185 | -7.033 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Leading the Way | 24.836 | 20.654 | 18.65 | 16.658 | 15.039 | 13.524 | 11.273 | -6.77 | -18.871 | -26.584 | -25.509 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Leading the Way | 20.675 | 18.493 | 16.884 | 15.175 | 13.932 | 12.903 | 11.171 | -7.686 | -21.709 | -31.631 | -30.405 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 66.222 | 60.552 | 57.562 | 54.481 | 52.394 | 50.798 | 47.999 | 17.271 | -4.75 | -19.632 | -16.544 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 28.703 | 26.892 | 24.899 | 22.57 | 20.911 | 19.456 | 17.058 | -9.114 | -29.347 | -43.531 | -43.396 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 21.062 | 19.356 | 17.435 | 15.394 | 14.102 | 13.156 | 11.494 | -7.276 | -21.556 | -31.746 | -30.691 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Leading the Way | 35.031 | 34.037 | 33.597 | 32.983 | 32.462 | 31.886 | 30.46 | 19.145 | 12.476 | 9.267 | 10.393 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 32.162 | 30.806 | 29.183 | 27.321 | 25.985 | 24.826 | 22.66 | -1.081 | -18.332 | -30.345 | -28.153 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Leading the Way | 68.43 | 68.349 | 68.332 | 68.311 | 68.287 | 68.259 | 68.227 | 67.944 | 67.595 | 67.211 | 66.896 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | -1.429 | -1.447 | -1.475 | -1.504 | -1.525 | -1.543 | -1.575 | -1.942 | -2.186 | -2.344 | -2.299 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Leading the Way | 115.921 | 102.264 | 88.92 | 82.799 | 78.307 | 74.468 | 68.707 | 25.371 | -4.187 | -21.893 | -20.262 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 56.771 | 55.737 | 54.463 | 52.958 | 52.162 | 51.652 | 50.353 | 32.211 | 17.918 | 7.618 | 8.743 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 26.726 | 25.321 | 24.641 | 23.818 | 23.257 | 22.779 | 21.866 | 10.763 | 2.25 | -3.239 | -2.831 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 34.9 | 32.566 | 31.659 | 30.69 | 29.62 | 28.454 | 27.094 | 19.814 | 9.467 | -2.769 | -20.066 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - System Transformation | 46.988 | 46.931 | 45.65 | 45.747 | 45.767 | 45.719 | 45.549 | 44.043 | 38.592 | 32.828 | 25.012 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - System Transformation | 57.94 | 56.243 | 55.441 | 54.641 | 53.767 | 52.835 | 51.864 | 46.372 | 37.434 | 25.476 | 7.016 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - System Transformation | 35.088 | 33.293 | 31.401 | 29.484 | 27.403 | 25.197 | 22.817 | 10.063 | -8.904 | -29.867 | -58.661 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - System Transformation | 23.655 | 21.813 | 20.476 | 19.174 | 17.767 | 16.287 | 14.673 | 6.347 | -6.06 | -19.822 | -39.796 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - System Transformation | 15.164 | 14.384 | 13.427 | 12.616 | 11.712 | 10.738 | 9.66 | 4.221 | -2.164 | -8.56 | -17.277 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 33.386 | 32.747 | 32.242 | 31.729 | 31.132 | 30.471 | 29.734 | 25.33 | 17.4 | 9.29 | -1.94 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - System Transformation | 40.276 | 39.076 | 38.299 | 37.455 | 36.485 | 35.41 | 28.959 | -9.541 | -19.276 | -29.369 | -42.87 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 98.361 | 96.533 | 95.992 | 95.384 | 94.618 | 93.723 | 92.68 | 85.627 | 70.545 | 53.644 | 28.887 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - System Transformation | 38.344 | 37.676 | 37.212 | 36.716 | 36.164 | 35.569 | 34.933 | 31.225 | 24.884 | 18.113 | 8.585 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - System Transformation | 40.338 | 38.98 | 38.168 | 37.349 | 36.427 | 35.427 | 34.296 | 28.218 | 18.65 | 7.473 | -8.945 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - System Transformation | 68.395 | 66.68 | 65.607 | 62.902 | 61.916 | 60.882 | 59.731 | 54.219 | 46.265 | 38.097 | 27.036 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 21.555 | 20.284 | 19.955 | 19.605 | 19.211 | 18.78 | 18.304 | 15.421 | 10.574 | 5.643 | -0.537 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - System Transformation | 52.964 | 50.986 | 49.578 | 48.066 | 46.4 | 44.597 | 42.59 | 31.348 | 14.644 | -1.678 | -20.905 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - System Transformation | 24.473 | 20.425 | 18.879 | 17.44 | 15.877 | 14.235 | 12.479 | 3.932 | -6.914 | -16.465 | -28.72 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - System Transformation | 20.134 | 18.26 | 17.245 | 16.214 | 15.062 | 13.824 | 12.446 | 5.131 | -6.87 | -19.549 | -36.502 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 65.123 | 60.174 | 58.488 | 56.874 | 55.066 | 53.108 | 50.9 | 39.485 | 21.157 | 1.204 | -26.143 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 27.881 | 26.475 | 25.275 | 23.915 | 22.347 | 20.583 | 18.551 | 6.346 | -13.217 | -33.238 | -58.568 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 20.375 | 19.155 | 18.106 | 17.062 | 15.908 | 14.671 | 13.267 | 5.986 | -6.103 | -20.057 | -39.238 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - System Transformation | 34.71 | 33.906 | 33.793 | 33.579 | 33.23 | 32.713 | 31.469 | 24.203 | 17.58 | 11.8 | 5.407 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 31.755 | 30.685 | 29.678 | 28.575 | 27.327 | 25.975 | 24.462 | 16.223 | 1.402 | -13.336 | -33.661 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - System Transformation | 68.314 | 68.171 | 68.087 | 67.997 | 67.898 | 67.79 | 67.675 | 66.992 | 66.083 | 65.129 | 64.169 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | -1.439 | -1.453 | -1.472 | -1.489 | -1.51 | -1.532 | -1.56 | -1.704 | -1.961 | -2.168 | -2.406 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - System Transformation | 114.914 | 102.508 | 91.385 | 87.803 | 83.953 | 79.886 | 75.44 | 53.506 | 29.831 | 4.798 | -29.86 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 56.304 | 55.76 | 55.314 | 54.785 | 54.161 | 53.456 | 52.622 | 47.086 | 35.362 | 21.651 | 1.898 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 26.349 | 25.189 | 24.941 | 24.629 | 24.21 | 23.686 | 22.998 | 18.243 | 9.747 | 1.83 | -8.022 | BSP
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 35.706 | 33.321 | 32.032 | 30.516 | 29.425 | 28.482 | 27.378 | 22.447 | 8.587 | -2.181 | -13.1 | BSP
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NPg Best View | 47.837 | 47.958 | 46.669 | 46.693 | 46.805 | 46.954 | 47.008 | 47.072 | 41.357 | 36.904 | 32.314 | BSP
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NPg Best View | 58.612 | 56.971 | 55.917 | 54.776 | 53.91 | 53.176 | 52.335 | 48.818 | 34.763 | 23 | 11.386 | BSP
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NPg Best View | 36.362 | 34.735 | 32.587 | 30.231 | 28.312 | 26.534 | 24.473 | 14.961 | -8.639 | -27.901 | -46.958 | BSP
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NPg Best View | 24.53 | 22.7 | 21.06 | 19.314 | 18.027 | 16.899 | 15.567 | 9.702 | -6.392 | -19.426 | -32.483 | BSP
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NPg Best View | 16.26 | 15.796 | 14.971 | 14.157 | 13.564 | 12.992 | 12.204 | 8.631 | 1.174 | -4.117 | -9.255 | BSP
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 33.918 | 33.406 | 32.839 | 32.175 | 31.653 | 31.147 | 30.502 | 27.355 | 17.545 | 9.923 | 2.77 | BSP
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NPg Best View | 41.194 | 40.025 | 38.991 | 37.775 | 36.859 | 36.023 | 29.755 | -6.866 | -18.315 | -26.6 | -34.814 | BSP
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 99.584 | 98.043 | 97.412 | 96.537 | 95.96 | 95.442 | 94.694 | 90.669 | 71.003 | 54.946 | 39.418 | BSP
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NPg Best View | 38.698 | 38.178 | 37.758 | 37.267 | 36.803 | 36.339 | 35.781 | 33.153 | 25.403 | 18.885 | 12.712 | BSP
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NPg Best View | 41.328 | 39.977 | 38.821 | 37.544 | 36.655 | 35.927 | 35.023 | 31.1 | 18.463 | 8.547 | -1.629 | BSP
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NPg Best View | 69.307 | 67.741 | 66.555 | 63.637 | 62.762 | 61.998 | 61.069 | 57.302 | 48.063 | 40.906 | 33.64 | BSP
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 22.008 | 20.887 | 20.634 | 20.317 | 20.045 | 19.766 | 19.417 | 17.463 | 12.584 | 8.529 | 4.548 | BSP
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NPg Best View | 54.074 | 52.486 | 51.175 | 49.694 | 48.181 | 46.668 | 44.941 | 36.444 | 20.184 | 7.113 | -5.609 | BSP
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NPg Best View | 25.366 | 21.66 | 20.254 | 18.827 | 17.613 | 16.425 | 14.961 | 8.586 | -3.515 | -12.43 | -20.788 | BSP
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NPg Best View | 21.091 | 19.386 | 18.279 | 17.046 | 16.013 | 15.069 | 13.932 | 8.806 | -5.836 | -17.468 | -28.829 | BSP
NPgN | MELROSEGATE | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 66.938 | 62.103 | 59.99 | 57.748 | 56.001 | 54.501 | 52.674 | 44.81 | 21.572 | 3.548 | -14.436 | BSP
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 29.401 | 28.255 | 26.95 | 25.289 | 23.922 | 22.567 | 20.9 | 11.912 | -9.234 | -25.707 | -41.929 | BSP
NPgN | POTTER HOUSE | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 21.519 | 20.358 | 19.013 | 17.522 | 16.437 | 15.533 | 14.467 | 9.936 | -5.124 | -17.266 | -29.717 | BSP
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NPg Best View | 35.294 | 34.599 | 34.413 | 34.002 | 33.539 | 32.958 | 31.691 | 25.017 | 17.791 | 13.681 | 10.143 | BSP
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 32.547 | 31.671 | 30.572 | 29.245 | 28.133 | 27.09 | 25.807 | 19.996 | 1.811 | -12.713 | -26.501 | BSP
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NPg Best View | 68.613 | 68.606 | 68.651 | 68.683 | 68.7 | 68.701 | 68.675 | 68.489 | 68.145 | 67.766 | 67.382 | BSP
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | -1.418 | -1.424 | -1.442 | -1.461 | -1.476 | -1.491 | -1.51 | -1.606 | -1.859 | -2.044 | -2.221 | BSP
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NPg Best View | 117.26 | 104.894 | 93.272 | 88.796 | 85.518 | 82.504 | 78.862 | 62.282 | 32.009 | 10.198 | -11.493 | BSP
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 56.919 | 56.24 | 55.284 | 54.159 | 53.33 | 52.653 | 51.894 | 47.98 | 32.469 | 19.66 | 6.745 | BSP
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 26.956 | 25.798 | 25.34 | 24.741 | 24.2 | 23.659 | 22.971 | 18.828 | 9.872 | 3.396 | -2.967 | BSP
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Consumer Transformation | 5.565 | 5.195 | 4.593 | 3.889 | 3.444 | 3.109 | 2.697 | 0.916 | -4.634 | -8.93 | -13.435 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Consumer Transformation | 12.024 | 11.098 | 9.017 | 8.049 | 7.304 | 6.659 | 5.883 | 2.53 | -6.131 | -12.638 | -19.017 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 7.996 | 7.615 | 9.028 | 8.357 | 7.878 | 7.456 | 6.936 | 4.564 | -0.752 | -4.809 | -8.86 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Consumer Transformation | 6.223 | 5.948 | 5.468 | 4.899 | 4.514 | 4.194 | 3.792 | 2.043 | -3.259 | -7.459 | -11.671 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Consumer Transformation | 26.375 | 26.377 | 26.378 | 26.379 | 26.38 | 26.381 | 26.382 | 26.386 | 26.389 | 26.392 | 26.394 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Consumer Transformation | 2.828 | 2.784 | 2.674 | 2.532 | 2.459 | 2.401 | 2.315 | 1.83 | -0.08 | -1.545 | -2.991 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Consumer Transformation | 4.071 | 4.042 | 4.004 | 3.967 | 3.93 | 3.893 | 3.845 | 3.634 | 3.387 | 3.201 | 3.032 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Consumer Transformation | 4.613 | 4.453 | 4.222 | 3.95 | 3.724 | 3.513 | 3.264 | 1.89 | -1.057 | -3.348 | -5.537 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Consumer Transformation | 8.527 | 8.412 | 8.207 | 7.961 | 7.812 | 7.702 | 7.557 | 6.798 | 3.747 | 1.304 | -1.191 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Consumer Transformation | 12.497 | 12.194 | 11.715 | 11.211 | 10.813 | 10.441 | 9.965 | 7.823 | 4.178 | 1.69 | -0.593 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Consumer Transformation | 5.008 | 4.414 | 3.953 | 3.456 | 3.066 | 2.707 | 2.273 | 0.169 | -5.993 | -11.023 | -15.813 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Consumer Transformation | 11.88 | 11.324 | 11.011 | 10.635 | 10.396 | 10.195 | 9.933 | 8.578 | 3.869 | 0.083 | -3.61 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Consumer Transformation | 7.549 | 7.147 | 6.602 | 6.009 | 5.571 | 5.164 | 4.681 | 2.062 | -2.855 | -6.403 | -9.703 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Consumer Transformation | 6.762 | 6.11 | 5.725 | 5.293 | 5.003 | 4.743 | 4.419 | 2.831 | -1.475 | -4.859 | -8.114 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 13.302 | 13.163 | 12.933 | 12.664 | 12.433 | 12.188 | 11.39 | 7.709 | 4.411 | 2.396 | 0.858 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 16.845 | 16.859 | 16.825 | 16.723 | 16.631 | 16.536 | 16.42 | 15.757 | 14.612 | 14.055 | 13.647 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Consumer Transformation | 9.711 | 8.796 | 8.628 | 8.416 | 8.243 | 8.063 | 7.826 | 6.422 | 2.171 | -1.115 | -3.991 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Consumer Transformation | 10.928 | 10.297 | 9.923 | 9.501 | 9.162 | 8.841 | 8.455 | 6.573 | 1.527 | -2.575 | -6.383 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Consumer Transformation | 16.115 | 15.932 | 15.661 | 15.366 | 15.145 | 14.947 | 14.704 | 13.523 | 10.101 | 7.355 | 4.768 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Consumer Transformation | 10.428 | 10.357 | 10.243 | 10.092 | 9.947 | 9.781 | 9.571 | 7.995 | 5.405 | 3.859 | 2.757 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Consumer Transformation | 21.589 | 21.318 | 20.95 | 20.551 | 20.193 | 19.838 | 19.413 | 17.1 | 12.404 | 8.803 | 5.53 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 17.773 | 17.618 | 17.401 | 17.162 | 16.953 | 16.747 | 16.505 | 15.297 | 12.401 | 9.943 | 7.61 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Consumer Transformation | 13.232 | 12.496 | 11.809 | 11.028 | 10.466 | 9.973 | 9.381 | 6.7 | 0.46 | -4.383 | -9.175 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Consumer Transformation | 7.878 | 7.346 | 7.224 | 7.076 | 6.989 | 6.929 | 6.843 | 6.438 | 4.404 | 2.807 | 1.207 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Consumer Transformation | 9.164 | 8.782 | 8.141 | 7.387 | 6.864 | 6.429 | 5.878 | 3.043 | -3.531 | -8.178 | -12.786 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Consumer Transformation | 7.887 | 7.239 | 6.642 | 6.052 | 5.57 | 5.144 | 4.62 | 2.415 | -1.588 | -4.509 | -7.364 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Consumer Transformation | 8.088 | 7.801 | 7.358 | 6.847 | 6.47 | 6.146 | 5.741 | 3.831 | -1.012 | -4.662 | -8.194 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Consumer Transformation | 9.14 | 8.926 | 8.582 | 8.178 | 7.829 | 7.498 | 7.085 | 5.239 | 0.865 | -2.663 | -5.97 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Consumer Transformation | 3.953 | 3.685 | 3.22 | 2.659 | 2.26 | 1.897 | 1.441 | -0.763 | -6.922 | -11.741 | -16.317 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Consumer Transformation | 7.827 | 7.453 | 6.936 | 6.355 | 5.864 | 5.404 | 4.861 | 2.346 | -2.826 | -7.08 | -11.263 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Consumer Transformation | 10.356 | 10.171 | 10.258 | 10.312 | 10.387 | 10.459 | 10.503 | 10.587 | 8.984 | 7.742 | 6.573 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Consumer Transformation | 6.444 | 5.512 | 5.263 | 5.012 | 4.799 | 4.595 | 4.333 | 3.101 | 0.307 | -1.861 | -3.885 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Consumer Transformation | 17.096 | 15.793 | 15.097 | 14.276 | 13.672 | 13.132 | 12.475 | 9.309 | 2.385 | -2.652 | -7.539 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Consumer Transformation | 13 | 12.978 | 12.899 | 12.796 | 12.74 | 12.699 | 12.63 | 12.31 | 10.935 | 9.882 | 8.8 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Consumer Transformation | 6.784 | 6.756 | 6.717 | 6.674 | 6.64 | 6.61 | 6.574 | 6.412 | 6.096 | 5.853 | 5.615 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 12.734 | 12.734 | 12.688 | 12.609 | 12.569 | 12.537 | 12.483 | 12.076 | 10.211 | 8.807 | 7.499 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 16.844 | 16.802 | 16.713 | 16.589 | 16.512 | 16.444 | 16.349 | 15.635 | 13.622 | 12.211 | 10.934 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Consumer Transformation | 4.777 | 4.73 | 4.66 | 4.584 | 4.547 | 4.528 | 4.503 | 4.361 | 3.4 | 2.591 | 1.724 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Consumer Transformation | 9.17 | 9.017 | 8.794 | 8.557 | 8.399 | 8.264 | 8.1 | 7.345 | 5.266 | 3.657 | 2.081 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Consumer Transformation | 10.346 | 10.152 | 9.831 | 9.468 | 9.198 | 8.95 | 8.632 | 7.156 | 2.787 | -0.67 | -3.912 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 23.142 | 22.862 | 22.825 | 22.78 | 22.753 | 22.729 | 22.685 | 22.484 | 21.23 | 20.195 | 19.253 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Consumer Transformation | 6.812 | 6.71 | 6.502 | 6.256 | 6.077 | 5.898 | 5.651 | 4.116 | 0.089 | -2.71 | -5.093 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Consumer Transformation | 5.141 | 4.318 | 3.672 | 2.919 | 2.343 | 1.816 | 1.155 | -2.136 | -8.517 | -12.819 | -16.721 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Consumer Transformation | 12.069 | 10.801 | 10.399 | 9.924 | 9.571 | 9.248 | 8.839 | 6.886 | 1.185 | -3.226 | -7.392 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 8.94 | 8.809 | 8.586 | 8.35 | 8.13 | 7.903 | 7.6 | 6.159 | 3.1 | 0.765 | -1.281 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 14.274 | 14.005 | 13.59 | 13.15 | 12.812 | 12.5 | 12.105 | 10.304 | 4.963 | 0.589 | -3.532 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Consumer Transformation | 4.292 | 3.828 | 3.706 | 3.559 | 3.451 | 3.359 | 3.237 | 2.648 | 0.298 | -1.645 | -3.594 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Consumer Transformation | 18.325 | 18.14 | 17.83 | 17.457 | 17.154 | 16.869 | 16.512 | 14.76 | 10.035 | 6.34 | 2.937 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Consumer Transformation | 18.913 | 18.903 | 18.869 | 18.82 | 18.795 | 18.773 | 18.741 | 18.561 | 17.492 | 16.57 | 15.675 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Consumer Transformation | 8.133 | 7.955 | 7.664 | 7.355 | 7.13 | 6.932 | 6.664 | 5.448 | 2.78 | 0.808 | -1.168 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Consumer Transformation | 9.076 | 9.069 | 9.033 | 8.982 | 8.936 | 8.883 | 8.805 | 8.255 | 7.104 | 6.315 | 5.649 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Consumer Transformation | 1.72 | 1.542 | 1.195 | 0.751 | 0.465 | 0.238 | -0.059 | -1.429 | -6.207 | -10.03 | -13.887 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Consumer Transformation | 5.394 | 4.633 | 3.662 | 2.827 | 2.116 | 1.428 | 0.582 | -3.187 | -9.409 | -13.84 | -17.787 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Consumer Transformation | 10.61 | 10.138 | 8.707 | 7.95 | 7.411 | 6.961 | 6.42 | 3.859 | -2.374 | -7.056 | -11.779 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Consumer Transformation | 15.66 | 15.341 | 15.296 | 15.225 | 15.157 | 15.078 | 14.966 | 14.227 | 12.64 | 11.534 | 10.619 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Consumer Transformation | 10.913 | 9.477 | 9.131 | 8.704 | 8.41 | 8.156 | 7.818 | 6.102 | -0.381 | -5.451 | -10.279 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Consumer Transformation | 8.018 | 7.584 | 6.923 | 6.187 | 5.632 | 5.133 | 4.513 | 1.656 | -4.478 | -9.146 | -13.696 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Consumer Transformation | 22.68 | 22.18 | 21.486 | 20.835 | 20.296 | 19.787 | 19.129 | 16.239 | 11.863 | 8.841 | 5.962 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Consumer Transformation | 5.227 | 4.964 | 4.541 | 4.047 | 3.698 | 3.4 | 3.034 | 1.303 | -3.362 | -7.031 | -10.681 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Consumer Transformation | 11.82 | 11.59 | 11.241 | 10.861 | 10.63 | 10.455 | 10.238 | 9.328 | 6.517 | 4.317 | 1.975 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Consumer Transformation | 18.308 | 18.204 | 18.003 | 17.75 | 17.562 | 17.388 | 17.163 | 16.014 | 12.323 | 9.404 | 6.68 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Consumer Transformation | 9.389 | 9.395 | 7.904 | 7.813 | 7.769 | 7.732 | 7.666 | 7.142 | 5.194 | 3.836 | 2.593 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Consumer Transformation | 27.466 | 27.51 | 27.533 | 27.53 | 27.51 | 27.466 | 27.395 | 26.687 | 25.428 | 24.774 | 24.435 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Consumer Transformation | 14.594 | 14.119 | 14.086 | 14.028 | 14.044 | 14.091 | 14.116 | 14.191 | 13.025 | 12.097 | 11.015 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Consumer Transformation | 2.827 | 2.6 | 2.197 | 1.702 | 1.144 | 0.494 | -0.345 | -5.436 | -10.796 | -13.314 | -14.465 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Consumer Transformation | 18.156 | 18.271 | 18.37 | 18.453 | 18.537 | 18.618 | 18.689 | 18.977 | 18.775 | 18.589 | 18.379 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 7.483 | 6.946 | 6.441 | 5.872 | 5.407 | 4.971 | 4.44 | 2.093 | -2.502 | -5.962 | -9.247 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Consumer Transformation | 3.124 | 2.987 | 2.723 | 2.4 | 2.255 | 2.173 | 2.06 | 1.51 | -1.807 | -4.464 | -7.297 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Consumer Transformation | 14.311 | 13.972 | 13.481 | 12.956 | 12.518 | 12.091 | 11.558 | 9.034 | 4.956 | 2.071 | -0.591 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Consumer Transformation | 15.286 | 12.906 | 12.908 | 12.884 | 12.879 | 12.866 | 12.814 | 12.389 | 10.451 | 9.018 | 7.774 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Consumer Transformation | 8.687 | 7.892 | 7.209 | 6.509 | 5.988 | 5.528 | 4.955 | 2.284 | -4.564 | -9.866 | -15.057 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Consumer Transformation | 18.48 | 18.373 | 18.207 | 18.041 | 17.927 | 17.835 | 17.715 | 17.181 | 15.412 | 14.008 | 12.565 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Consumer Transformation | 8.644 | 8.07 | 7.229 | 6.311 | 5.66 | 5.12 | 4.454 | 1.516 | -5.03 | -9.949 | -15.064 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Consumer Transformation | 4.229 | 3.481 | 2.898 | 2.215 | 1.671 | 1.159 | 0.537 | -2.419 | -8.438 | -12.81 | -16.853 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Consumer Transformation | 2.94 | 2.544 | 2.011 | 1.496 | 1.113 | 0.793 | 0.399 | -1.323 | -4.812 | -7.368 | -9.977 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Consumer Transformation | 8.546 | 8.512 | 8.447 | 23.765 | 23.701 | 23.639 | 23.558 | 22.978 | 21.854 | 21.181 | 20.635 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Consumer Transformation | 21.058 | 20.777 | 20.753 | 20.717 | 20.696 | 20.682 | 20.666 | 20.593 | 19.833 | 19.223 | 18.633 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Consumer Transformation | 19.302 | 19.113 | 18.802 | 18.44 | 18.201 | 18.022 | 17.798 | 16.764 | 13.528 | 11.085 | 8.569 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Consumer Transformation | 16.736 | 16.876 | 17.008 | 17.132 | 17.251 | 17.363 | 17.468 | 17.926 | 18.234 | 18.494 | 18.727 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Consumer Transformation | 14.789 | 14.876 | 14.907 | 14.916 | 14.956 | 14.998 | 15.003 | 14.915 | 13.794 | 13.055 | 12.361 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Consumer Transformation | 1.44 | 1.447 | 1.355 | 1.175 | 20.935 | 20.755 | 20.491 | 18.159 | 12.587 | 8.875 | 5.969 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Consumer Transformation | 7.736 | 7.369 | 6.838 | 6.265 | 5.85 | 5.482 | 5.034 | 3.06 | -1.384 | -4.839 | -8.306 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Consumer Transformation | 6.882 | 6.498 | 5.919 | 5.277 | 4.781 | 4.324 | 3.765 | 1.246 | -3.428 | -6.667 | -9.702 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Consumer Transformation | 17.738 | 17.669 | 17.563 | 17.443 | 17.322 | 17.194 | 17.034 | 16.223 | 14.463 | 13.062 | 11.835 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Consumer Transformation | 6.71 | 6.574 | 6.362 | 6.137 | 5.966 | 5.811 | 5.61 | 4.671 | 2.118 | 0.189 | -1.639 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 6.868 | 6.545 | 6.115 | 5.684 | 5.306 | 4.939 | 4.49 | 2.414 | -1.039 | -3.641 | -6.093 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Consumer Transformation | 18.668 | 18.655 | 18.613 | 18.558 | 18.52 | 18.485 | 18.434 | 18.144 | 17.252 | 16.583 | 15.96 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Consumer Transformation | 7.049 | 6.794 | 6.412 | 6.013 | 5.735 | 5.496 | 5.197 | 3.922 | 0.778 | -1.634 | -4.067 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Consumer Transformation | 2.79 | 2.77 | 2.74 | 2.709 | 2.682 | 2.655 | 2.62 | 2.455 | 2.152 | 1.935 | 1.734 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Consumer Transformation | 9.297 | 8.961 | 8.823 | 8.653 | 8.538 | 8.435 | 8.301 | 7.505 | 4.93 | 2.918 | 1.03 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Consumer Transformation | 15.083 | 14.906 | 14.638 | 14.347 | 14.113 | 13.897 | 13.623 | 12.417 | 10.008 | 8.181 | 6.409 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Consumer Transformation | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Consumer Transformation | 21.267 | 21.102 | 20.864 | 20.618 | 20.435 | 20.275 | 20.075 | 19.153 | 16.648 | 14.716 | 12.843 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Consumer Transformation | 8.565 | 8.26 | 7.795 | 7.298 | 7 | 6.78 | 6.505 | 5.279 | 1.304 | -1.794 | -5.054 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Consumer Transformation | 14.265 | 14.013 | 13.634 | 13.21 | 12.928 | 12.693 | 12.406 | 11.037 | 7.53 | 4.88 | 2.241 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Consumer Transformation | 33.362 | 33.003 | 32.967 | 32.925 | 32.899 | 32.882 | 32.857 | 32.752 | 32.158 | 31.699 | 31.239 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Consumer Transformation | 4.367 | 3.515 | 2.782 | 1.975 | 1.376 | 0.876 | 0.262 | -2.299 | -7.585 | -11.423 | -15.369 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Consumer Transformation | 15.032 | 14.288 | 13.968 | 13.581 | 13.257 | 12.944 | 12.587 | 10.55 | 5.644 | 1.722 | -2.048 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Consumer Transformation | 12.019 | 11.924 | 11.752 | 11.545 | 11.347 | 11.144 | 10.883 | 9.472 | 5.152 | 1.676 | -1.424 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Consumer Transformation | 15.02 | 14.97 | 14.881 | 14.772 | 14.702 | 14.644 | 14.569 | 14.106 | 12.451 | 11.139 | 9.857 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 24.355 | 22.518 | 22.154 | 21.767 | 21.462 | 21.175 | 20.823 | 19.308 | 16.372 | 14.149 | 12.036 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Consumer Transformation | 5.278 | 4.762 | 4.386 | 3.961 | 3.615 | 3.289 | 2.906 | 1.046 | -3.836 | -7.929 | -11.843 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Consumer Transformation | 1.489 | 0.663 | 0.021 | -0.647 | -1.143 | -1.568 | -2.086 | -4.404 | -10.526 | -15.514 | -20.547 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Consumer Transformation | 3.371 | 3.328 | 1.982 | 1.916 | 1.855 | 1.793 | 1.712 | 1.313 | 0.819 | 0.511 | 0.256 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Consumer Transformation | 8.846 | 8.369 | 10.006 | 9.63 | 9.334 | 9.049 | 8.676 | 6.902 | 1.973 | -1.889 | -5.485 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Consumer Transformation | 7.321 | 7.184 | 6.907 | 6.546 | 6.396 | 6.315 | 6.196 | 5.508 | 0.871 | -2.946 | -6.943 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Consumer Transformation | 32.739 | 31.373 | 31.319 | 31.25 | 31.187 | 31.12 | 31.033 | 30.497 | 28.688 | 27.175 | 25.823 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Consumer Transformation | 12.237 | 12.107 | 11.879 | 11.609 | 11.396 | 11.194 | 10.94 | 9.772 | 5.841 | 2.572 | -0.462 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Consumer Transformation | 8.941 | 8.232 | 7.953 | 7.704 | 7.513 | 7.337 | 7.118 | 6.2 | 3.932 | 2.176 | 0.517 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Consumer Transformation | 8.854 | 8.914 | 8.936 | 8.934 | 8.975 | 9.024 | 9.06 | 9.137 | 8.236 | 7.538 | 6.808 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Consumer Transformation | 13.987 | 13.948 | 13.849 | 13.709 | 13.587 | 13.466 | 13.306 | 12.511 | 9.622 | 7.283 | 5.169 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 14.778 | 14.756 | 14.674 | 14.529 | 14.348 | 14.113 | 13.798 | 11.4 | 7.578 | 5.285 | 3.715 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 18.921 | 18.78 | 18.562 | 18.293 | 18.128 | 17.99 | 17.827 | 16.946 | 13.613 | 10.714 | 7.729 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Consumer Transformation | 5.673 | 4.637 | 4.315 | 3.934 | 3.638 | 3.367 | 3.056 | 1.454 | -2.483 | -5.709 | -8.88 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Consumer Transformation | 5.851 | 4.209 | 2.968 | 1.583 | 0.492 | -0.462 | -1.576 | -6.359 | -14.669 | -20.824 | -27.028 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Consumer Transformation | 13.346 | 12.464 | 11.983 | 11.552 | 11.213 | 10.918 | 10.555 | 9.024 | 6.058 | 3.866 | 1.661 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Consumer Transformation | 15.838 | 14.997 | 14.542 | 14.025 | 13.653 | 13.321 | 12.906 | 11.044 | 6.11 | 2.267 | -1.407 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Consumer Transformation | 9.987 | 9.831 | 9.541 | 9.19 | 8.921 | 8.674 | 8.352 | 6.904 | 3.061 | 0.037 | -2.801 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Consumer Transformation | 11.112 | 11.161 | 11.203 | 11.239 | 11.269 | 11.296 | 11.315 | 11.373 | 11.281 | 11.189 | 11.093 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Consumer Transformation | 21.529 | 21.455 | 21.313 | 21.128 | 21.005 | 20.902 | 20.774 | 20.199 | 18.597 | 17.358 | 16.103 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Consumer Transformation | 16.319 | 16.459 | 16.577 | 16.677 | 16.78 | 16.878 | 16.962 | 17.307 | 16.754 | 16.311 | 15.887 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 10.833 | 10.42 | 9.828 | 9.181 | 8.703 | 8.285 | 7.788 | 5.568 | 0.536 | -3.325 | -7.164 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.967 | 21.939 | 21.885 | 21.826 | 21.79 | 21.762 | 21.721 | 21.53 | 20.911 | 20.418 | 19.902 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Consumer Transformation | 2.695 | 2.446 | 2.024 | 1.533 | 1.203 | 0.931 | 0.589 | -0.881 | -5.681 | -9.466 | -13.194 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Consumer Transformation | 6.609 | 6.595 | 6.57 | 6.541 | 6.522 | 6.506 | 6.484 | 6.378 | 6.024 | 5.748 | 5.48 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Consumer Transformation | 8.145 | 7.347 | 7.046 | 6.743 | 6.539 | 6.39 | 6.195 | 5.351 | 2.94 | 1.166 | -0.72 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Consumer Transformation | 12.992 | 12.406 | 11.541 | 10.556 | 9.734 | 8.96 | 8.014 | 3.325 | -6.97 | -14.869 | -22.133 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Consumer Transformation | 10.52 | 9.018 | 8.116 | 7.587 | 7.193 | 6.835 | 6.383 | 4.119 | -1.844 | -6.337 | -10.528 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 3.963 | 3.807 | 3.599 | 3.371 | 3.159 | 2.941 | 2.684 | 1.326 | -1.362 | -3.496 | -5.414 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 3.962 | 3.912 | 3.852 | 3.789 | 3.727 | 3.664 | 3.593 | 3.221 | 2.692 | 2.227 | 1.792 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Consumer Transformation | 3.268 | 2.875 | 23.93 | 23.628 | 23.41 | 23.212 | 22.953 | 21.264 | 17.413 | 14.742 | 12.284 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Consumer Transformation | 13.88 | 13.319 | 12.887 | 12.439 | 12.053 | 11.689 | 11.234 | 9.334 | 6.994 | 5.513 | 4.179 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Consumer Transformation | 4.362 | 4.205 | 3.984 | 3.749 | 3.566 | 3.397 | 3.197 | 2.347 | 0.885 | -0.222 | -1.289 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Consumer Transformation | 3.598 | 3.471 | 3.3 | 3.122 | 2.958 | 2.792 | 2.59 | 1.608 | 0.094 | -1.027 | -2.024 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 14.045 | 13.407 | 12.996 | 12.502 | 12.11 | 11.749 | 11.288 | 9.18 | 3.483 | -1.016 | -5.316 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Consumer Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Consumer Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Consumer Transformation | 17.649 | 17.118 | 16.892 | 16.63 | 16.455 | 16.304 | 16.111 | 15.228 | 12.137 | 9.658 | 7.258 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Consumer Transformation | 15.292 | 14.247 | 14.179 | 14.097 | 14.013 | 13.922 | 13.807 | 13.151 | 11.964 | 11.072 | 10.308 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Consumer Transformation | 10.955 | 10.71 | 10.337 | 9.942 | 9.67 | 9.444 | 9.154 | 7.752 | 4.353 | 1.866 | -0.611 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Consumer Transformation | 12.991 | 12.69 | 12.287 | 11.892 | 11.554 | 11.229 | 10.826 | 8.944 | 5.741 | 3.349 | 1.096 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Consumer Transformation | 10.513 | 9.719 | 9.498 | 9.225 | 9.009 | 8.804 | 8.552 | 7.344 | 4.041 | 1.351 | -1.189 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Consumer Transformation | 11.305 | 11.164 | 10.921 | 10.633 | 10.456 | 10.313 | 10.126 | 9.105 | 5.864 | 3.379 | 0.923 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Consumer Transformation | 18.742 | 17.958 | 17.925 | 17.861 | 17.834 | 17.818 | 17.773 | 17.458 | 15.556 | 14.051 | 12.589 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Consumer Transformation | 16.518 | 16.196 | 15.709 | 15.176 | 14.776 | 14.402 | 13.931 | 11.42 | 6.346 | 2.755 | -0.55 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | 8.886 | 8.748 | 8.537 | 8.318 | 8.12 | 7.923 | 7.671 | 6.565 | 4.95 | 3.816 | 2.808 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Consumer Transformation | 12.849 | 12.386 | 10.424 | 9.83 | 9.437 | 9.099 | 8.676 | 6.513 | 0.59 | -3.683 | -7.768 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Consumer Transformation | 23.286 | 13.72 | 6.548 | 6.074 | 5.725 | 5.416 | 5.037 | 3.088 | -1.587 | -5.043 | -8.361 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Consumer Transformation | 2.501 | 1.629 | 0.832 | -1.733 | -2.324 | -2.85 | -3.503 | -6.346 | -12.158 | -16.589 | -20.967 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Consumer Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Consumer Transformation | 5.51 | 5.391 | 5.224 | 5.029 | 4.882 | 4.744 | 4.581 | 3.642 | 1.218 | -0.722 | -2.564 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Consumer Transformation | 12.153 | 11.318 | 10.939 | 10.453 | 10.1 | 9.79 | 9.423 | 7.677 | 3.521 | 0.483 | -2.472 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 8.028 | 6.37 | 6.229 | 6.031 | 5.927 | 5.849 | 5.733 | 5.039 | 1.965 | -0.352 | -2.596 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 27.962 | 27.985 | 28.008 | 28.03 | 28.05 | 28.07 | 28.089 | 28.17 | 28.235 | 28.289 | 28.337 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Consumer Transformation | 19.994 | 18.919 | 18.506 | 18.037 | 17.699 | 17.404 | 17.047 | 15.473 | 11.713 | 8.756 | 5.809 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Consumer Transformation | 8.385 | 7.786 | 7.939 | 8.027 | 8.081 | 8.079 | 8 | 6.768 | 4.155 | 2.896 | 2.296 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Consumer Transformation | 4.207 | 4.13 | 4.114 | 4.095 | 4.072 | 4.045 | 4.015 | 3.818 | 3.487 | 3.124 | 2.756 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Consumer Transformation | 14.423 | 14.067 | 13.545 | 12.993 | 12.624 | 12.324 | 11.959 | 10.314 | 5.121 | 0.862 | -3.44 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Consumer Transformation | 2.514 | 2.207 | 1.782 | 1.319 | 0.893 | 0.466 | -0.055 | -2.594 | -6.879 | -10.132 | -13.083 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Consumer Transformation | 8.844 | 7.894 | 7.551 | 7.189 | 6.868 | 6.57 | 6.201 | 4.635 | 2.515 | 1.064 | -0.35 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 25.255 | 24.714 | 24.226 | 23.669 | 23.226 | 22.808 | 22.298 | 19.887 | 14.087 | 9.48 | 5.147 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Consumer Transformation | 11.801 | 11.478 | 10.951 | 10.335 | 9.93 | 9.607 | 9.204 | 7.37 | 2.3 | -1.5 | -5.36 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Consumer Transformation | 11.334 | 10.964 | 10.42 | 9.824 | 9.376 | 8.976 | 8.485 | 6.251 | 0.794 | -3.577 | -7.894 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Consumer Transformation | 14.012 | 13.833 | 13.928 | 13.999 | 14.096 | 14.197 | 14.28 | 14.61 | 13.905 | 13.348 | 12.756 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Consumer Transformation | 32.718 | 32.298 | 31.743 | 31.181 | 30.708 | 30.252 | 29.712 | 27.235 | 21.616 | 16.945 | 12.486 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Consumer Transformation | 9.781 | 8.23 | 8.144 | 8.027 | 7.933 | 7.832 | 7.68 | 6.83 | 4.481 | 2.713 | 1.168 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Consumer Transformation | 8.306 | 7.577 | 7.214 | 6.795 | 6.466 | 6.158 | 5.78 | 4.048 | -0.549 | -4.331 | -7.954 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Consumer Transformation | 30.746 | 30.756 | 30.766 | 30.774 | 30.784 | 30.794 | 30.804 | 30.846 | 30.841 | 30.838 | 30.829 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Consumer Transformation | 9.132 | 9.108 | 24.425 | 24.311 | 24.261 | 24.239 | 24.199 | 23.996 | 22.176 | 20.668 | 19.116 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Consumer Transformation | 8.732 | 7.065 | 21.673 | 21.259 | 20.918 | 20.587 | 20.17 | 18.244 | 13.339 | 9.469 | 5.865 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Consumer Transformation | 9.548 | 9.299 | 8.961 | 8.585 | 8.232 | 7.88 | 7.454 | 5.317 | 1.625 | -1.252 | -3.934 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Consumer Transformation | 12.117 | 12.008 | 11.85 | 11.691 | 11.552 | 11.418 | 11.256 | 10.609 | 9.395 | 8.449 | 7.598 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Consumer Transformation | 20.28 | 19.748 | 19.649 | 19.524 | 19.449 | 19.383 | 19.286 | 18.796 | 16.259 | 14.12 | 12.089 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Consumer Transformation | 10.982 | 10.518 | 9.86 | 9.229 | 8.718 | 8.243 | 7.644 | 4.895 | -0.369 | -4.145 | -7.669 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Consumer Transformation | 12.327 | 11.927 | 11.595 | 11.211 | 10.936 | 10.697 | 10.407 | 9.094 | 4.756 | 1.147 | -2.378 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Consumer Transformation | 10.932 | 10.327 | 9.924 | 9.479 | 9.106 | 8.755 | 8.317 | 6.43 | 2.288 | -1.013 | -4.131 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 4.893 | 4.883 | 4.844 | 4.788 | 4.766 | 4.75 | 4.725 | 4.56 | 3.592 | 2.843 | 2.117 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 4.755 | 4.744 | 4.708 | 4.648 | 4.612 | 4.579 | 4.533 | 4.218 | 3.014 | 2.14 | 1.35 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 7.538 | 7.438 | 7.284 | 7.111 | 6.973 | 6.848 | 6.69 | 5.99 | 4.729 | 3.829 | 2.952 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 7.413 | 7.31 | 7.149 | 6.963 | 6.825 | 6.709 | 6.562 | 5.909 | 4.247 | 2.987 | 1.73 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Consumer Transformation | 13.169 | 12.968 | 12.673 | 12.349 | 12.071 | 11.802 | 11.479 | 10.028 | 5.845 | 2.21 | -1.213 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 22.12 | 21.697 | 21.131 | 20.594 | 20.187 | 19.83 | 19.384 | 17.389 | 13.554 | 10.745 | 7.947 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Consumer Transformation | 29.807 | 28.928 | 28.903 | 28.874 | 28.844 | 28.812 | 28.774 | 28.528 | 28.159 | 27.871 | 27.624 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Consumer Transformation | 5.818 | 5.4 | 5.369 | 5.335 | 5.307 | 5.283 | 5.251 | 5.106 | 4.643 | 4.276 | 3.921 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Consumer Transformation | 11.67 | 11.698 | 11.688 | 11.656 | 11.653 | 11.659 | 11.648 | 11.562 | 9.86 | 8.438 | 7.105 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Falling Short | 5.354 | 5.249 | 5.081 | 4.85 | 4.548 | 4.203 | 3.864 | 2.518 | 1.708 | 1.157 | 0.797 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Falling Short | 11.918 | 11.344 | 9.805 | 9.405 | 8.887 | 8.304 | 7.743 | 5.368 | 3.758 | 2.833 | 2.337 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 7.916 | 7.723 | 9.47 | 9.157 | 8.767 | 8.328 | 7.895 | 6.003 | 4.627 | 3.62 | 2.913 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Falling Short | 6.086 | 5.975 | 5.804 | 5.572 | 5.268 | 4.922 | 4.586 | 3.246 | 2.527 | 2.103 | 1.854 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Falling Short | 26.374 | 26.375 | 26.375 | 26.376 | 26.376 | 26.377 | 26.377 | 26.378 | 26.379 | 26.379 | 26.379 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Falling Short | 2.653 | 2.605 | 2.538 | 2.448 | 2.334 | 2.201 | 2.062 | 1.373 | 0.697 | 0.107 | -0.357 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Falling Short | 4.071 | 4.049 | 4.024 | 3.997 | 3.963 | 3.927 | 3.892 | 3.73 | 3.601 | 3.502 | 3.421 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Falling Short | 4.35 | 4.161 | 3.948 | 3.706 | 3.429 | 3.128 | 2.816 | 1.165 | -0.585 | -2.143 | -3.409 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Falling Short | 8.264 | 8.163 | 8.036 | 7.883 | 7.696 | 7.488 | 7.274 | 6.21 | 5.154 | 4.196 | 3.378 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Falling Short | 12.49 | 12.376 | 12.202 | 11.977 | 11.67 | 11.308 | 10.951 | 9.378 | 8.293 | 7.651 | 7.37 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Falling Short | 4.921 | 4.448 | 4.206 | 3.922 | 3.574 | 3.185 | 2.799 | 1.047 | -0.334 | -1.359 | -2.07 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Falling Short | 11.772 | 11.304 | 11.175 | 11.004 | 10.785 | 10.533 | 10.274 | 9.142 | 8.369 | 7.828 | 7.548 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Falling Short | 7.448 | 7.156 | 6.823 | 6.45 | 6.014 | 5.528 | 5.027 | 2.503 | 0.097 | -1.863 | -3.21 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Falling Short | 6.672 | 6.107 | 5.913 | 5.684 | 5.403 | 5.087 | 4.77 | 3.343 | 2.239 | 1.379 | 0.755 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 13.203 | 13.113 | 12.988 | 12.827 | 12.614 | 12.354 | 11.583 | 8.26 | 6.479 | 5.207 | 4.714 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 16.71 | 16.698 | 16.672 | 16.632 | 16.575 | 16.503 | 16.422 | 15.83 | 14.79 | 13.865 | 13.269 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Falling Short | 9.656 | 8.764 | 8.677 | 8.553 | 8.384 | 8.179 | 7.96 | 6.855 | 5.853 | 5.167 | 4.893 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Falling Short | 10.901 | 10.351 | 10.136 | 9.874 | 9.559 | 9.206 | 8.849 | 7.333 | 6.403 | 5.784 | 5.453 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Falling Short | 16.138 | 16.045 | 15.927 | 15.786 | 15.609 | 15.406 | 15.205 | 14.341 | 13.748 | 13.351 | 13.145 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Falling Short | 10.399 | 10.358 | 10.3 | 10.219 | 10.108 | 9.965 | 9.793 | 8.6 | 7.026 | 5.876 | 5.443 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Falling Short | 21.508 | 21.312 | 21.083 | 20.816 | 20.499 | 20.143 | 19.772 | 17.878 | 16.046 | 14.646 | 13.795 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 17.608 | 17.417 | 17.206 | 16.971 | 16.705 | 16.419 | 16.132 | 14.738 | 13.452 | 12.291 | 11.257 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Falling Short | 13.207 | 12.699 | 12.405 | 12.051 | 11.618 | 11.136 | 10.666 | 8.654 | 7.233 | 6.182 | 5.423 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Falling Short | 7.781 | 7.305 | 7.283 | 7.241 | 7.177 | 7.1 | 7.023 | 6.681 | 6.423 | 6.261 | 6.168 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Falling Short | 8.861 | 8.753 | 8.568 | 8.304 | 7.946 | 7.523 | 7.085 | 4.979 | 3.181 | 1.991 | 1.506 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Falling Short | 7.911 | 7.509 | 7.261 | 6.971 | 6.608 | 6.202 | 5.808 | 4.207 | 3.22 | 2.582 | 2.178 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Falling Short | 8.12 | 8.019 | 7.874 | 7.687 | 7.435 | 7.144 | 6.856 | 5.549 | 4.449 | 3.675 | 3.248 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Falling Short | 9.101 | 8.958 | 8.769 | 8.527 | 8.224 | 7.884 | 7.554 | 6.158 | 5.258 | 4.652 | 4.239 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Falling Short | 3.916 | 3.803 | 3.631 | 3.396 | 3.084 | 2.722 | 2.36 | 0.781 | -0.331 | -1.051 | -1.399 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Falling Short | 7.644 | 7.336 | 6.982 | 6.576 | 6.107 | 5.6 | 5.099 | 2.768 | 0.774 | -0.915 | -2.37 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Falling Short | 10.126 | 9.878 | 9.931 | 9.962 | 9.969 | 9.96 | 9.944 | 9.776 | 9.515 | 9.319 | 9.217 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Falling Short | 6.371 | 5.495 | 5.358 | 5.197 | 4.994 | 4.762 | 4.533 | 3.477 | 2.638 | 2.017 | 1.578 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Falling Short | 16.913 | 15.824 | 15.529 | 15.164 | 14.706 | 14.186 | 13.667 | 11.161 | 8.829 | 7.017 | 5.81 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Falling Short | 12.905 | 12.912 | 12.902 | 12.874 | 12.823 | 12.76 | 12.697 | 12.413 | 12.201 | 12.064 | 11.982 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Falling Short | 6.785 | 6.769 | 6.751 | 6.728 | 6.702 | 6.673 | 6.644 | 6.52 | 6.427 | 6.355 | 6.299 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 12.639 | 12.644 | 12.634 | 12.607 | 12.559 | 12.497 | 12.426 | 12.02 | 11.568 | 11.235 | 11.083 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 16.787 | 16.779 | 16.757 | 16.719 | 16.66 | 16.584 | 16.494 | 15.921 | 15.215 | 14.698 | 14.5 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Falling Short | 4.723 | 4.708 | 4.689 | 4.668 | 4.641 | 4.61 | 4.58 | 4.43 | 4.292 | 4.171 | 4.063 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Falling Short | 9.185 | 9.125 | 9.05 | 8.96 | 8.847 | 8.719 | 8.596 | 8.081 | 7.769 | 7.585 | 7.493 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Falling Short | 10.318 | 10.229 | 10.102 | 9.936 | 9.715 | 9.461 | 9.213 | 8.159 | 7.483 | 7.073 | 6.853 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 23.089 | 22.804 | 22.786 | 22.756 | 22.709 | 22.65 | 22.592 | 22.362 | 22.253 | 22.186 | 22.144 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Falling Short | 6.708 | 6.668 | 6.594 | 6.483 | 6.318 | 6.111 | 5.885 | 4.638 | 3.331 | 2.431 | 2.1 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Falling Short | 5.049 | 4.491 | 4.275 | 3.972 | 3.561 | 3.074 | 2.58 | 0.203 | -1.846 | -3.169 | -3.678 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Falling Short | 12.022 | 10.896 | 10.744 | 10.54 | 10.269 | 9.957 | 9.649 | 8.266 | 7.221 | 6.568 | 6.235 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 8.931 | 8.856 | 8.747 | 8.605 | 8.412 | 8.184 | 7.956 | 6.949 | 6.255 | 5.834 | 5.645 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 14.279 | 14.142 | 13.962 | 13.741 | 13.455 | 13.128 | 12.807 | 11.511 | 10.803 | 10.376 | 10.135 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Falling Short | 4.093 | 3.617 | 3.52 | 3.402 | 3.255 | 3.094 | 2.934 | 2.135 | 1.369 | 0.695 | 0.079 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Falling Short | 18.277 | 18.188 | 18.057 | 17.879 | 17.643 | 17.372 | 17.101 | 15.87 | 14.92 | 14.31 | 14.027 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Falling Short | 18.836 | 18.809 | 18.775 | 18.733 | 18.681 | 18.623 | 18.565 | 18.285 | 18.037 | 17.805 | 17.585 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Falling Short | 8.046 | 7.989 | 7.898 | 7.779 | 7.612 | 7.415 | 7.222 | 6.379 | 5.829 | 5.501 | 5.336 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Falling Short | 8.941 | 8.902 | 8.851 | 8.787 | 8.704 | 8.608 | 8.499 | 7.86 | 7.122 | 6.508 | 6.11 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Falling Short | 1.573 | 1.503 | 1.381 | 1.203 | 0.964 | 0.687 | 0.413 | -0.725 | -1.409 | -1.897 | -2.242 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Falling Short | 5.627 | 5.229 | 4.771 | 4.29 | 3.695 | 3.019 | 2.357 | -0.443 | -2.224 | -3.319 | -3.85 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Falling Short | 10.426 | 10.231 | 9.231 | 8.918 | 8.528 | 8.089 | 7.65 | 5.633 | 3.897 | 2.606 | 1.765 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Falling Short | 15.503 | 15.134 | 15.062 | 14.969 | 14.85 | 14.711 | 14.557 | 13.674 | 12.662 | 11.82 | 11.253 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Falling Short | 10.743 | 9.433 | 9.324 | 9.155 | 8.919 | 8.64 | 8.359 | 7.034 | 5.924 | 5.192 | 4.814 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Falling Short | 8.009 | 7.812 | 7.545 | 7.211 | 6.79 | 6.311 | 5.837 | 3.841 | 2.614 | 1.866 | 1.521 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Falling Short | 22.787 | 22.596 | 22.348 | 22.064 | 21.686 | 21.245 | 20.821 | 19 | 17.802 | 17.131 | 16.816 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Falling Short | 5.019 | 4.862 | 4.657 | 4.398 | 4.08 | 3.724 | 3.365 | 1.766 | 0.522 | -0.451 | -1.166 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Falling Short | 11.76 | 11.678 | 11.564 | 11.424 | 11.246 | 11.047 | 10.85 | 10.099 | 9.745 | 9.509 | 9.35 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Falling Short | 18.228 | 18.175 | 18.091 | 17.974 | 17.815 | 17.628 | 17.439 | 16.559 | 15.858 | 15.384 | 15.138 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Falling Short | 9.265 | 9.288 | 7.853 | 7.836 | 7.795 | 7.735 | 7.664 | 7.19 | 6.581 | 6.141 | 5.965 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Falling Short | 27.393 | 27.409 | 27.413 | 27.399 | 27.367 | 27.315 | 27.242 | 26.641 | 25.765 | 25.139 | 24.956 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Falling Short | 14.36 | 13.885 | 13.896 | 13.892 | 13.87 | 13.835 | 13.795 | 13.606 | 13.469 | 13.329 | 13.204 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Falling Short | 2.752 | 2.584 | 2.332 | 1.982 | 1.504 | 0.913 | 0.258 | -3.603 | -7.966 | -11.015 | -12.118 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Falling Short | 17.932 | 17.951 | 17.96 | 17.958 | 17.947 | 17.928 | 17.904 | 17.718 | 17.438 | 17.118 | 16.785 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 7.441 | 7.043 | 6.792 | 6.489 | 6.112 | 5.691 | 5.282 | 3.501 | 2.179 | 1.22 | 0.556 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Falling Short | 2.982 | 2.973 | 2.935 | 2.869 | 2.771 | 2.652 | 2.532 | 2.043 | 1.727 | 1.49 | 1.32 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Falling Short | 14.293 | 14.111 | 13.881 | 13.605 | 13.257 | 12.864 | 12.473 | 10.651 | 9.19 | 8.19 | 7.597 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Falling Short | 15.147 | 12.735 | 12.738 | 12.72 | 12.668 | 12.593 | 12.508 | 12.019 | 11.514 | 11.16 | 11.038 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Falling Short | 8.589 | 8.038 | 7.75 | 7.411 | 6.979 | 6.489 | 6.007 | 3.783 | 1.951 | 0.59 | -0.376 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Falling Short | 18.359 | 18.298 | 18.222 | 18.131 | 18.016 | 17.887 | 17.76 | 17.164 | 16.652 | 16.228 | 15.858 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Falling Short | 8.541 | 8.335 | 8.053 | 7.699 | 7.245 | 6.733 | 6.232 | 4.143 | 2.813 | 1.979 | 1.486 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Falling Short | 4.113 | 3.522 | 3.237 | 2.883 | 2.439 | 1.937 | 1.435 | -0.88 | -2.822 | -4.245 | -5.1 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Falling Short | 2.942 | 2.783 | 2.585 | 2.359 | 2.076 | 1.753 | 1.44 | 0.144 | -0.617 | -1.083 | -1.33 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Falling Short | 8.489 | 8.483 | 8.467 | 23.839 | 23.797 | 23.742 | 23.675 | 23.231 | 22.649 | 22.23 | 22.083 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Falling Short | 21.019 | 20.747 | 20.742 | 20.731 | 20.715 | 20.697 | 20.679 | 20.596 | 20.513 | 20.457 | 20.415 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Falling Short | 19.151 | 19.103 | 19.022 | 18.908 | 18.752 | 18.571 | 18.39 | 17.587 | 16.91 | 16.416 | 16.117 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Falling Short | 16.589 | 16.657 | 16.72 | 16.776 | 16.828 | 16.874 | 16.916 | 17.063 | 17.134 | 17.16 | 17.171 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Falling Short | 14.622 | 14.678 | 14.715 | 14.733 | 14.724 | 14.694 | 14.657 | 14.398 | 14.077 | 13.839 | 13.731 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Falling Short | 1.29 | 1.284 | 1.242 | 1.153 | 20.906 | 20.701 | 20.436 | 18.575 | 16.129 | 14.374 | 13.829 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Falling Short | 7.677 | 7.481 | 7.239 | 6.953 | 6.603 | 6.213 | 5.833 | 4.243 | 3.235 | 2.532 | 2.023 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Falling Short | 6.868 | 6.705 | 6.483 | 6.203 | 5.841 | 5.427 | 5.019 | 3.209 | 1.788 | 0.832 | 0.312 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Falling Short | 17.704 | 17.64 | 17.559 | 17.46 | 17.337 | 17.198 | 17.057 | 16.38 | 15.8 | 15.374 | 15.108 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Falling Short | 6.607 | 6.519 | 6.404 | 6.263 | 6.084 | 5.879 | 5.673 | 4.751 | 4.054 | 3.547 | 3.216 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 6.899 | 6.714 | 6.497 | 6.251 | 5.949 | 5.613 | 5.282 | 3.774 | 2.596 | 1.773 | 1.231 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Falling Short | 18.62 | 18.615 | 18.601 | 18.576 | 18.538 | 18.491 | 18.441 | 18.191 | 17.961 | 17.799 | 17.724 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Falling Short | 6.999 | 6.887 | 6.737 | 6.56 | 6.333 | 6.076 | 5.824 | 4.827 | 4.258 | 3.869 | 3.613 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Falling Short | 2.79 | 2.783 | 2.774 | 2.761 | 2.743 | 2.722 | 2.702 | 2.608 | 2.532 | 2.489 | 2.468 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Falling Short | 9.132 | 8.795 | 8.7 | 8.583 | 8.44 | 8.274 | 8.101 | 7.201 | 6.298 | 5.539 | 4.994 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Falling Short | 15.048 | 14.954 | 14.833 | 14.684 | 14.496 | 14.286 | 14.081 | 13.205 | 12.614 | 12.224 | 11.958 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Falling Short | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Falling Short | 21.25 | 21.184 | 21.098 | 20.993 | 20.858 | 20.703 | 20.552 | 19.893 | 19.44 | 19.165 | 19.031 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Falling Short | 8.444 | 8.333 | 8.185 | 8.008 | 7.782 | 7.528 | 7.278 | 6.257 | 5.648 | 5.214 | 4.893 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Falling Short | 14.175 | 14.063 | 13.919 | 13.744 | 13.525 | 13.28 | 13.035 | 11.94 | 11.106 | 10.502 | 10.112 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Falling Short | 33.322 | 32.977 | 32.97 | 32.955 | 32.933 | 32.905 | 32.878 | 32.764 | 32.686 | 32.64 | 32.611 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Falling Short | 4.217 | 3.684 | 3.447 | 3.136 | 2.727 | 2.261 | 1.812 | -0.015 | -1.104 | -1.737 | -2.082 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Falling Short | 14.785 | 14.054 | 13.801 | 13.51 | 13.18 | 12.822 | 12.447 | 10.403 | 7.974 | 5.835 | 4.188 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Falling Short | 11.862 | 11.74 | 11.583 | 11.387 | 11.143 | 10.868 | 10.584 | 9.205 | 7.999 | 7.084 | 6.504 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Falling Short | 14.914 | 14.868 | 14.81 | 14.739 | 14.652 | 14.553 | 14.448 | 13.902 | 13.341 | 12.866 | 12.516 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 24.411 | 22.711 | 22.563 | 22.381 | 22.151 | 21.891 | 21.64 | 20.633 | 20.062 | 19.73 | 19.564 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Falling Short | 5.126 | 4.618 | 4.326 | 3.994 | 3.612 | 3.199 | 2.783 | 0.87 | -0.732 | -2.105 | -3.257 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Falling Short | 1.373 | 0.78 | 0.502 | 0.178 | -0.221 | -0.666 | -1.099 | -2.937 | -4.188 | -5.099 | -5.797 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Falling Short | 3.332 | 3.293 | 1.963 | 1.906 | 1.837 | 1.757 | 1.676 | 1.273 | 0.906 | 0.613 | 0.409 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Falling Short | 8.826 | 8.455 | 10.291 | 10.092 | 9.827 | 9.52 | 9.217 | 7.891 | 6.997 | 6.453 | 6.186 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Falling Short | 7.162 | 7.161 | 7.133 | 7.074 | 6.982 | 6.871 | 6.757 | 6.248 | 5.85 | 5.551 | 5.347 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Falling Short | 32.707 | 31.327 | 31.272 | 31.205 | 31.125 | 31.033 | 30.933 | 30.463 | 30.094 | 29.821 | 29.693 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Falling Short | 12.213 | 12.128 | 12.011 | 11.858 | 11.662 | 11.439 | 11.222 | 10.344 | 9.868 | 9.582 | 9.416 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Falling Short | 8.956 | 8.335 | 8.194 | 8.044 | 7.86 | 7.655 | 7.455 | 6.679 | 6.309 | 6.088 | 5.949 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Falling Short | 8.7 | 8.731 | 8.751 | 8.759 | 8.755 | 8.741 | 8.72 | 8.572 | 8.355 | 8.145 | 7.989 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Falling Short | 13.929 | 13.902 | 13.853 | 13.774 | 13.665 | 13.539 | 13.413 | 12.838 | 12.398 | 12.126 | 11.987 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 14.531 | 14.429 | 14.296 | 14.119 | 13.89 | 13.609 | 13.279 | 11.056 | 8.154 | 5.888 | 4.71 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 18.67 | 18.499 | 18.311 | 18.1 | 17.868 | 17.622 | 17.374 | 16.14 | 14.956 | 13.816 | 12.709 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Falling Short | 5.465 | 4.421 | 4.154 | 3.856 | 3.523 | 3.168 | 2.807 | 0.979 | -0.878 | -2.567 | -4.038 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Falling Short | 5.607 | 4.317 | 3.679 | 2.931 | 2.041 | 1.066 | 0.119 | -4.035 | -7.422 | -10.246 | -12.558 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Falling Short | 13.373 | 12.709 | 12.53 | 12.338 | 12.096 | 11.822 | 11.559 | 10.445 | 9.68 | 9.175 | 8.827 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Falling Short | 15.842 | 15.166 | 14.996 | 14.775 | 14.485 | 14.151 | 13.825 | 12.49 | 11.681 | 11.185 | 10.923 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Falling Short | 9.937 | 9.867 | 9.752 | 9.591 | 9.374 | 9.122 | 8.876 | 7.866 | 7.275 | 6.927 | 6.749 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Falling Short | 10.988 | 10.978 | 10.964 | 10.943 | 10.918 | 10.889 | 10.858 | 10.657 | 10.406 | 10.133 | 9.857 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Falling Short | 21.433 | 21.371 | 21.291 | 21.19 | 21.067 | 20.931 | 20.795 | 20.168 | 19.592 | 19.074 | 18.634 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Falling Short | 16.14 | 16.21 | 16.27 | 16.317 | 16.352 | 16.379 | 16.403 | 16.455 | 16.427 | 16.392 | 16.362 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 10.821 | 10.62 | 10.367 | 10.067 | 9.697 | 9.285 | 8.882 | 7.157 | 5.936 | 5.046 | 4.416 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 21.886 | 21.855 | 21.817 | 21.771 | 21.714 | 21.652 | 21.588 | 21.285 | 21.015 | 20.763 | 20.528 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Falling Short | 2.618 | 2.517 | 2.364 | 2.158 | 1.886 | 1.575 | 1.27 | 0.068 | -0.577 | -0.994 | -1.262 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Falling Short | 6.605 | 6.6 | 6.593 | 6.582 | 6.567 | 6.549 | 6.532 | 6.46 | 6.411 | 6.383 | 6.367 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Falling Short | 7.94 | 7.27 | 7.172 | 7.049 | 6.889 | 6.705 | 6.52 | 5.748 | 5.272 | 4.944 | 4.751 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Falling Short | 12.993 | 12.669 | 12.246 | 11.72 | 11.059 | 10.307 | 9.551 | 6.066 | 3.261 | 1.312 | 0.28 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Falling Short | 10.419 | 9.055 | 8.416 | 8.172 | 7.849 | 7.473 | 7.092 | 5.345 | 3.985 | 3.098 | 2.713 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Falling Short | 3.89 | 3.734 | 3.56 | 3.362 | 3.135 | 2.886 | 2.631 | 1.347 | 0.11 | -0.917 | -1.69 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Falling Short | 3.853 | 3.753 | 3.649 | 3.54 | 3.425 | 3.306 | 3.185 | 2.555 | 1.9 | 1.25 | 0.623 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Falling Short | 3.048 | 2.725 | 23.922 | 23.783 | 23.598 | 23.377 | 23.131 | 21.654 | 19.911 | 18.561 | 17.822 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Falling Short | 13.921 | 13.528 | 13.357 | 13.14 | 12.857 | 12.531 | 12.22 | 10.939 | 10.18 | 9.765 | 9.573 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Falling Short | 4.37 | 4.27 | 4.151 | 4.015 | 3.853 | 3.676 | 3.506 | 2.789 | 2.316 | 1.957 | 1.663 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Falling Short | 3.585 | 3.488 | 3.375 | 3.247 | 3.095 | 2.925 | 2.755 | 1.936 | 1.22 | 0.667 | 0.28 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 13.964 | 13.471 | 13.323 | 13.114 | 12.832 | 12.505 | 12.19 | 10.815 | 9.845 | 9.25 | 8.913 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Falling Short | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Falling Short | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Falling Short | 17.573 | 17.099 | 16.997 | 16.868 | 16.7 | 16.51 | 16.322 | 15.526 | 14.989 | 14.6 | 14.32 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Falling Short | 15.21 | 14.14 | 14.061 | 13.969 | 13.86 | 13.738 | 13.611 | 12.924 | 12.204 | 11.594 | 11.14 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Falling Short | 10.87 | 10.782 | 10.66 | 10.508 | 10.308 | 10.076 | 9.84 | 8.779 | 7.983 | 7.451 | 7.196 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Falling Short | 13.019 | 12.842 | 12.633 | 12.397 | 12.107 | 11.782 | 11.461 | 9.995 | 8.864 | 8.056 | 7.516 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Falling Short | 10.407 | 9.622 | 9.47 | 9.282 | 9.054 | 8.8 | 8.546 | 7.409 | 6.53 | 5.828 | 5.297 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Falling Short | 11.224 | 11.181 | 11.109 | 11.011 | 10.874 | 10.712 | 10.542 | 9.734 | 9.05 | 8.575 | 8.355 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Falling Short | 18.617 | 17.836 | 17.84 | 17.824 | 17.788 | 17.738 | 17.683 | 17.376 | 17.057 | 16.824 | 16.696 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Falling Short | 16.42 | 16.255 | 16.043 | 15.783 | 15.454 | 15.07 | 14.673 | 12.683 | 10.834 | 9.489 | 8.761 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | 8.91 | 8.842 | 8.748 | 8.631 | 8.477 | 8.298 | 8.126 | 7.392 | 6.925 | 6.665 | 6.557 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Falling Short | 12.71 | 12.4 | 10.741 | 10.519 | 10.224 | 9.879 | 9.527 | 7.79 | 6.089 | 4.79 | 4.028 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Falling Short | 23.071 | 13.618 | 6.659 | 6.417 | 6.115 | 5.771 | 5.417 | 3.68 | 2.034 | 0.753 | -0.075 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Falling Short | 2.564 | 2.013 | 1.691 | -0.47 | -0.93 | -1.453 | -1.957 | -4.091 | -5.484 | -6.41 | -7.043 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Falling Short | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Falling Short | 5.424 | 5.316 | 5.194 | 5.057 | 4.9 | 4.728 | 4.549 | 3.613 | 2.654 | 1.83 | 1.195 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Falling Short | 12.02 | 11.263 | 11.069 | 10.833 | 10.544 | 10.224 | 9.902 | 8.313 | 6.641 | 5.211 | 4.14 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 7.877 | 6.278 | 6.261 | 6.214 | 6.133 | 6.03 | 5.922 | 5.335 | 4.737 | 4.334 | 4.153 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 27.936 | 27.948 | 27.958 | 27.968 | 27.977 | 27.985 | 27.992 | 28.019 | 28.032 | 28.037 | 28.039 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Falling Short | 19.949 | 19.006 | 18.823 | 18.599 | 18.323 | 18.016 | 17.717 | 16.473 | 15.684 | 15.12 | 14.701 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Falling Short | 8.073 | 7.359 | 7.423 | 7.443 | 7.41 | 7.323 | 7.186 | 5.933 | 4.01 | 2.618 | 2.202 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Falling Short | 3.989 | 3.804 | 3.68 | 3.553 | 3.42 | 3.284 | 3.144 | 2.389 | 1.553 | 0.662 | -0.254 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Falling Short | 14.394 | 14.247 | 14.061 | 13.84 | 13.566 | 13.257 | 12.958 | 11.781 | 11.2 | 10.85 | 10.626 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Falling Short | 2.466 | 2.238 | 1.967 | 1.651 | 1.269 | 0.846 | 0.421 | -1.612 | -3.362 | -4.689 | -5.599 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Falling Short | 8.77 | 7.934 | 7.769 | 7.566 | 7.312 | 7.028 | 6.753 | 5.584 | 4.78 | 4.244 | 3.89 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 25.198 | 24.78 | 24.528 | 24.222 | 23.845 | 23.424 | 23.008 | 21.179 | 19.85 | 18.903 | 18.271 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Falling Short | 11.719 | 11.638 | 11.499 | 11.306 | 11.042 | 10.733 | 10.429 | 9.123 | 8.162 | 7.521 | 7.181 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Falling Short | 11.308 | 11.133 | 10.911 | 10.645 | 10.315 | 9.945 | 9.586 | 8.042 | 6.953 | 6.192 | 5.65 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Falling Short | 13.803 | 13.566 | 13.627 | 13.672 | 13.704 | 13.724 | 13.741 | 13.763 | 13.717 | 13.662 | 13.616 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Falling Short | 32.7 | 32.378 | 32.015 | 31.616 | 31.15 | 30.643 | 30.143 | 27.958 | 26.365 | 25.1 | 24.066 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Falling Short | 9.695 | 8.142 | 8.099 | 8.027 | 7.918 | 7.781 | 7.637 | 6.928 | 6.339 | 5.955 | 5.817 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Falling Short | 8.255 | 7.592 | 7.386 | 7.133 | 6.826 | 6.484 | 6.146 | 4.745 | 3.918 | 3.343 | 2.944 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Falling Short | 30.729 | 30.736 | 30.741 | 30.746 | 30.75 | 30.753 | 30.756 | 30.767 | 30.773 | 30.773 | 30.773 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Falling Short | 8.998 | 9.001 | 24.389 | 24.359 | 24.312 | 24.253 | 24.194 | 23.948 | 23.772 | 23.629 | 23.521 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Falling Short | 8.752 | 7.208 | 22.032 | 21.818 | 21.541 | 21.225 | 20.918 | 19.596 | 18.731 | 18.219 | 17.959 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Falling Short | 9.46 | 9.266 | 9.041 | 8.778 | 8.466 | 8.123 | 7.775 | 6.026 | 4.343 | 3.001 | 2.026 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Falling Short | 12.141 | 12.075 | 11.99 | 11.89 | 11.765 | 11.624 | 11.49 | 10.986 | 10.772 | 10.663 | 10.603 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Falling Short | 20.218 | 19.694 | 19.65 | 19.585 | 19.494 | 19.385 | 19.277 | 18.836 | 18.612 | 18.469 | 18.388 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Falling Short | 11 | 10.798 | 10.541 | 10.243 | 9.853 | 9.401 | 8.955 | 6.992 | 5.594 | 4.731 | 4.341 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Falling Short | 12.266 | 11.952 | 11.787 | 11.582 | 11.334 | 11.057 | 10.785 | 9.709 | 9.169 | 8.808 | 8.573 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Falling Short | 10.928 | 10.449 | 10.268 | 10.037 | 9.74 | 9.403 | 9.076 | 7.779 | 7.106 | 6.736 | 6.534 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 4.859 | 4.862 | 4.859 | 4.847 | 4.826 | 4.799 | 4.772 | 4.626 | 4.484 | 4.387 | 4.338 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 4.702 | 4.705 | 4.698 | 4.681 | 4.652 | 4.614 | 4.571 | 4.308 | 3.984 | 3.757 | 3.663 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 7.533 | 7.5 | 7.451 | 7.384 | 7.294 | 7.19 | 7.088 | 6.648 | 6.325 | 6.125 | 6.02 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 7.393 | 7.362 | 7.316 | 7.252 | 7.167 | 7.069 | 6.975 | 6.563 | 6.246 | 6.043 | 5.92 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Falling Short | 13.166 | 13.011 | 12.824 | 12.603 | 12.337 | 12.044 | 11.759 | 10.604 | 9.942 | 9.47 | 9.097 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 22.142 | 21.965 | 21.75 | 21.512 | 21.208 | 20.863 | 20.527 | 19.04 | 17.942 | 17.188 | 16.696 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Falling Short | 29.718 | 28.795 | 28.73 | 28.662 | 28.589 | 28.512 | 28.431 | 27.982 | 27.471 | 26.977 | 26.537 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Falling Short | 5.803 | 5.393 | 5.38 | 5.363 | 5.34 | 5.314 | 5.288 | 5.171 | 5.076 | 5.008 | 4.959 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Falling Short | 11.56 | 11.567 | 11.562 | 11.541 | 11.505 | 11.458 | 11.409 | 11.194 | 11.043 | 10.92 | 10.833 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Leading the Way | 5.477 | 4.966 | 4.183 | 3.31 | 2.809 | 2.508 | 1.89 | -4.757 | -9.662 | -12.875 | -12.185 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Leading the Way | 11.964 | 10.888 | 8.616 | 7.497 | 6.719 | 6.124 | 5.241 | -5.37 | -13.177 | -18.601 | -17.617 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 7.957 | 7.486 | 8.77 | 7.974 | 7.462 | 7.062 | 6.375 | -0.147 | -4.873 | -8.053 | -7.745 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Leading the Way | 6.18 | 5.824 | 5.225 | 4.531 | 4.118 | 3.823 | 3.222 | -3.182 | -7.975 | -11.302 | -10.738 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Leading the Way | 26.375 | 26.377 | 26.378 | 26.379 | 26.38 | 26.381 | 26.382 | 26.386 | 26.389 | 26.391 | 26.394 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Leading the Way | 2.809 | 2.729 | 2.567 | 2.376 | 2.282 | 2.223 | 2.065 | -0.118 | -1.769 | -2.873 | -2.588 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Leading the Way | 4.072 | 4.043 | 4.005 | 3.967 | 3.932 | 3.898 | 3.849 | 3.516 | 3.289 | 3.131 | 3.1 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Leading the Way | 4.586 | 4.378 | 4.085 | 3.755 | 3.498 | 3.272 | 2.946 | -0.335 | -2.978 | -4.912 | -5.186 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Leading the Way | 8.492 | 8.304 | 8.007 | 7.683 | 7.502 | 7.396 | 7.155 | 3.707 | 0.978 | -0.985 | -0.733 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Leading the Way | 12.467 | 12.11 | 11.549 | 10.961 | 10.542 | 10.181 | 9.582 | 4.906 | 1.794 | 0.039 | 0.55 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Leading the Way | 4.98 | 4.317 | 3.751 | 3.147 | 2.722 | 2.365 | 1.718 | -5.45 | -11.054 | -15.212 | -14.982 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Leading the Way | 11.843 | 11.209 | 10.784 | 10.294 | 10.009 | 9.804 | 9.328 | 3.761 | -0.436 | -3.393 | -2.906 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Leading the Way | 7.509 | 7.027 | 6.361 | 5.635 | 5.129 | 4.685 | 3.997 | -1.75 | -5.944 | -8.613 | -8.762 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Leading the Way | 6.742 | 6.035 | 5.558 | 5.024 | 4.705 | 4.451 | 3.94 | -1.126 | -4.88 | -7.417 | -7.104 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 13.286 | 13.107 | 12.807 | 12.45 | 12.151 | 11.841 | 10.881 | 5.35 | 2.708 | 1.356 | 1.537 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 16.82 | 16.724 | 16.591 | 16.446 | 16.317 | 16.197 | 16.055 | 14.801 | 13.968 | 13.695 | 14.006 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Leading the Way | 9.699 | 8.747 | 8.516 | 8.231 | 8.019 | 7.81 | 7.376 | 2.473 | -1.233 | -3.772 | -3.334 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Leading the Way | 10.897 | 10.204 | 9.74 | 9.225 | 8.842 | 8.509 | 7.897 | 1.844 | -2.694 | -5.956 | -5.609 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Leading the Way | 16.096 | 15.862 | 15.517 | 15.147 | 14.898 | 14.699 | 14.298 | 10.244 | 7.209 | 5.086 | 5.39 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Leading the Way | 10.404 | 10.297 | 10.128 | 9.914 | 9.706 | 9.475 | 9.14 | 6.216 | 4.14 | 3.057 | 3.051 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Leading the Way | 21.552 | 21.218 | 20.76 | 20.268 | 19.858 | 19.472 | 18.892 | 13.462 | 9.282 | 6.32 | 6.126 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 17.766 | 17.59 | 17.338 | 17.057 | 16.837 | 16.632 | 16.298 | 13.014 | 10.345 | 8.246 | 7.998 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Leading the Way | 13.182 | 12.325 | 11.479 | 10.549 | 9.948 | 9.48 | 8.672 | 1.072 | -4.448 | -8.173 | -7.756 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Leading the Way | 7.86 | 7.293 | 7.12 | 6.932 | 6.836 | 6.787 | 6.651 | 4.25 | 2.425 | 1.145 | 1.522 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Leading the Way | 9.063 | 8.536 | 7.698 | 6.751 | 6.141 | 5.702 | 4.932 | -2.966 | -8.696 | -12.211 | -11.642 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Leading the Way | 7.869 | 7.154 | 6.463 | 5.788 | 5.289 | 4.895 | 4.306 | -0.911 | -4.417 | -6.67 | -6.195 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Leading the Way | 8.047 | 7.643 | 7.056 | 6.429 | 6.011 | 5.7 | 5.125 | -0.776 | -4.987 | -7.729 | -7.131 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Leading the Way | 9.132 | 8.876 | 8.467 | 8 | 7.643 | 7.328 | 6.781 | 1.4 | -2.568 | -5.456 | -5.173 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Leading the Way | 3.92 | 3.57 | 2.98 | 2.287 | 1.845 | 1.485 | 0.768 | -6.556 | -12.008 | -15.727 | -15.159 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Leading the Way | 7.8 | 7.365 | 6.763 | 6.106 | 5.599 | 5.157 | 4.504 | -1.599 | -6.386 | -10.051 | -10.429 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Leading the Way | 10.349 | 10.14 | 10.194 | 10.221 | 10.289 | 10.365 | 10.361 | 8.523 | 7.121 | 6.147 | 6.788 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Leading the Way | 6.446 | 5.496 | 5.21 | 4.92 | 4.701 | 4.503 | 4.166 | 0.787 | -1.733 | -3.519 | -3.363 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Leading the Way | 17.021 | 15.541 | 14.633 | 13.641 | 12.97 | 12.433 | 11.568 | 3.275 | -2.766 | -6.625 | -6.119 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Leading the Way | 12.987 | 12.938 | 12.823 | 12.689 | 12.629 | 12.601 | 12.499 | 10.799 | 9.571 | 8.74 | 9.05 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Leading the Way | 6.783 | 6.75 | 6.704 | 6.655 | 6.621 | 6.593 | 6.55 | 6.163 | 5.885 | 5.694 | 5.706 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 12.717 | 12.68 | 12.587 | 12.463 | 12.4 | 12.36 | 12.231 | 10.096 | 8.49 | 7.421 | 7.765 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 16.819 | 16.731 | 16.585 | 16.402 | 16.288 | 16.198 | 16.011 | 13.704 | 12.013 | 10.985 | 11.197 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Leading the Way | 4.763 | 4.697 | 4.6 | 4.499 | 4.454 | 4.442 | 4.385 | 3.31 | 2.424 | 1.759 | 1.83 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Leading the Way | 9.158 | 8.977 | 8.709 | 8.424 | 8.256 | 8.129 | 7.885 | 5.392 | 3.568 | 2.353 | 2.574 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Leading the Way | 10.332 | 10.088 | 9.692 | 9.254 | 8.969 | 8.735 | 8.267 | 3.01 | -0.859 | -3.549 | -2.979 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 23.143 | 22.855 | 22.803 | 22.741 | 22.711 | 22.69 | 22.581 | 21.122 | 20.044 | 19.297 | 19.629 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Leading the Way | 6.79 | 6.639 | 6.353 | 6.021 | 5.792 | 5.575 | 5.152 | 0.488 | -2.86 | -4.856 | -4.242 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Leading the Way | 5.08 | 4.152 | 3.353 | 2.444 | 1.799 | 1.247 | 0.371 | -7.385 | -12.787 | -15.926 | -15.282 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Leading the Way | 12.053 | 10.714 | 10.208 | 9.642 | 9.268 | 8.963 | 8.393 | 1.519 | -3.571 | -7.118 | -6.422 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 8.941 | 8.794 | 8.538 | 8.267 | 8.043 | 7.822 | 7.415 | 3.578 | 0.9 | -0.89 | -0.521 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 14.26 | 13.944 | 13.448 | 12.921 | 12.565 | 12.267 | 11.646 | 5.242 | 0.458 | -2.973 | -2.448 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Leading the Way | 4.28 | 3.781 | 3.614 | 3.437 | 3.324 | 3.244 | 3.099 | 0.397 | -1.787 | -3.504 | -3.328 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Leading the Way | 18.299 | 18.056 | 17.662 | 17.209 | 16.879 | 16.594 | 16.064 | 10.426 | 6.224 | 3.295 | 3.71 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Leading the Way | 18.909 | 18.888 | 18.838 | 18.773 | 18.743 | 18.726 | 18.653 | 17.446 | 16.486 | 15.752 | 15.877 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Leading the Way | 8.108 | 7.887 | 7.531 | 7.163 | 6.929 | 6.76 | 6.427 | 2.975 | 0.606 | -0.894 | -0.509 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Leading the Way | 9.065 | 9.04 | 8.98 | 8.905 | 8.838 | 8.77 | 8.65 | 7.339 | 6.371 | 5.769 | 5.807 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Leading the Way | 1.673 | 1.396 | 0.918 | 0.352 | 0.026 | -0.18 | -0.65 | -6.421 | -10.7 | -13.692 | -13.026 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Leading the Way | 5.409 | 4.614 | 3.542 | 2.593 | 1.852 | 1.167 | 0.119 | -7.774 | -13.161 | -16.5 | -15.989 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Leading the Way | 10.527 | 9.919 | 8.309 | 7.39 | 6.789 | 6.351 | 5.635 | -1.769 | -7.314 | -11.015 | -10.686 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Leading the Way | 15.65 | 15.312 | 15.238 | 15.137 | 15.045 | 14.944 | 14.773 | 12.988 | 11.649 | 10.795 | 10.85 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Leading the Way | 10.875 | 9.346 | 8.875 | 8.34 | 8.013 | 7.773 | 7.253 | -0.434 | -6.223 | -10.317 | -9.339 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Leading the Way | 7.979 | 7.462 | 6.67 | 5.796 | 5.202 | 4.722 | 3.888 | -3.788 | -9.259 | -12.909 | -12.506 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Leading the Way | 22.668 | 22.127 | 21.352 | 20.622 | 20.089 | 19.626 | 18.9 | 12.968 | 9.114 | 6.797 | 7.242 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Leading the Way | 5.176 | 4.829 | 4.29 | 3.682 | 3.292 | 3.003 | 2.472 | -3.048 | -7.21 | -10.107 | -9.849 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Leading the Way | 11.789 | 11.498 | 11.06 | 10.592 | 10.334 | 10.176 | 9.852 | 6.435 | 3.934 | 2.252 | 2.579 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Leading the Way | 18.287 | 18.133 | 17.863 | 17.544 | 17.333 | 17.158 | 16.79 | 12.447 | 9.161 | 6.858 | 7.267 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Leading the Way | 9.367 | 9.333 | 7.789 | 7.648 | 7.576 | 7.525 | 7.383 | 5.16 | 3.521 | 2.525 | 2.893 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Leading the Way | 27.457 | 27.485 | 27.485 | 27.454 | 27.397 | 27.309 | 27.172 | 25.785 | 24.83 | 24.417 | 24.566 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Leading the Way | 14.569 | 14.052 | 13.965 | 13.856 | 13.856 | 13.914 | 13.89 | 12.536 | 11.516 | 10.856 | 11.266 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Leading the Way | 2.791 | 2.52 | 2.033 | 1.416 | 0.731 | -0.081 | -1.157 | -7.745 | -11.789 | -13.264 | -13.292 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Leading the Way | 18.152 | 18.26 | 18.35 | 18.429 | 18.51 | 18.594 | 18.663 | 18.51 | 18.337 | 18.19 | 18.415 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 7.469 | 6.852 | 6.244 | 5.593 | 5.111 | 4.695 | 4.045 | -1.67 | -5.726 | -8.438 | -8.091 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Leading the Way | 3.078 | 2.858 | 2.484 | 2.054 | 1.876 | 1.814 | 1.554 | -2.271 | -5.195 | -7.169 | -6.617 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Leading the Way | 14.299 | 13.921 | 13.363 | 12.773 | 12.325 | 11.914 | 11.311 | 6.13 | 2.576 | 0.329 | 0.491 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Leading the Way | 15.28 | 12.88 | 12.845 | 12.778 | 12.751 | 12.723 | 12.569 | 10.338 | 8.693 | 7.647 | 8.11 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Leading the Way | 8.655 | 7.767 | 6.944 | 6.115 | 5.563 | 5.128 | 4.371 | -3.798 | -9.957 | -14.284 | -13.851 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Leading the Way | 18.467 | 18.33 | 18.124 | 17.925 | 17.803 | 17.725 | 17.572 | 15.5 | 13.88 | 12.7 | 12.848 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Leading the Way | 8.567 | 7.858 | 6.831 | 5.738 | 5.043 | 4.554 | 3.727 | -4.458 | -10.318 | -14.186 | -13.704 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Leading the Way | 4.199 | 3.333 | 2.603 | 1.794 | 1.199 | 0.68 | -0.123 | -7.44 | -12.64 | -15.978 | -15.431 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Leading the Way | 2.902 | 2.43 | 1.791 | 1.178 | 0.761 | 0.461 | -0.024 | -4.468 | -7.558 | -9.551 | -9.212 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Leading the Way | 8.527 | 8.467 | 8.369 | 23.651 | 23.56 | 23.478 | 23.346 | 22.073 | 21.168 | 20.716 | 20.797 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Leading the Way | 21.053 | 20.758 | 20.718 | 20.672 | 20.647 | 20.636 | 20.609 | 19.764 | 19.071 | 18.547 | 18.696 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Leading the Way | 19.246 | 18.965 | 18.541 | 18.081 | 17.804 | 17.636 | 17.3 | 13.478 | 10.616 | 8.754 | 9.148 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Leading the Way | 16.736 | 16.875 | 17.007 | 17.131 | 17.249 | 17.362 | 17.468 | 17.856 | 18.17 | 18.435 | 18.733 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Leading the Way | 14.78 | 14.841 | 14.836 | 14.813 | 14.839 | 14.881 | 14.844 | 13.503 | 12.604 | 12.139 | 12.697 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Leading the Way | 1.398 | 1.334 | 1.129 | 0.807 | 20.451 | 20.155 | 19.577 | 13.351 | 8.784 | 6.156 | 6.611 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Leading the Way | 7.726 | 7.304 | 6.681 | 6.014 | 5.581 | 5.239 | 4.664 | -0.815 | -4.807 | -7.578 | -7.33 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Leading the Way | 6.859 | 6.384 | 5.684 | 4.938 | 4.413 | 3.969 | 3.289 | -2.54 | -6.514 | -8.874 | -8.319 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Leading the Way | 17.731 | 17.648 | 17.52 | 17.376 | 17.244 | 17.109 | 16.882 | 14.794 | 13.214 | 12.059 | 12.06 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Leading the Way | 6.719 | 6.555 | 6.296 | 6.026 | 5.841 | 5.688 | 5.426 | 2.347 | 0.104 | -1.449 | -1.085 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 6.867 | 6.52 | 6.044 | 5.567 | 5.185 | 4.831 | 4.322 | -0.003 | -3.125 | -5.304 | -5.362 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Leading the Way | 18.659 | 18.63 | 18.567 | 18.489 | 18.441 | 18.403 | 18.313 | 17.262 | 16.489 | 15.988 | 16.116 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Leading the Way | 7.024 | 6.712 | 6.244 | 5.76 | 5.458 | 5.236 | 4.825 | 0.909 | -1.862 | -3.674 | -3.268 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Leading the Way | 2.79 | 2.767 | 2.733 | 2.699 | 2.673 | 2.65 | 2.614 | 2.212 | 1.941 | 1.765 | 1.805 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Leading the Way | 9.278 | 8.906 | 8.716 | 8.491 | 8.349 | 8.235 | 7.991 | 5.101 | 2.855 | 1.305 | 1.475 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Leading the Way | 15.072 | 14.866 | 14.555 | 14.224 | 13.988 | 13.79 | 13.471 | 10.404 | 8.236 | 6.763 | 6.95 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Leading the Way | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Leading the Way | 21.251 | 21.053 | 20.764 | 20.47 | 20.272 | 20.119 | 19.847 | 16.821 | 14.559 | 12.985 | 13.211 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Leading the Way | 8.517 | 8.123 | 7.535 | 6.919 | 6.587 | 6.396 | 5.97 | 1.21 | -2.275 | -4.559 | -4.054 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Leading the Way | 14.229 | 13.914 | 13.443 | 12.929 | 12.62 | 12.394 | 11.986 | 7.824 | 4.772 | 2.79 | 3.081 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Leading the Way | 33.356 | 32.986 | 32.935 | 32.883 | 32.855 | 32.841 | 32.804 | 32.104 | 31.566 | 31.187 | 31.319 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Leading the Way | 4.291 | 3.32 | 2.431 | 1.482 | 0.848 | 0.393 | -0.35 | -7.023 | -11.722 | -14.675 | -14.137 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Leading the Way | 14.981 | 14.143 | 13.715 | 13.234 | 12.853 | 12.511 | 12.04 | 6.611 | 2.162 | -1.203 | -1.558 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Leading the Way | 11.999 | 11.852 | 11.61 | 11.338 | 11.104 | 10.878 | 10.463 | 5.479 | 1.614 | -1.257 | -0.944 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Leading the Way | 15.005 | 14.926 | 14.798 | 14.651 | 14.562 | 14.499 | 14.365 | 12.498 | 11.02 | 9.954 | 10.046 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 24.348 | 22.485 | 22.073 | 21.634 | 21.322 | 21.053 | 20.607 | 16.86 | 14.253 | 12.521 | 12.756 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Leading the Way | 5.262 | 4.699 | 4.245 | 3.736 | 3.361 | 3.026 | 2.47 | -3.102 | -7.588 | -11.045 | -11.214 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Leading the Way | 1.435 | 0.515 | -0.259 | -1.051 | -1.579 | -1.968 | -2.683 | -10.075 | -15.691 | -19.793 | -19.612 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Leading the Way | 3.37 | 3.325 | 1.97 | 1.894 | 1.828 | 1.763 | 1.67 | 1.039 | 0.63 | 0.406 | 0.402 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Leading the Way | 8.842 | 8.323 | 9.885 | 9.429 | 9.115 | 8.84 | 8.31 | 2.304 | -2.129 | -5.258 | -4.677 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Leading the Way | 7.268 | 7.029 | 6.616 | 6.129 | 5.942 | 5.89 | 5.576 | 0.221 | -3.926 | -6.862 | -6.185 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Leading the Way | 32.732 | 31.348 | 31.268 | 31.171 | 31.089 | 31.005 | 30.819 | 28.73 | 27.109 | 25.887 | 25.983 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Leading the Way | 12.231 | 12.07 | 11.788 | 11.46 | 11.235 | 11.04 | 10.617 | 5.956 | 2.419 | -0.175 | 0.254 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Leading the Way | 8.955 | 8.231 | 7.913 | 7.625 | 7.427 | 7.261 | 6.973 | 4.18 | 2.195 | 0.853 | 1.195 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Leading the Way | 8.84 | 8.874 | 8.863 | 8.828 | 8.855 | 8.904 | 8.894 | 7.901 | 7.141 | 6.656 | 6.988 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Leading the Way | 13.978 | 13.91 | 13.773 | 13.599 | 13.472 | 13.355 | 13.108 | 9.702 | 7.124 | 5.238 | 5.639 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 14.749 | 14.684 | 14.54 | 14.321 | 14.057 | 13.722 | 13.265 | 8.991 | 5.903 | 4.197 | 4.111 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 18.9 | 18.709 | 18.424 | 18.092 | 17.912 | 17.788 | 17.539 | 13.829 | 10.753 | 8.299 | 8.208 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Leading the Way | 5.649 | 4.542 | 4.133 | 3.684 | 3.36 | 3.085 | 2.689 | -1.708 | -5.263 | -7.984 | -8.222 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Leading the Way | 5.738 | 3.857 | 2.336 | 0.722 | -0.45 | -1.366 | -2.685 | -12.902 | -20.195 | -24.914 | -24.803 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Leading the Way | 13.328 | 12.404 | 11.855 | 11.365 | 11.018 | 10.748 | 10.332 | 6.624 | 3.951 | 2.174 | 2.341 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Leading the Way | 15.816 | 14.917 | 14.368 | 13.751 | 13.356 | 13.04 | 12.423 | 6.441 | 2.115 | -0.78 | -0.2 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Leading the Way | 9.972 | 9.772 | 9.418 | 9.001 | 8.722 | 8.492 | 8.018 | 3.292 | -0.078 | -2.341 | -1.797 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Leading the Way | 11.113 | 11.16 | 11.201 | 11.237 | 11.269 | 11.297 | 11.318 | 11.239 | 11.157 | 11.073 | 11.112 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Leading the Way | 21.511 | 21.389 | 21.19 | 20.961 | 20.823 | 20.723 | 20.533 | 18.651 | 17.244 | 16.3 | 16.444 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Leading the Way | 16.319 | 16.45 | 16.557 | 16.652 | 16.755 | 16.858 | 16.93 | 16.325 | 15.847 | 15.503 | 15.964 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 10.798 | 10.294 | 9.576 | 8.813 | 8.299 | 7.9 | 7.251 | 1.135 | -3.352 | -6.415 | -6.13 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 21.96 | 21.919 | 21.847 | 21.774 | 21.733 | 21.709 | 21.655 | 20.924 | 20.368 | 19.972 | 20.029 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Leading the Way | 2.66 | 2.319 | 1.772 | 1.163 | 0.797 | 0.545 | 0.015 | -5.744 | -9.937 | -12.757 | -11.982 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Leading the Way | 6.608 | 6.59 | 6.559 | 6.524 | 6.506 | 6.491 | 6.459 | 6.03 | 5.717 | 5.501 | 5.559 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Leading the Way | 8.113 | 7.254 | 6.868 | 6.488 | 6.256 | 6.123 | 5.87 | 2.927 | 0.799 | -0.556 | -0.164 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Leading the Way | 12.926 | 12.193 | 11.126 | 9.941 | 9.033 | 8.234 | 6.895 | -5.522 | -14.6 | -20.819 | -20.357 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Leading the Way | 10.481 | 8.899 | 7.877 | 7.22 | 6.773 | 6.4 | 5.715 | -1.392 | -6.641 | -10.142 | -9.551 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Leading the Way | 3.958 | 3.785 | 3.548 | 3.285 | 3.055 | 2.822 | 2.478 | -0.599 | -3.012 | -4.798 | -5.011 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Leading the Way | 3.961 | 3.909 | 3.846 | 3.778 | 3.714 | 3.649 | 3.569 | 3.005 | 2.512 | 2.088 | 1.848 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Leading the Way | 3.217 | 2.747 | 23.699 | 23.3 | 23.019 | 22.788 | 22.393 | 17.989 | 14.705 | 12.675 | 12.809 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Leading the Way | 13.875 | 13.289 | 12.813 | 12.321 | 11.937 | 11.594 | 11.107 | 7.881 | 5.897 | 4.844 | 5.114 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Leading the Way | 4.359 | 4.185 | 3.936 | 3.673 | 3.486 | 3.325 | 3.08 | 1.253 | -0.037 | -0.895 | -0.871 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Leading the Way | 3.596 | 3.459 | 3.269 | 3.07 | 2.899 | 2.73 | 2.493 | 0.635 | -0.705 | -1.619 | -1.702 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 14.012 | 13.294 | 12.778 | 12.196 | 11.793 | 11.469 | 10.858 | 3.848 | -1.3 | -4.939 | -4.332 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Leading the Way | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Leading the Way | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Leading the Way | 17.636 | 17.066 | 16.78 | 16.457 | 16.266 | 16.123 | 15.812 | 12.17 | 9.421 | 7.481 | 7.875 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Leading the Way | 15.29 | 14.238 | 14.156 | 14.059 | 13.965 | 13.865 | 13.712 | 12.336 | 11.298 | 10.572 | 10.499 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Leading the Way | 10.92 | 10.612 | 10.147 | 9.659 | 9.355 | 9.135 | 8.733 | 4.592 | 1.614 | -0.281 | 0.072 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Leading the Way | 12.985 | 12.656 | 12.203 | 11.756 | 11.406 | 11.091 | 10.618 | 6.561 | 3.681 | 1.705 | 1.722 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Leading the Way | 10.499 | 9.664 | 9.383 | 9.049 | 8.812 | 8.606 | 8.225 | 4.331 | 1.353 | -0.823 | -0.664 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Leading the Way | 11.27 | 11.065 | 10.733 | 10.353 | 10.136 | 9.988 | 9.657 | 5.854 | 2.994 | 1.086 | 1.391 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Leading the Way | 18.726 | 17.909 | 17.832 | 17.732 | 17.693 | 17.684 | 17.582 | 15.324 | 13.642 | 12.457 | 12.876 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Leading the Way | 16.479 | 16.083 | 15.484 | 14.831 | 14.377 | 13.983 | 13.332 | 7.259 | 2.922 | 0.248 | 0.537 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | 8.885 | 8.738 | 8.507 | 8.264 | 8.067 | 7.878 | 7.589 | 5.425 | 4.001 | 3.117 | 3.24 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Leading the Way | 12.791 | 12.166 | 10.011 | 9.258 | 8.798 | 8.45 | 7.822 | 0.848 | -4.167 | -7.263 | -6.367 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Leading the Way | 23.231 | 13.574 | 6.282 | 5.694 | 5.29 | 4.97 | 4.447 | -1.016 | -5.096 | -7.787 | -7.524 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Leading the Way | 2.478 | 1.539 | 0.625 | -2.059 | -2.666 | -3.151 | -3.972 | -11.247 | -16.465 | -19.988 | -19.657 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Leading the Way | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Leading the Way | 5.495 | 5.342 | 5.128 | 4.888 | 4.719 | 4.573 | 4.332 | 1.595 | -0.549 | -2.113 | -2.157 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Leading the Way | 12.108 | 11.123 | 10.583 | 9.989 | 9.587 | 9.272 | 8.782 | 3.919 | 0.354 | -1.933 | -1.538 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 7.997 | 6.283 | 6.067 | 5.801 | 5.671 | 5.595 | 5.377 | 1.817 | -0.875 | -2.67 | -2.124 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 27.962 | 27.985 | 28.008 | 28.03 | 28.05 | 28.07 | 28.089 | 28.17 | 28.234 | 28.288 | 28.337 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Leading the Way | 19.969 | 18.837 | 18.341 | 17.79 | 17.433 | 17.157 | 16.673 | 12.081 | 8.721 | 6.403 | 6.633 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Leading the Way | 8.359 | 7.722 | 7.815 | 7.835 | 7.811 | 7.715 | 7.496 | 4.59 | 2.697 | 2.031 | 2.715 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Leading the Way | 4.207 | 4.129 | 4.113 | 4.094 | 4.07 | 4.044 | 4.014 | 3.741 | 3.41 | 3.049 | 2.758 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Leading the Way | 14.377 | 13.941 | 13.296 | 12.613 | 12.206 | 11.929 | 11.34 | 5.147 | 0.426 | -2.936 | -2.574 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Leading the Way | 2.504 | 2.166 | 1.687 | 1.17 | 0.726 | 0.295 | -0.328 | -5.565 | -9.406 | -12.103 | -12.275 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Leading the Way | 8.834 | 7.848 | 7.455 | 7.053 | 6.727 | 6.451 | 6.081 | 3.186 | 1.3 | 0.125 | 0.262 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 25.227 | 24.62 | 24.035 | 23.38 | 22.91 | 22.506 | 21.8 | 14.808 | 9.656 | 6.036 | 6.382 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Leading the Way | 11.739 | 11.295 | 10.61 | 9.85 | 9.4 | 9.097 | 8.508 | 2.39 | -2.039 | -4.877 | -4.252 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Leading the Way | 11.301 | 10.856 | 10.204 | 9.504 | 9.041 | 8.675 | 8.017 | 1.369 | -3.579 | -7.092 | -6.856 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Leading the Way | 14.004 | 13.806 | 13.877 | 13.928 | 14.022 | 14.129 | 14.186 | 13.389 | 12.789 | 12.397 | 12.902 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Leading the Way | 32.708 | 32.239 | 31.593 | 30.933 | 30.434 | 29.986 | 29.269 | 22.613 | 17.438 | 13.498 | 13.36 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Leading the Way | 9.772 | 8.198 | 8.071 | 7.905 | 7.792 | 7.68 | 7.414 | 4.598 | 2.572 | 1.264 | 1.639 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Leading the Way | 8.288 | 7.507 | 7.065 | 6.562 | 6.21 | 5.91 | 5.356 | -0.211 | -4.404 | -7.487 | -7.246 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Leading the Way | 30.745 | 30.755 | 30.763 | 30.769 | 30.779 | 30.789 | 30.797 | 30.797 | 30.798 | 30.805 | 30.839 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Leading the Way | 9.108 | 9.046 | 24.311 | 24.147 | 24.079 | 24.063 | 23.94 | 21.879 | 20.234 | 19.062 | 19.381 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Leading the Way | 8.727 | 7.019 | 21.553 | 21.064 | 20.712 | 20.399 | 19.837 | 13.825 | 9.376 | 6.205 | 6.647 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Leading the Way | 9.528 | 9.239 | 8.847 | 8.425 | 8.055 | 7.701 | 7.203 | 2.787 | -0.578 | -3.057 | -3.402 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Leading the Way | 12.117 | 12.001 | 11.826 | 11.647 | 11.504 | 11.373 | 11.158 | 9.625 | 8.551 | 7.824 | 7.938 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Leading the Way | 20.275 | 19.72 | 19.579 | 19.404 | 19.319 | 19.257 | 19.032 | 16.078 | 13.802 | 12.136 | 12.542 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Leading the Way | 10.956 | 10.426 | 9.658 | 8.917 | 8.372 | 7.906 | 7.146 | 0.55 | -4.075 | -6.993 | -6.514 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Leading the Way | 12.297 | 11.832 | 11.408 | 10.933 | 10.623 | 10.389 | 9.918 | 4.741 | 0.802 | -2.102 | -1.742 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Leading the Way | 10.916 | 10.276 | 9.811 | 9.297 | 8.918 | 8.59 | 8.001 | 2.828 | -0.919 | -3.547 | -3.271 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 4.889 | 4.863 | 4.802 | 4.725 | 4.698 | 4.685 | 4.623 | 3.511 | 2.678 | 2.119 | 2.322 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 4.744 | 4.714 | 4.651 | 4.568 | 4.518 | 4.479 | 4.397 | 3.031 | 1.99 | 1.306 | 1.498 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 7.527 | 7.405 | 7.221 | 7.023 | 6.883 | 6.77 | 6.588 | 4.945 | 3.834 | 3.142 | 3.27 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 7.398 | 7.261 | 7.059 | 6.84 | 6.697 | 6.592 | 6.414 | 4.36 | 2.869 | 1.859 | 2.04 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Leading the Way | 13.155 | 12.918 | 12.561 | 12.167 | 11.874 | 11.614 | 11.106 | 6.154 | 2.283 | -0.736 | -0.685 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 22.096 | 21.616 | 20.957 | 20.335 | 19.911 | 19.579 | 19.039 | 14.237 | 10.847 | 8.658 | 8.883 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Leading the Way | 29.806 | 28.923 | 28.893 | 28.859 | 28.824 | 28.785 | 28.737 | 28.363 | 28.043 | 27.798 | 27.663 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Leading the Way | 5.815 | 5.387 | 5.346 | 5.303 | 5.274 | 5.252 | 5.212 | 4.655 | 4.237 | 3.932 | 3.99 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Leading the Way | 11.664 | 11.67 | 11.63 | 11.572 | 11.56 | 11.565 | 11.477 | 9.563 | 8.074 | 6.993 | 7.447 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - System Transformation | 5.236 | 5.048 | 4.759 | 4.435 | 4.079 | 3.694 | 3.239 | 0.996 | -2.293 | -6.921 | -14.107 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - System Transformation | 11.738 | 11.004 | 9.245 | 8.685 | 8.067 | 7.416 | 6.675 | 3.25 | -3.476 | -10.277 | -18.987 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 7.797 | 7.512 | 9.123 | 8.713 | 8.263 | 7.785 | 7.255 | 4.49 | 0.64 | -3.752 | -10.025 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - System Transformation | 6.008 | 5.814 | 5.518 | 5.192 | 4.832 | 4.454 | 4.044 | 1.935 | -1.668 | -5.976 | -12.493 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - System Transformation | 26.375 | 26.376 | 26.376 | 26.377 | 26.378 | 26.378 | 26.379 | 26.38 | 26.38 | 26.38 | 26.38 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - System Transformation | 2.685 | 2.644 | 2.571 | 2.487 | 2.382 | 2.258 | 2.108 | 1.195 | -0.45 | -2.31 | -4.812 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - System Transformation | 4.063 | 4.032 | 3.994 | 3.958 | 3.919 | 3.879 | 3.838 | 3.626 | 3.381 | 3.18 | 2.948 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - System Transformation | 4.423 | 4.252 | 4.041 | 3.809 | 3.549 | 3.261 | 2.927 | 1.051 | -1.783 | -4.637 | -8.013 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - System Transformation | 8.3 | 8.205 | 8.07 | 7.93 | 7.762 | 7.569 | 7.323 | 5.922 | 3.411 | 0.401 | -3.672 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - System Transformation | 12.338 | 12.083 | 11.732 | 11.39 | 11.011 | 10.599 | 10.14 | 7.797 | 5.094 | 2.356 | -1.477 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - System Transformation | 4.834 | 4.268 | 3.911 | 3.559 | 3.173 | 2.761 | 2.313 | -0.144 | -4.822 | -9.81 | -16.749 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - System Transformation | 11.711 | 11.199 | 11.002 | 10.787 | 10.541 | 10.27 | 9.97 | 8.156 | 5.048 | 1.225 | -4.587 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - System Transformation | 7.369 | 7.028 | 6.62 | 6.203 | 5.743 | 5.244 | 4.697 | 1.524 | -2.423 | -6.532 | -11.92 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - System Transformation | 6.616 | 5.998 | 5.724 | 5.447 | 5.141 | 4.813 | 4.459 | 2.417 | -0.798 | -4.412 | -9.684 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 13.169 | 13.042 | 12.861 | 12.658 | 12.409 | 12.115 | 11.295 | 7.421 | 4.825 | 2.675 | 0.144 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 16.735 | 16.731 | 16.706 | 16.669 | 16.616 | 16.517 | 16.301 | 15.046 | 14.738 | 13.838 | 12.806 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - System Transformation | 9.63 | 8.696 | 8.548 | 8.384 | 8.184 | 7.956 | 7.705 | 6.022 | 2.869 | -0.264 | -4.605 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - System Transformation | 10.8 | 10.177 | 9.862 | 9.532 | 9.173 | 8.791 | 8.401 | 6.186 | 3.031 | -0.846 | -6.694 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - System Transformation | 16.042 | 15.882 | 15.68 | 15.487 | 15.276 | 15.049 | 14.801 | 13.367 | 11.172 | 8.526 | 4.482 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - System Transformation | 10.382 | 10.329 | 10.251 | 10.149 | 10.01 | 9.833 | 9.608 | 7.98 | 5.788 | 4.24 | 2.69 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - System Transformation | 21.454 | 21.194 | 20.882 | 20.564 | 20.207 | 19.817 | 19.384 | 16.89 | 13.198 | 9.591 | 4.983 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 17.653 | 17.458 | 17.229 | 16.99 | 16.732 | 16.46 | 16.173 | 14.564 | 11.883 | 9.13 | 5.581 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - System Transformation | 13.036 | 12.412 | 11.957 | 11.484 | 10.976 | 10.438 | 9.84 | 6.706 | 2.639 | -2.378 | -9.776 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - System Transformation | 7.769 | 7.272 | 7.218 | 7.162 | 7.091 | 7.009 | 6.9 | 6.323 | 4.688 | 2.971 | 0.641 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - System Transformation | 8.771 | 8.568 | 8.244 | 7.87 | 7.434 | 6.947 | 6.36 | 3.213 | -1.37 | -6.435 | -13.551 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - System Transformation | 7.681 | 7.12 | 6.684 | 6.284 | 5.853 | 5.398 | 4.9 | 2.566 | -0.222 | -3.394 | -7.711 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - System Transformation | 7.958 | 7.76 | 7.488 | 7.217 | 6.912 | 6.568 | 6.137 | 3.773 | 0.574 | -3.231 | -8.767 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - System Transformation | 9.036 | 8.818 | 8.516 | 8.19 | 7.835 | 7.463 | 7.071 | 5.002 | 1.759 | -1.692 | -6.566 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - System Transformation | 3.813 | 3.608 | 3.303 | 2.966 | 2.588 | 2.18 | 1.73 | -0.831 | -5.027 | -9.745 | -16.764 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - System Transformation | 7.624 | 7.26 | 6.815 | 6.347 | 5.848 | 5.325 | 4.756 | 1.835 | -2.505 | -7.125 | -13.092 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - System Transformation | 10.215 | 9.991 | 10.057 | 10.107 | 10.132 | 10.137 | 10.11 | 9.76 | 8.083 | 6.508 | 4.531 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - System Transformation | 6.325 | 5.381 | 5.16 | 4.956 | 4.727 | 4.482 | 4.216 | 2.792 | 0.42 | -1.88 | -4.886 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - System Transformation | 16.791 | 15.591 | 15.137 | 14.661 | 14.133 | 13.542 | 12.811 | 8.904 | 4.169 | -1.403 | -9.046 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - System Transformation | 12.908 | 12.903 | 12.871 | 12.828 | 12.772 | 12.705 | 12.614 | 12.109 | 10.944 | 9.711 | 8.007 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - System Transformation | 6.776 | 6.753 | 6.724 | 6.695 | 6.665 | 6.632 | 6.597 | 6.42 | 6.182 | 5.924 | 5.581 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 12.653 | 12.662 | 12.647 | 12.618 | 12.569 | 12.502 | 12.41 | 11.744 | 10.265 | 8.733 | 6.679 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 16.777 | 16.767 | 16.737 | 16.69 | 16.623 | 16.531 | 16.408 | 15.501 | 13.98 | 12.483 | 10.504 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - System Transformation | 4.718 | 4.697 | 4.673 | 4.652 | 4.627 | 4.599 | 4.557 | 4.321 | 3.589 | 2.712 | 1.441 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - System Transformation | 9.111 | 9.002 | 8.867 | 8.738 | 8.6 | 8.456 | 8.301 | 7.466 | 6.075 | 4.477 | 2.084 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - System Transformation | 10.232 | 10.062 | 9.827 | 9.589 | 9.324 | 9.039 | 8.732 | 7.032 | 3.856 | 0.459 | -4.391 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 23.089 | 22.79 | 22.749 | 22.708 | 22.657 | 22.6 | 22.538 | 22.137 | 21.199 | 20.123 | 18.502 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - System Transformation | 6.669 | 6.579 | 6.435 | 6.282 | 6.087 | 5.852 | 5.568 | 3.71 | 0.509 | -2.43 | -6.2 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - System Transformation | 4.9 | 4.207 | 3.803 | 3.35 | 2.835 | 2.269 | 1.621 | -1.845 | -6.567 | -11.116 | -17.085 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - System Transformation | 11.931 | 10.713 | 10.438 | 10.152 | 9.828 | 9.476 | 9.075 | 6.867 | 2.457 | -1.941 | -7.888 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 8.863 | 8.705 | 8.489 | 8.278 | 8.037 | 7.776 | 7.496 | 5.927 | 3.57 | 1.319 | -1.776 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 14.144 | 13.889 | 13.562 | 13.25 | 12.907 | 12.545 | 12.167 | 10.062 | 6.469 | 2.308 | -4.018 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - System Transformation | 4.139 | 3.663 | 3.557 | 3.445 | 3.312 | 3.164 | 2.987 | 2.042 | -0.269 | -2.592 | -5.368 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - System Transformation | 18.218 | 18.059 | 17.83 | 17.576 | 17.29 | 16.98 | 16.634 | 14.685 | 11.251 | 7.704 | 2.701 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - System Transformation | 18.859 | 18.84 | 18.808 | 18.771 | 18.727 | 18.677 | 18.619 | 18.245 | 17.321 | 16.293 | 14.868 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - System Transformation | 7.972 | 7.837 | 7.648 | 7.468 | 7.262 | 7.035 | 6.769 | 5.392 | 3.322 | 1.166 | -1.883 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - System Transformation | 8.983 | 8.954 | 8.907 | 8.848 | 8.771 | 8.675 | 8.558 | 7.775 | 6.631 | 5.608 | 4.46 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - System Transformation | 1.509 | 1.399 | 1.199 | 0.959 | 0.685 | 0.383 | 0.046 | -1.847 | -4.952 | -9.001 | -15.118 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - System Transformation | 5.177 | 4.424 | 3.587 | 2.921 | 2.203 | 1.451 | 0.668 | -3.272 | -7.642 | -12.191 | -18.532 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - System Transformation | 10.29 | 9.987 | 8.847 | 8.443 | 7.997 | 7.511 | 6.93 | 4.007 | -0.424 | -5.502 | -12.501 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - System Transformation | 15.569 | 15.216 | 15.147 | 15.061 | 14.95 | 14.816 | 14.654 | 13.629 | 12.108 | 10.869 | 9.609 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - System Transformation | 10.695 | 9.316 | 9.111 | 8.885 | 8.613 | 8.305 | 7.931 | 5.787 | 0.639 | -4.537 | -11.413 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - System Transformation | 7.834 | 7.494 | 7.04 | 6.569 | 6.055 | 5.511 | 4.93 | 1.885 | -2.286 | -6.922 | -13.75 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - System Transformation | 22.501 | 22.068 | 21.541 | 21.094 | 20.602 | 20.079 | 19.498 | 16.636 | 13.146 | 9.944 | 5.682 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - System Transformation | 4.991 | 4.792 | 4.513 | 4.202 | 3.856 | 3.486 | 3.071 | 0.871 | -2.567 | -6.583 | -12.305 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - System Transformation | 11.663 | 11.52 | 11.33 | 11.144 | 10.941 | 10.728 | 10.491 | 9.323 | 7.592 | 5.147 | 1.307 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - System Transformation | 18.203 | 18.113 | 17.972 | 17.813 | 17.627 | 17.42 | 17.182 | 15.766 | 13.087 | 10.207 | 6.094 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - System Transformation | 9.287 | 9.313 | 7.87 | 7.848 | 7.803 | 7.734 | 7.626 | 6.852 | 5.23 | 3.686 | 1.716 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - System Transformation | 27.427 | 27.452 | 27.458 | 27.442 | 27.402 | 27.335 | 27.241 | 26.436 | 25.208 | 24.489 | 23.954 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - System Transformation | 14.411 | 13.953 | 13.974 | 13.986 | 13.98 | 13.961 | 13.915 | 13.574 | 12.644 | 11.293 | 9.207 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - System Transformation | 2.721 | 2.453 | 2.039 | 1.542 | 0.941 | 0.234 | -0.579 | -5.613 | -10.407 | -12.885 | -14.376 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - System Transformation | 18.045 | 18.11 | 18.158 | 18.193 | 18.214 | 18.225 | 18.222 | 18.094 | 17.499 | 16.893 | 16.252 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 7.321 | 6.813 | 6.413 | 6.008 | 5.57 | 5.1 | 4.57 | 1.87 | -1.303 | -4.947 | -10.008 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - System Transformation | 2.939 | 2.909 | 2.834 | 2.745 | 2.637 | 2.512 | 2.346 | 1.37 | -0.759 | -3.696 | -8.326 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - System Transformation | 14.176 | 13.879 | 13.5 | 13.121 | 12.704 | 12.258 | 11.768 | 9.234 | 5.795 | 2.73 | -1.024 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - System Transformation | 15.184 | 12.768 | 12.755 | 12.73 | 12.677 | 12.602 | 12.506 | 11.721 | 10.063 | 8.455 | 6.243 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - System Transformation | 8.413 | 7.699 | 7.216 | 6.78 | 6.294 | 5.77 | 5.164 | 2.01 | -3.575 | -9.315 | -16.982 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - System Transformation | 18.347 | 18.255 | 18.14 | 18.039 | 17.923 | 17.797 | 17.642 | 16.876 | 15.279 | 13.593 | 11.409 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - System Transformation | 8.323 | 7.957 | 7.467 | 6.967 | 6.422 | 5.845 | 5.194 | 2.027 | -2.511 | -7.831 | -15.531 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - System Transformation | 3.978 | 3.279 | 2.84 | 2.375 | 1.863 | 1.301 | 0.659 | -2.787 | -6.8 | -11.385 | -17.598 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - System Transformation | 2.719 | 2.419 | 2.059 | 1.745 | 1.406 | 1.048 | 0.661 | -1.232 | -3.457 | -6.239 | -10.27 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - System Transformation | 8.487 | 8.475 | 8.449 | 23.811 | 23.759 | 23.69 | 23.593 | 22.957 | 22.086 | 21.35 | 20.507 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - System Transformation | 21.026 | 20.753 | 20.747 | 20.736 | 20.721 | 20.703 | 20.677 | 20.556 | 19.931 | 19.303 | 18.54 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - System Transformation | 19.095 | 19.001 | 18.854 | 18.697 | 18.516 | 18.311 | 18.041 | 16.678 | 14.623 | 11.928 | 7.931 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - System Transformation | 16.664 | 16.764 | 16.854 | 16.935 | 17.007 | 17.07 | 17.126 | 17.3 | 17.292 | 17.264 | 17.235 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - System Transformation | 14.684 | 14.749 | 14.782 | 14.808 | 14.809 | 14.787 | 14.737 | 14.304 | 13.323 | 12.447 | 11.422 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - System Transformation | 1.322 | 1.322 | 1.268 | 1.159 | 20.881 | 20.63 | 20.304 | 17.567 | 13.086 | 9.395 | 4.849 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - System Transformation | 7.549 | 7.254 | 6.882 | 6.513 | 6.115 | 5.699 | 5.259 | 3.045 | -0.17 | -3.821 | -9.025 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - System Transformation | 6.707 | 6.412 | 6.018 | 5.62 | 5.183 | 4.708 | 4.154 | 1.391 | -1.887 | -5.382 | -10.06 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - System Transformation | 17.697 | 17.609 | 17.493 | 17.368 | 17.229 | 17.079 | 16.92 | 16.001 | 14.59 | 13.228 | 11.407 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - System Transformation | 6.565 | 6.433 | 6.261 | 6.095 | 5.907 | 5.701 | 5.474 | 4.271 | 2.17 | -0.003 | -2.803 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 6.77 | 6.47 | 6.115 | 5.783 | 5.424 | 5.047 | 4.64 | 2.581 | -0.269 | -2.906 | -6.203 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - System Transformation | 18.623 | 18.612 | 18.584 | 18.551 | 18.507 | 18.455 | 18.392 | 17.993 | 17.315 | 16.595 | 15.572 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - System Transformation | 6.881 | 6.682 | 6.426 | 6.187 | 5.925 | 5.643 | 5.331 | 3.766 | 1.808 | -0.811 | -4.825 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - System Transformation | 2.78 | 2.763 | 2.741 | 2.72 | 2.696 | 2.67 | 2.639 | 2.48 | 2.206 | 1.986 | 1.731 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - System Transformation | 9.164 | 8.828 | 8.723 | 8.607 | 8.467 | 8.308 | 8.12 | 6.948 | 4.81 | 2.55 | -0.499 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - System Transformation | 14.986 | 14.829 | 14.625 | 14.42 | 14.195 | 13.958 | 13.699 | 12.403 | 10.534 | 8.622 | 6.053 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - System Transformation | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - System Transformation | 21.178 | 21.048 | 20.888 | 20.742 | 20.579 | 20.405 | 20.211 | 19.212 | 17.362 | 15.431 | 12.749 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - System Transformation | 8.328 | 8.142 | 7.898 | 7.668 | 7.415 | 7.144 | 6.83 | 5.211 | 2.596 | -0.83 | -6.066 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - System Transformation | 14.101 | 13.933 | 13.713 | 13.485 | 13.235 | 12.968 | 12.666 | 11.076 | 8.591 | 5.757 | 1.733 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - System Transformation | 33.321 | 32.968 | 32.949 | 32.93 | 32.906 | 32.878 | 32.842 | 32.674 | 32.174 | 31.651 | 30.973 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - System Transformation | 4.048 | 3.36 | 2.917 | 2.456 | 1.955 | 1.427 | 0.82 | -1.94 | -5.509 | -9.707 | -15.775 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - System Transformation | 14.833 | 14.123 | 13.876 | 13.596 | 13.279 | 12.914 | 12.467 | 9.909 | 5.736 | 1.337 | -3.975 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - System Transformation | 11.874 | 11.723 | 11.518 | 11.297 | 11.041 | 10.758 | 10.45 | 8.594 | 5.182 | 1.673 | -2.952 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - System Transformation | 14.931 | 14.888 | 14.828 | 14.762 | 14.68 | 14.585 | 14.472 | 13.767 | 12.377 | 10.881 | 8.904 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 24.288 | 22.49 | 22.218 | 21.951 | 21.666 | 21.368 | 21.054 | 19.501 | 17.461 | 15.276 | 12.105 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - System Transformation | 5.123 | 4.581 | 4.23 | 3.867 | 3.477 | 3.066 | 2.639 | 0.282 | -3.598 | -7.894 | -13.754 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - System Transformation | 1.223 | 0.503 | 0.066 | -0.353 | -0.807 | -1.286 | -1.815 | -4.5 | -8.9 | -14.05 | -21.594 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - System Transformation | 3.33 | 3.28 | 1.933 | 1.867 | 1.792 | 1.711 | 1.621 | 1.136 | 0.628 | 0.19 | -0.299 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - System Transformation | 8.713 | 8.226 | 9.922 | 9.645 | 9.33 | 8.99 | 8.625 | 6.575 | 2.782 | -1.04 | -6.33 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - System Transformation | 7.127 | 7.116 | 7.061 | 6.985 | 6.886 | 6.764 | 6.588 | 5.403 | 2.228 | -1.767 | -7.937 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - System Transformation | 32.7 | 31.312 | 31.245 | 31.17 | 31.083 | 30.985 | 30.884 | 30.172 | 29.035 | 27.652 | 25.552 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - System Transformation | 12.167 | 12.026 | 11.828 | 11.619 | 11.39 | 11.147 | 10.9 | 9.488 | 6.735 | 3.665 | -0.93 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - System Transformation | 8.846 | 8.133 | 7.896 | 7.706 | 7.501 | 7.288 | 7.071 | 5.977 | 4.405 | 2.52 | -0.236 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - System Transformation | 8.75 | 8.805 | 8.843 | 8.869 | 8.881 | 8.879 | 8.856 | 8.578 | 7.775 | 6.772 | 5.332 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - System Transformation | 13.932 | 13.882 | 13.793 | 13.684 | 13.556 | 13.415 | 13.257 | 12.329 | 10.016 | 7.802 | 4.854 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 14.633 | 14.557 | 14.433 | 14.256 | 14.016 | 13.709 | 13.322 | 10.576 | 6.652 | 3.982 | 1.72 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 18.739 | 18.603 | 18.438 | 18.254 | 18.052 | 17.833 | 17.59 | 16.148 | 13.183 | 9.809 | 5.354 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - System Transformation | 5.5 | 4.469 | 4.198 | 3.907 | 3.589 | 3.247 | 2.851 | 0.664 | -2.791 | -6.576 | -11.242 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - System Transformation | 5.376 | 3.922 | 3.032 | 2.102 | 1.118 | 0.066 | -1.138 | -6.962 | -12.268 | -19.686 | -30.219 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - System Transformation | 13.184 | 12.366 | 12.023 | 11.753 | 11.461 | 11.155 | 10.805 | 9.203 | 6.927 | 4.537 | 1.318 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - System Transformation | 15.716 | 14.939 | 14.631 | 14.312 | 13.962 | 13.59 | 13.189 | 11.049 | 7.658 | 3.817 | -1.929 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - System Transformation | 9.88 | 9.742 | 9.526 | 9.287 | 9.021 | 8.735 | 8.425 | 6.729 | 4.051 | 1.067 | -3.389 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - System Transformation | 11.05 | 11.066 | 11.071 | 11.071 | 11.065 | 11.052 | 11.032 | 10.858 | 10.488 | 10.134 | 9.786 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - System Transformation | 21.438 | 21.371 | 21.271 | 21.159 | 21.034 | 20.894 | 20.716 | 19.754 | 18.66 | 17.137 | 14.924 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - System Transformation | 16.224 | 16.321 | 16.403 | 16.474 | 16.531 | 16.576 | 16.604 | 16.62 | 15.823 | 15.097 | 14.234 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 10.656 | 10.342 | 9.943 | 9.546 | 9.118 | 8.665 | 8.163 | 5.643 | 2.203 | -1.882 | -7.702 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 21.899 | 21.867 | 21.824 | 21.78 | 21.729 | 21.673 | 21.606 | 21.24 | 20.647 | 19.954 | 19.038 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - System Transformation | 2.507 | 2.327 | 2.062 | 1.783 | 1.47 | 1.135 | 0.763 | -1.196 | -4.232 | -8.205 | -14.242 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - System Transformation | 6.6 | 6.589 | 6.574 | 6.558 | 6.54 | 6.52 | 6.499 | 6.373 | 6.094 | 5.813 | 5.425 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - System Transformation | 7.877 | 7.146 | 6.975 | 6.82 | 6.643 | 6.449 | 6.217 | 5.127 | 3.567 | 1.456 | -1.612 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - System Transformation | 12.761 | 12.263 | 11.598 | 10.889 | 10.105 | 9.258 | 8.331 | 3.156 | -4.084 | -11.824 | -22.725 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - System Transformation | 10.343 | 8.897 | 8.136 | 7.8 | 7.416 | 6.997 | 6.535 | 3.93 | -0.39 | -4.919 | -11.271 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - System Transformation | 3.891 | 3.712 | 3.5 | 3.282 | 3.043 | 2.788 | 2.515 | 0.962 | -1.416 | -3.662 | -6.419 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - System Transformation | 3.904 | 3.823 | 3.735 | 3.644 | 3.547 | 3.444 | 3.336 | 2.741 | 2.022 | 1.317 | 0.586 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - System Transformation | 3.062 | 2.728 | 23.897 | 23.738 | 23.538 | 23.294 | 22.974 | 20.957 | 17.669 | 14.643 | 10.957 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - System Transformation | 13.776 | 13.254 | 12.914 | 12.578 | 12.217 | 11.841 | 11.44 | 9.593 | 7.87 | 6.224 | 4.069 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - System Transformation | 4.315 | 4.172 | 3.995 | 3.819 | 3.635 | 3.447 | 3.252 | 2.3 | 1.238 | 0.026 | -1.676 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - System Transformation | 3.555 | 3.423 | 3.264 | 3.107 | 2.934 | 2.751 | 2.556 | 1.517 | 0.192 | -1.002 | -2.431 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 13.886 | 13.299 | 13.013 | 12.702 | 12.353 | 11.972 | 11.533 | 9.203 | 4.902 | 0.492 | -5.645 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - System Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - System Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - System Transformation | 17.538 | 17.024 | 16.864 | 16.701 | 16.516 | 16.319 | 16.102 | 14.9 | 12.621 | 10.023 | 6.264 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - System Transformation | 15.241 | 14.173 | 14.087 | 13.993 | 13.885 | 13.765 | 13.63 | 12.835 | 11.751 | 10.843 | 9.887 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - System Transformation | 10.768 | 10.601 | 10.382 | 10.172 | 9.934 | 9.674 | 9.371 | 7.769 | 5.365 | 2.657 | -1.206 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - System Transformation | 12.89 | 12.605 | 12.267 | 11.958 | 11.62 | 11.263 | 10.881 | 8.897 | 6.227 | 3.691 | 0.448 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - System Transformation | 10.406 | 9.598 | 9.399 | 9.178 | 8.934 | 8.672 | 8.392 | 6.818 | 4.354 | 1.562 | -2.397 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - System Transformation | 11.175 | 11.096 | 10.974 | 10.839 | 10.68 | 10.498 | 10.283 | 8.975 | 6.737 | 4.137 | 0.26 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - System Transformation | 18.638 | 17.859 | 17.856 | 17.839 | 17.803 | 17.75 | 17.67 | 17.091 | 15.485 | 13.832 | 11.599 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - System Transformation | 16.318 | 16.063 | 15.732 | 15.394 | 15.008 | 14.581 | 14.092 | 11.294 | 7.325 | 3.46 | -1.591 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | 8.843 | 8.704 | 8.52 | 8.34 | 8.143 | 7.936 | 7.715 | 6.617 | 5.353 | 4.221 | 2.708 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - System Transformation | 12.623 | 12.261 | 10.512 | 10.224 | 9.889 | 9.495 | 8.986 | 6.063 | 2.129 | -2.629 | -9.246 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - System Transformation | 23.047 | 13.555 | 6.529 | 6.24 | 5.91 | 5.543 | 5.11 | 2.757 | -0.866 | -4.736 | -9.819 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - System Transformation | 2.279 | 1.501 | 0.918 | -1.387 | -1.936 | -2.51 | -3.135 | -6.24 | -10.665 | -15.384 | -22.07 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - System Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - System Transformation | 5.428 | 5.32 | 5.191 | 5.052 | 4.894 | 4.722 | 4.528 | 3.347 | 1.319 | -0.78 | -3.457 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - System Transformation | 11.97 | 11.182 | 10.93 | 10.656 | 10.353 | 10 | 9.525 | 6.967 | 4.295 | 0.714 | -4.136 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 7.884 | 6.273 | 6.229 | 6.164 | 6.073 | 5.96 | 5.804 | 4.822 | 2.339 | -0.167 | -3.532 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 27.949 | 27.966 | 27.982 | 27.996 | 28.008 | 28.02 | 28.029 | 28.062 | 28.072 | 28.075 | 28.079 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - System Transformation | 19.863 | 18.852 | 18.573 | 18.277 | 17.959 | 17.627 | 17.271 | 15.456 | 12.856 | 9.77 | 5.247 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - System Transformation | 8.209 | 7.536 | 7.623 | 7.656 | 7.621 | 7.517 | 7.335 | 5.583 | 2.74 | 0.996 | -0.383 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - System Transformation | 4.1 | 3.964 | 3.887 | 3.803 | 3.711 | 3.612 | 3.505 | 2.872 | 2.024 | 1.136 | 0.241 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - System Transformation | 14.237 | 13.979 | 13.656 | 13.349 | 13.02 | 12.679 | 12.317 | 10.39 | 7.155 | 2.976 | -3.659 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - System Transformation | 2.4 | 2.085 | 1.696 | 1.296 | 0.86 | 0.397 | -0.102 | -2.766 | -6.389 | -9.732 | -13.846 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - System Transformation | 8.689 | 7.773 | 7.5 | 7.222 | 6.921 | 6.603 | 6.254 | 4.648 | 3.057 | 1.406 | -0.642 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 25.107 | 24.6 | 24.223 | 23.821 | 23.385 | 22.922 | 22.428 | 19.747 | 15.521 | 10.986 | 4.617 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - System Transformation | 11.585 | 11.413 | 11.149 | 10.864 | 10.542 | 10.188 | 9.758 | 7.526 | 4.212 | 0.125 | -5.988 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - System Transformation | 11.178 | 10.891 | 10.524 | 10.159 | 9.764 | 9.346 | 8.88 | 6.444 | 2.493 | -1.85 | -8.129 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - System Transformation | 13.887 | 13.68 | 13.763 | 13.833 | 13.885 | 13.924 | 13.94 | 13.868 | 13.021 | 12.103 | 10.853 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - System Transformation | 32.572 | 32.128 | 31.617 | 31.139 | 30.63 | 30.101 | 29.563 | 26.719 | 22.453 | 17.736 | 11.198 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - System Transformation | 9.699 | 8.118 | 8.029 | 7.925 | 7.796 | 7.644 | 7.475 | 6.361 | 4.513 | 2.692 | 0.103 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - System Transformation | 8.192 | 7.462 | 7.158 | 6.835 | 6.486 | 6.119 | 5.746 | 3.704 | 0.546 | -3.139 | -8.605 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - System Transformation | 30.736 | 30.746 | 30.753 | 30.761 | 30.767 | 30.772 | 30.777 | 30.785 | 30.767 | 30.733 | 30.678 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - System Transformation | 9.013 | 9.014 | 24.39 | 24.355 | 24.308 | 24.25 | 24.171 | 23.69 | 22.481 | 20.846 | 18.301 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - System Transformation | 8.632 | 6.966 | 21.641 | 21.336 | 20.999 | 20.64 | 20.257 | 18.19 | 14.473 | 10.772 | 5.647 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - System Transformation | 9.435 | 9.19 | 8.889 | 8.571 | 8.224 | 7.849 | 7.427 | 5.155 | 1.902 | -1.114 | -4.725 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - System Transformation | 12.086 | 11.969 | 11.821 | 11.678 | 11.528 | 11.376 | 11.226 | 10.514 | 9.764 | 8.844 | 7.419 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - System Transformation | 20.208 | 19.659 | 19.577 | 19.492 | 19.39 | 19.279 | 19.162 | 18.378 | 16.59 | 14.482 | 11.224 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - System Transformation | 10.755 | 10.343 | 9.843 | 9.408 | 8.927 | 8.409 | 7.835 | 4.903 | 1.096 | -2.812 | -8.222 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - System Transformation | 12.191 | 11.822 | 11.58 | 11.32 | 11.039 | 10.745 | 10.442 | 8.791 | 6.134 | 2.631 | -2.771 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - System Transformation | 10.827 | 10.239 | 9.911 | 9.573 | 9.207 | 8.826 | 8.432 | 6.436 | 3.569 | 0.427 | -4.294 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 4.86 | 4.861 | 4.852 | 4.838 | 4.816 | 4.789 | 4.75 | 4.48 | 3.704 | 2.904 | 1.798 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 4.71 | 4.711 | 4.7 | 4.679 | 4.646 | 4.604 | 4.543 | 4.143 | 3.133 | 2.214 | 1.105 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 7.49 | 7.42 | 7.319 | 7.215 | 7.099 | 6.974 | 6.828 | 6.108 | 5.159 | 4.207 | 2.913 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 7.353 | 7.29 | 7.2 | 7.105 | 6.998 | 6.883 | 6.742 | 6.041 | 4.816 | 3.517 | 1.74 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - System Transformation | 13.103 | 12.883 | 12.605 | 12.32 | 12.018 | 11.708 | 11.399 | 9.697 | 6.825 | 3.457 | -1.714 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 21.938 | 21.6 | 21.206 | 20.875 | 20.513 | 20.129 | 19.692 | 17.531 | 14.549 | 11.441 | 7.194 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - System Transformation | 29.761 | 28.857 | 28.809 | 28.757 | 28.7 | 28.637 | 28.567 | 28.142 | 27.609 | 27.12 | 26.648 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - System Transformation | 5.798 | 5.381 | 5.358 | 5.336 | 5.31 | 5.281 | 5.245 | 5.061 | 4.692 | 4.305 | 3.796 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - System Transformation | 11.586 | 11.596 | 11.586 | 11.57 | 11.541 | 11.502 | 11.45 | 11.052 | 9.753 | 8.238 | 6.055 | Primary
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NPg Best View | 5.609 | 5.298 | 4.736 | 4.091 | 3.674 | 3.371 | 3.019 | 1.645 | -3.66 | -7.845 | -12.287 | Primary
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NPg Best View | 12.173 | 11.365 | 9.414 | 8.582 | 7.976 | 7.469 | 6.878 | 4.361 | -3.776 | -10.032 | -16.297 | Primary
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 8.063 | 7.752 | 9.216 | 8.609 | 8.165 | 7.779 | 7.326 | 5.39 | 0.416 | -3.464 | -7.437 | Primary
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NPg Best View | 6.296 | 6.092 | 5.671 | 5.174 | 4.839 | 4.568 | 4.244 | 2.936 | -2.104 | -6.19 | -10.349 | Primary
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NPg Best View | 26.376 | 26.378 | 26.379 | 26.381 | 26.382 | 26.383 | 26.384 | 26.388 | 26.391 | 26.394 | 26.396 | Primary
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NPg Best View | 2.919 | 2.925 | 2.851 | 2.744 | 2.685 | 2.638 | 2.559 | 2.163 | 0.378 | -1.018 | -2.444 | Primary
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NPg Best View | 4.085 | 4.064 | 4.037 | 4.01 | 3.984 | 3.958 | 3.926 | 3.773 | 3.557 | 3.384 | 3.223 | Primary
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NPg Best View | 4.696 | 4.586 | 4.388 | 4.148 | 3.932 | 3.721 | 3.471 | 2.163 | -0.537 | -2.675 | -4.824 | Primary
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NPg Best View | 8.618 | 8.569 | 8.394 | 8.189 | 8.031 | 7.912 | 7.766 | 7.129 | 4.229 | 1.864 | -0.606 | Primary
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NPg Best View | 12.691 | 12.501 | 12.159 | 11.769 | 11.514 | 11.27 | 10.939 | 9.403 | 6.18 | 3.911 | 1.723 | Primary
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NPg Best View | 5.095 | 4.571 | 4.157 | 3.708 | 3.339 | 2.997 | 2.599 | 0.775 | -5.076 | -9.938 | -14.67 | Primary
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NPg Best View | 11.936 | 11.429 | 11.141 | 10.797 | 10.556 | 10.349 | 10.096 | 8.909 | 4.445 | 0.794 | -2.858 | Primary
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NPg Best View | 7.632 | 7.29 | 6.78 | 6.215 | 5.773 | 5.344 | 4.839 | 2.292 | -2.122 | -5.358 | -8.574 | Primary
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NPg Best View | 6.832 | 6.236 | 5.888 | 5.498 | 5.222 | 4.973 | 4.675 | 3.316 | -0.735 | -3.981 | -7.183 | Primary
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 13.324 | 13.206 | 12.968 | 12.685 | 12.399 | 12.084 | 11.211 | 7.387 | 4.63 | 2.973 | 1.509 | Primary
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 16.868 | 16.902 | 16.866 | 16.769 | 16.653 | 16.533 | 16.393 | 15.711 | 14.684 | 14.204 | 13.812 | Primary
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NPg Best View | 9.753 | 8.878 | 8.725 | 8.53 | 8.338 | 8.134 | 7.878 | 6.536 | 2.614 | -0.476 | -3.31 | Primary
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NPg Best View | 10.958 | 10.367 | 10.013 | 9.619 | 9.28 | 8.96 | 8.592 | 6.931 | 2.146 | -1.8 | -5.547 | Primary
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NPg Best View | 16.165 | 16.022 | 15.784 | 15.52 | 15.322 | 15.144 | 14.93 | 13.938 | 10.701 | 8.052 | 5.5 | Primary
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NPg Best View | 10.44 | 10.37 | 10.24 | 10.061 | 9.869 | 9.639 | 9.35 | 7.517 | 5.367 | 4.13 | 3.077 | Primary
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NPg Best View | 21.625 | 21.39 | 21.039 | 20.653 | 20.284 | 19.911 | 19.476 | 17.238 | 12.962 | 9.626 | 6.423 | Primary
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 17.85 | 17.743 | 17.563 | 17.36 | 17.174 | 16.986 | 16.765 | 15.701 | 12.958 | 10.583 | 8.284 | Primary
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NPg Best View | 13.304 | 12.642 | 12.02 | 11.314 | 10.813 | 10.382 | 9.886 | 7.725 | 1.814 | -2.871 | -7.587 | Primary
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NPg Best View | 7.934 | 7.438 | 7.34 | 7.22 | 7.148 | 7.101 | 7.035 | 6.749 | 4.791 | 3.232 | 1.644 | Primary
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NPg Best View | 9.224 | 8.904 | 8.298 | 7.587 | 7.066 | 6.627 | 6.094 | 3.531 | -2.453 | -6.746 | -11.244 | Primary
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NPg Best View | 8.034 | 7.492 | 7.003 | 6.511 | 6.134 | 5.811 | 5.422 | 3.83 | 0.156 | -2.614 | -5.393 | Primary
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NPg Best View | 8.153 | 7.931 | 7.532 | 7.072 | 6.722 | 6.427 | 6.077 | 4.521 | -0.028 | -3.524 | -6.992 | Primary
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NPg Best View | 9.175 | 9.017 | 8.706 | 8.354 | 8.024 | 7.718 | 7.365 | 5.916 | 1.792 | -1.616 | -4.867 | Primary
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NPg Best View | 3.991 | 3.778 | 3.346 | 2.832 | 2.443 | 2.093 | 1.676 | -0.194 | -5.989 | -10.614 | -15.12 | Primary
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NPg Best View | 7.922 | 7.62 | 7.168 | 6.657 | 6.226 | 5.825 | 5.365 | 3.267 | -1.622 | -5.73 | -9.845 | Primary
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NPg Best View | 10.486 | 10.363 | 10.491 | 10.581 | 10.673 | 10.756 | 10.805 | 10.936 | 9.408 | 8.21 | 7.045 | Primary
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NPg Best View | 6.535 | 5.664 | 5.465 | 5.26 | 5.081 | 4.907 | 4.689 | 3.707 | 1.12 | -0.94 | -2.922 | Primary
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NPg Best View | 17.23 | 16.023 | 15.406 | 14.666 | 14.12 | 13.632 | 13.051 | 10.342 | 3.9 | -0.873 | -5.66 | Primary
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NPg Best View | 13.062 | 13.073 | 13.023 | 12.949 | 12.913 | 12.892 | 12.849 | 12.663 | 11.36 | 10.34 | 9.274 | Primary
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NPg Best View | 6.787 | 6.763 | 6.727 | 6.689 | 6.659 | 6.632 | 6.601 | 6.472 | 6.176 | 5.941 | 5.708 | Primary
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 12.787 | 12.815 | 12.786 | 12.721 | 12.68 | 12.643 | 12.581 | 12.178 | 10.44 | 9.113 | 7.819 | Primary
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 16.869 | 16.839 | 16.75 | 16.623 | 16.526 | 16.432 | 16.308 | 15.513 | 13.697 | 12.42 | 11.165 | Primary
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NPg Best View | 4.791 | 4.756 | 4.689 | 4.618 | 4.578 | 4.557 | 4.532 | 4.41 | 3.463 | 2.661 | 1.798 | Primary
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NPg Best View | 9.197 | 9.07 | 8.87 | 8.656 | 8.519 | 8.403 | 8.268 | 7.667 | 5.701 | 4.145 | 2.593 | Primary
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NPg Best View | 10.413 | 10.279 | 10.004 | 9.693 | 9.454 | 9.239 | 8.977 | 7.83 | 3.691 | 0.346 | -2.85 | Primary
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 23.191 | 22.943 | 22.93 | 22.91 | 22.896 | 22.884 | 22.856 | 22.762 | 21.568 | 20.555 | 19.624 | Primary
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NPg Best View | 6.91 | 6.865 | 6.688 | 6.464 | 6.277 | 6.074 | 5.8 | 4.277 | 0.67 | -1.866 | -4.19 | Primary
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NPg Best View | 5.209 | 4.461 | 3.862 | 3.166 | 2.605 | 2.08 | 1.446 | -1.506 | -7.178 | -11.068 | -14.847 | Primary
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NPg Best View | 12.15 | 10.955 | 10.602 | 10.187 | 9.865 | 9.575 | 9.228 | 7.648 | 2.258 | -1.991 | -6.095 | Primary
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 9.042 | 8.978 | 8.821 | 8.647 | 8.488 | 8.319 | 8.094 | 7.009 | 4.216 | 2.017 | 0.023 | Primary
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 14.372 | 14.183 | 13.838 | 13.468 | 13.19 | 12.937 | 12.626 | 11.267 | 6.196 | 1.946 | -2.117 | Primary
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NPg Best View | 4.403 | 3.997 | 3.922 | 3.819 | 3.744 | 3.682 | 3.592 | 3.158 | 0.888 | -1.018 | -2.949 | Primary
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NPg Best View | 18.373 | 18.234 | 17.957 | 17.624 | 17.341 | 17.076 | 16.756 | 15.257 | 10.829 | 7.299 | 3.953 | Primary
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NPg Best View | 18.941 | 18.95 | 18.926 | 18.892 | 18.868 | 18.851 | 18.824 | 18.687 | 17.645 | 16.736 | 15.845 | Primary
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NPg Best View | 8.252 | 8.147 | 7.928 | 7.688 | 7.534 | 7.409 | 7.235 | 6.414 | 3.953 | 2.081 | 0.156 | Primary
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NPg Best View | 9.127 | 9.143 | 9.12 | 9.079 | 9.029 | 8.967 | 8.876 | 8.288 | 7.286 | 6.596 | 5.948 | Primary
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NPg Best View | 1.794 | 1.68 | 1.377 | 0.994 | 0.736 | 0.541 | 0.3 | -0.725 | -5.302 | -9.034 | -12.847 | Primary
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NPg Best View | 5.762 | 5.228 | 4.502 | 3.844 | 3.347 | 2.852 | 2.228 | -0.597 | -6.113 | -10.199 | -14.02 | Primary
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NPg Best View | 10.686 | 10.284 | 8.902 | 8.198 | 7.684 | 7.255 | 6.759 | 4.537 | -1.3 | -5.762 | -10.404 | Primary
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NPg Best View | 15.742 | 15.465 | 15.445 | 15.396 | 15.325 | 15.235 | 15.106 | 14.354 | 12.977 | 12.005 | 11.117 | Primary
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NPg Best View | 11.052 | 9.708 | 9.426 | 9.065 | 8.806 | 8.584 | 8.297 | 6.894 | 0.722 | -4.179 | -8.955 | Primary
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NPg Best View | 8.13 | 7.784 | 7.217 | 6.574 | 6.116 | 5.71 | 5.219 | 2.953 | -2.718 | -7.15 | -11.608 | Primary
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NPg Best View | 22.93 | 22.596 | 22.081 | 21.584 | 21.227 | 20.896 | 20.466 | 18.512 | 14.64 | 11.852 | 9.081 | Primary
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NPg Best View | 5.296 | 5.093 | 4.71 | 4.266 | 3.937 | 3.657 | 3.324 | 1.862 | -2.526 | -6.052 | -9.648 | Primary
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NPg Best View | 11.85 | 11.662 | 11.337 | 10.99 | 10.764 | 10.599 | 10.408 | 9.72 | 7.054 | 4.919 | 2.614 | Primary
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NPg Best View | 18.336 | 18.269 | 18.084 | 17.859 | 17.666 | 17.49 | 17.279 | 16.301 | 12.817 | 10.013 | 7.327 | Primary
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NPg Best View | 9.433 | 9.467 | 7.985 | 7.904 | 7.846 | 7.789 | 7.702 | 7.158 | 5.394 | 4.152 | 2.931 | Primary
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NPg Best View | 27.498 | 27.55 | 27.569 | 27.553 | 27.504 | 27.42 | 27.294 | 26.408 | 25.419 | 24.954 | 24.643 | Primary
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NPg Best View | 14.673 | 14.24 | 14.233 | 14.202 | 14.227 | 14.278 | 14.31 | 14.446 | 13.319 | 12.412 | 11.338 | Primary
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NPg Best View | 2.943 | 2.783 | 2.415 | 1.928 | 1.33 | 0.595 | -0.346 | -5.601 | -9.562 | -11.17 | -12.128 | Primary
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NPg Best View | 18.274 | 18.439 | 18.577 | 18.694 | 18.801 | 18.898 | 18.975 | 19.285 | 19.09 | 18.907 | 18.696 | Primary
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 7.55 | 7.087 | 6.639 | 6.139 | 5.722 | 5.338 | 4.894 | 3.042 | -1.239 | -4.545 | -7.751 | Primary
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NPg Best View | 3.147 | 3.051 | 2.802 | 2.513 | 2.359 | 2.275 | 2.177 | 1.822 | -1.364 | -3.964 | -6.769 | Primary
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NPg Best View | 14.413 | 14.15 | 13.737 | 13.286 | 12.923 | 12.571 | 12.143 | 10.101 | 6.446 | 3.79 | 1.215 | Primary
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NPg Best View | 15.359 | 13.029 | 13.05 | 13.05 | 13.031 | 12.999 | 12.931 | 12.545 | 10.808 | 9.494 | 8.271 | Primary
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NPg Best View | 8.87 | 8.208 | 7.629 | 7.025 | 6.568 | 6.168 | 5.683 | 3.544 | -2.871 | -7.952 | -13.059 | Primary
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NPg Best View | 18.564 | 18.506 | 18.382 | 18.252 | 18.164 | 18.098 | 18.008 | 17.632 | 15.949 | 14.584 | 13.16 | Primary
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NPg Best View | 8.752 | 8.278 | 7.531 | 6.715 | 6.157 | 5.712 | 5.188 | 2.946 | -3.159 | -7.862 | -12.871 | Primary
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NPg Best View | 4.306 | 3.634 | 3.103 | 2.481 | 1.964 | 1.475 | 0.903 | -1.655 | -7.202 | -11.315 | -15.267 | Primary
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NPg Best View | 3.065 | 2.754 | 2.303 | 1.858 | 1.544 | 1.289 | 0.979 | -0.327 | -3.533 | -5.954 | -8.504 | Primary
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NPg Best View | 8.549 | 8.519 | 8.448 | 23.758 | 23.672 | 23.584 | 23.474 | 22.817 | 21.868 | 21.314 | 20.788 | Primary
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NPg Best View | 21.073 | 20.799 | 20.781 | 20.75 | 20.731 | 20.719 | 20.705 | 20.649 | 19.899 | 19.293 | 18.705 | Primary
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NPg Best View | 19.351 | 19.205 | 18.919 | 18.59 | 18.364 | 18.195 | 17.993 | 17.147 | 14.081 | 11.725 | 9.244 | Primary
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NPg Best View | 16.827 | 17.003 | 17.163 | 17.311 | 17.447 | 17.571 | 17.679 | 18.139 | 18.439 | 18.693 | 18.921 | Primary
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NPg Best View | 14.936 | 15.092 | 15.176 | 15.23 | 15.299 | 15.361 | 15.38 | 15.362 | 14.358 | 13.686 | 13.002 | Primary
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NPg Best View | 1.488 | 1.513 | 1.393 | 1.169 | 20.828 | 20.517 | 20.099 | 17.307 | 12.486 | 9.298 | 6.475 | Primary
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NPg Best View | 7.79 | 7.487 | 7 | 6.482 | 6.093 | 5.757 | 5.37 | 3.798 | -0.379 | -3.705 | -7.109 | Primary
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NPg Best View | 6.984 | 6.686 | 6.191 | 5.63 | 5.211 | 4.825 | 4.364 | 2.356 | -1.889 | -4.905 | -7.853 | Primary
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NPg Best View | 17.765 | 17.719 | 17.628 | 17.525 | 17.409 | 17.283 | 17.133 | 16.41 | 14.797 | 13.481 | 12.279 | Primary
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NPg Best View | 6.782 | 6.701 | 6.521 | 6.329 | 6.161 | 6.007 | 5.819 | 5.046 | 2.685 | 0.857 | -0.934 | Primary
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 6.948 | 6.689 | 6.322 | 5.948 | 5.629 | 5.32 | 4.956 | 3.279 | 0.137 | -2.301 | -4.687 | Primary
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NPg Best View | 18.689 | 18.69 | 18.657 | 18.61 | 18.574 | 18.539 | 18.491 | 18.234 | 17.415 | 16.788 | 16.175 | Primary
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NPg Best View | 7.105 | 6.909 | 6.564 | 6.211 | 5.948 | 5.73 | 5.476 | 4.518 | 1.57 | -0.751 | -3.132 | Primary
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NPg Best View | 2.8 | 2.788 | 2.766 | 2.741 | 2.722 | 2.703 | 2.679 | 2.564 | 2.285 | 2.08 | 1.885 | Primary
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NPg Best View | 9.333 | 9.034 | 8.902 | 8.749 | 8.604 | 8.471 | 8.313 | 7.547 | 5.159 | 3.258 | 1.395 | Primary
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NPg Best View | 15.142 | 15.012 | 14.787 | 14.541 | 14.349 | 14.176 | 13.968 | 13.064 | 10.817 | 9.066 | 7.332 | Primary
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NPg Best View | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NPg Best View | 21.313 | 21.186 | 20.977 | 20.758 | 20.594 | 20.452 | 20.283 | 19.534 | 17.177 | 15.321 | 13.476 | Primary
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NPg Best View | 8.634 | 8.389 | 7.965 | 7.514 | 7.238 | 7.042 | 6.81 | 5.874 | 2.071 | -0.949 | -4.166 | Primary
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NPg Best View | 14.305 | 14.092 | 13.739 | 13.347 | 13.079 | 12.857 | 12.597 | 11.425 | 8.131 | 5.598 | 3.002 | Primary
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NPg Best View | 33.39 | 33.045 | 33.021 | 32.991 | 32.974 | 32.965 | 32.947 | 32.888 | 32.318 | 31.87 | 31.414 | Primary
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NPg Best View | 4.473 | 3.716 | 3.077 | 2.372 | 1.866 | 1.461 | 0.978 | -0.905 | -5.796 | -9.452 | -13.303 | Primary
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NPg Best View | 15.087 | 14.377 | 14.066 | 13.688 | 13.34 | 12.997 | 12.607 | 10.525 | 5.92 | 2.206 | -1.51 | Primary
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NPg Best View | 12.098 | 12.068 | 11.928 | 11.76 | 11.551 | 11.334 | 11.069 | 9.789 | 5.763 | 2.453 | -0.614 | Primary
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NPg Best View | 15.059 | 15.034 | 14.956 | 14.859 | 14.782 | 14.716 | 14.632 | 14.185 | 12.631 | 11.381 | 10.113 | Primary
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 24.425 | 22.646 | 22.345 | 22.021 | 21.782 | 21.563 | 21.3 | 20.191 | 17.494 | 15.381 | 13.319 | Primary
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NPg Best View | 5.358 | 4.903 | 4.567 | 4.189 | 3.864 | 3.551 | 3.193 | 1.546 | -3.089 | -7.049 | -10.915 | Primary
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NPg Best View | 1.586 | 0.848 | 0.272 | -0.32 | -0.768 | -1.139 | -1.572 | -3.392 | -9.219 | -14.07 | -19.032 | Primary
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NPg Best View | 3.41 | 3.389 | 2.065 | 2.016 | 1.973 | 1.926 | 1.861 | 1.529 | 1.127 | 0.869 | 0.63 | Primary
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NPg Best View | 8.983 | 8.596 | 10.307 | 9.998 | 9.754 | 9.518 | 9.215 | 7.826 | 3.198 | -0.511 | -4.048 | Primary
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NPg Best View | 7.354 | 7.255 | 6.989 | 6.654 | 6.495 | 6.412 | 6.306 | 5.749 | 1.203 | -2.57 | -6.55 | Primary
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NPg Best View | 32.752 | 31.396 | 31.344 | 31.278 | 31.203 | 31.123 | 31.024 | 30.479 | 28.778 | 27.331 | 25.993 | Primary
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NPg Best View | 12.288 | 12.203 | 12.008 | 11.778 | 11.589 | 11.411 | 11.198 | 10.283 | 6.518 | 3.325 | 0.326 | Primary
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NPg Best View | 9.016 | 8.367 | 8.132 | 7.923 | 7.757 | 7.606 | 7.428 | 6.755 | 4.637 | 2.952 | 1.335 | Primary
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NPg Best View | 8.936 | 9.03 | 9.079 | 9.1 | 9.154 | 9.211 | 9.247 | 9.335 | 8.476 | 7.801 | 7.074 | Primary
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NPg Best View | 14.021 | 14.013 | 13.935 | 13.822 | 13.712 | 13.604 | 13.47 | 12.83 | 10.073 | 7.801 | 5.707 | Primary
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 14.878 | 14.886 | 14.809 | 14.642 | 14.41 | 14.092 | 13.665 | 10.886 | 7.73 | 5.909 | 4.415 | Primary
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 19.018 | 18.924 | 18.744 | 18.511 | 18.372 | 18.257 | 18.116 | 17.316 | 14.031 | 11.16 | 8.187 | Primary
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NPg Best View | 5.737 | 4.75 | 4.455 | 4.109 | 3.814 | 3.541 | 3.239 | 1.759 | -1.978 | -5.081 | -8.207 | Primary
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NPg Best View | 6.026 | 4.533 | 3.44 | 2.217 | 1.275 | 0.463 | -0.462 | -4.263 | -11.967 | -17.832 | -23.873 | Primary
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NPg Best View | 13.482 | 12.692 | 12.302 | 11.945 | 11.685 | 11.466 | 11.2 | 10.11 | 7.384 | 5.298 | 3.147 | Primary
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NPg Best View | 15.884 | 15.105 | 14.692 | 14.232 | 13.886 | 13.584 | 13.228 | 11.774 | 7.144 | 3.45 | -0.156 | Primary
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NPg Best View | 10.039 | 9.938 | 9.691 | 9.396 | 9.163 | 8.955 | 8.7 | 7.633 | 4.024 | 1.111 | -1.674 | Primary
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NPg Best View | 11.177 | 11.253 | 11.317 | 11.372 | 11.419 | 11.458 | 11.486 | 11.569 | 11.486 | 11.399 | 11.304 | Primary
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NPg Best View | 21.577 | 21.534 | 21.419 | 21.262 | 21.158 | 21.071 | 20.964 | 20.518 | 18.992 | 17.784 | 16.546 | Primary
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NPg Best View | 16.425 | 16.609 | 16.762 | 16.891 | 17.013 | 17.125 | 17.217 | 17.587 | 17.042 | 16.602 | 16.174 | Primary
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 10.883 | 10.534 | 9.984 | 9.389 | 8.934 | 8.543 | 8.1 | 6.269 | 1.534 | -2.18 | -5.949 | Primary
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 22.009 | 22.004 | 21.967 | 21.927 | 21.901 | 21.883 | 21.853 | 21.721 | 21.136 | 20.66 | 20.152 | Primary
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NPg Best View | 2.755 | 2.571 | 2.189 | 1.753 | 1.441 | 1.191 | 0.894 | -0.224 | -4.804 | -8.49 | -12.162 | Primary
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NPg Best View | 6.616 | 6.607 | 6.587 | 6.562 | 6.546 | 6.533 | 6.516 | 6.44 | 6.102 | 5.831 | 5.568 | Primary
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NPg Best View | 8.199 | 7.454 | 7.178 | 6.905 | 6.699 | 6.549 | 6.37 | 5.721 | 3.479 | 1.792 | -0.054 | Primary
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NPg Best View | 13.065 | 12.573 | 11.766 | 10.852 | 10.052 | 9.29 | 8.399 | 4.224 | -5.277 | -12.722 | -19.839 | Primary
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NPg Best View | 10.593 | 9.156 | 8.298 | 7.817 | 7.438 | 7.085 | 6.656 | 4.649 | -0.869 | -5.112 | -9.234 | Primary
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NPg Best View | 3.999 | 3.873 | 3.683 | 3.471 | 3.258 | 3.036 | 2.779 | 1.497 | -0.974 | -2.976 | -4.858 | Primary
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NPg Best View | 4.018 | 3.994 | 3.957 | 3.914 | 3.867 | 3.814 | 3.749 | 3.406 | 2.915 | 2.475 | 2.049 | Primary
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NPg Best View | 3.335 | 2.979 | 24.05 | 23.757 | 23.521 | 23.292 | 22.996 | 21.232 | 17.796 | 15.398 | 12.992 | Primary
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NPg Best View | 13.976 | 13.493 | 13.146 | 12.782 | 12.49 | 12.215 | 11.879 | 10.517 | 8.503 | 7.174 | 5.91 | Primary
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NPg Best View | 4.397 | 4.269 | 4.079 | 3.875 | 3.723 | 3.584 | 3.424 | 2.771 | 1.421 | 0.364 | -0.675 | Primary
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NPg Best View | 3.634 | 3.534 | 3.387 | 3.23 | 3.086 | 2.938 | 2.761 | 1.909 | 0.553 | -0.476 | -1.442 | Primary
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 14.136 | 13.574 | 13.229 | 12.813 | 12.484 | 12.194 | 11.842 | 10.26 | 4.847 | 0.485 | -3.749 | Primary
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NPg Best View | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NPg Best View | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NPg Best View | 17.717 | 17.236 | 17.045 | 16.823 | 16.667 | 16.534 | 16.369 | 15.685 | 12.736 | 10.323 | 7.95 | Primary
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NPg Best View | 15.339 | 14.319 | 14.268 | 14.202 | 14.126 | 14.038 | 13.925 | 13.289 | 12.226 | 11.411 | 10.664 | Primary
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NPg Best View | 11.016 | 10.822 | 10.483 | 10.121 | 9.861 | 9.644 | 9.38 | 8.19 | 5.058 | 2.722 | 0.301 | Primary
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NPg Best View | 13.088 | 12.859 | 12.521 | 12.184 | 11.899 | 11.625 | 11.295 | 9.78 | 6.877 | 4.644 | 2.457 | Primary
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NPg Best View | 10.567 | 9.817 | 9.626 | 9.389 | 9.19 | 9.001 | 8.774 | 7.751 | 4.63 | 2.033 | -0.474 | Primary
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NPg Best View | 11.343 | 11.236 | 11.008 | 10.74 | 10.556 | 10.404 | 10.215 | 9.284 | 6.258 | 3.898 | 1.475 | Primary
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NPg Best View | 18.812 | 18.064 | 18.053 | 18.011 | 17.994 | 17.985 | 17.949 | 17.679 | 15.845 | 14.382 | 12.927 | Primary
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NPg Best View | 16.604 | 16.346 | 15.902 | 15.405 | 15.015 | 14.641 | 14.182 | 11.86 | 7.288 | 4.001 | 0.782 | Primary
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | 8.964 | 8.877 | 8.729 | 8.567 | 8.438 | 8.308 | 8.138 | 7.36 | 5.951 | 4.915 | 3.948 | Primary
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NPg Best View | 12.914 | 12.518 | 10.585 | 10.035 | 9.634 | 9.284 | 8.87 | 6.941 | 1.421 | -2.618 | -6.624 | Primary
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NPg Best View | 23.356 | 13.845 | 6.704 | 6.266 | 5.918 | 5.603 | 5.226 | 3.426 | -0.877 | -4.112 | -7.365 | Primary
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NPg Best View | 2.696 | 1.967 | 1.304 | -1.142 | -1.615 | -2.027 | -2.527 | -4.619 | -9.992 | -14.218 | -18.491 | Primary
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NPg Best View | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NPg Best View | 5.549 | 5.452 | 5.299 | 5.115 | 4.97 | 4.83 | 4.664 | 3.735 | 1.45 | -0.4 | -2.223 | Primary
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NPg Best View | 12.225 | 11.45 | 11.106 | 10.666 | 10.324 | 10.022 | 9.677 | 8.158 | 4.235 | 1.318 | -1.591 | Primary
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 8.106 | 6.493 | 6.385 | 6.22 | 6.132 | 6.065 | 5.963 | 5.367 | 2.477 | 0.267 | -1.95 | Primary
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 27.975 | 28.004 | 28.031 | 28.056 | 28.079 | 28.101 | 28.12 | 28.201 | 28.265 | 28.318 | 28.365 | Primary
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NPg Best View | 20.028 | 18.999 | 18.618 | 18.194 | 17.881 | 17.613 | 17.306 | 16.049 | 12.49 | 9.628 | 6.729 | Primary
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NPg Best View | 8.55 | 8.011 | 8.186 | 8.273 | 8.285 | 8.207 | 8.018 | 6.428 | 4.419 | 3.582 | 3.042 | Primary
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NPg Best View | 4.301 | 4.263 | 4.279 | 4.287 | 4.285 | 4.274 | 4.248 | 4.066 | 3.739 | 3.381 | 3.019 | Primary
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NPg Best View | 14.487 | 14.19 | 13.721 | 13.222 | 12.897 | 12.642 | 12.342 | 11.064 | 6.079 | 1.912 | -2.342 | Primary
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NPg Best View | 2.604 | 2.363 | 1.999 | 1.597 | 1.229 | 0.855 | 0.408 | -1.768 | -5.651 | -8.676 | -11.549 | Primary
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NPg Best View | 8.918 | 8.027 | 7.743 | 7.443 | 7.182 | 6.947 | 6.666 | 5.507 | 3.616 | 2.273 | 0.912 | Primary
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 25.316 | 24.837 | 24.398 | 23.898 | 23.494 | 23.117 | 22.677 | 20.665 | 15.198 | 10.767 | 6.503 | Primary
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NPg Best View | 11.842 | 11.576 | 11.082 | 10.514 | 10.125 | 9.818 | 9.456 | 7.969 | 3.201 | -0.446 | -4.239 | Primary
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NPg Best View | 11.392 | 11.087 | 10.597 | 10.064 | 9.666 | 9.322 | 8.925 | 7.175 | 1.984 | -2.261 | -6.514 | Primary
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NPg Best View | 14.122 | 13.99 | 14.121 | 14.223 | 14.337 | 14.451 | 14.54 | 14.907 | 14.218 | 13.667 | 13.073 | Primary
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NPg Best View | 32.847 | 32.521 | 32.05 | 31.567 | 31.164 | 30.776 | 30.326 | 28.306 | 23.006 | 18.493 | 14.107 | Primary
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NPg Best View | 9.865 | 8.361 | 8.313 | 8.231 | 8.163 | 8.08 | 7.949 | 7.233 | 5.108 | 3.469 | 1.962 | Primary
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NPg Best View | 8.335 | 7.655 | 7.314 | 6.936 | 6.61 | 6.311 | 5.969 | 4.548 | 0.17 | -3.503 | -7.076 | Primary
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NPg Best View | 30.752 | 30.767 | 30.779 | 30.788 | 30.8 | 30.811 | 30.82 | 30.863 | 30.858 | 30.855 | 30.847 | Primary
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NPg Best View | 9.173 | 9.18 | 24.517 | 24.428 | 24.387 | 24.373 | 24.346 | 24.245 | 22.484 | 21 | 19.456 | Primary
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NPg Best View | 8.83 | 7.239 | 21.911 | 21.562 | 21.272 | 20.996 | 20.661 | 19.157 | 14.536 | 10.805 | 7.261 | Primary
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NPg Best View | 9.603 | 9.398 | 9.098 | 8.759 | 8.437 | 8.114 | 7.735 | 5.84 | 2.462 | -0.231 | -2.851 | Primary
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NPg Best View | 12.166 | 12.093 | 11.977 | 11.858 | 11.762 | 11.669 | 11.556 | 11.125 | 10.031 | 9.133 | 8.306 | Primary
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NPg Best View | 20.336 | 19.844 | 19.772 | 19.677 | 19.615 | 19.562 | 19.483 | 19.136 | 16.693 | 14.595 | 12.582 | Primary
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NPg Best View | 11.181 | 10.849 | 10.321 | 9.796 | 9.391 | 9.014 | 8.54 | 6.393 | 1.645 | -1.865 | -5.29 | Primary
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NPg Best View | 12.365 | 12.006 | 11.701 | 11.352 | 11.091 | 10.869 | 10.612 | 9.531 | 5.358 | 1.825 | -1.664 | Primary
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NPg Best View | 11.01 | 10.473 | 10.144 | 9.778 | 9.486 | 9.216 | 8.889 | 7.521 | 3.66 | 0.483 | -2.572 | Primary
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NPg Best View | 4.907 | 4.908 | 4.873 | 4.823 | 4.797 | 4.779 | 4.752 | 4.609 | 3.685 | 2.959 | 2.239 | Primary
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NPg Best View | 4.77 | 4.77 | 4.736 | 4.679 | 4.633 | 4.589 | 4.532 | 4.201 | 3.086 | 2.27 | 1.492 | Primary
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NPg Best View | 7.565 | 7.49 | 7.359 | 7.214 | 7.1 | 7.002 | 6.883 | 6.37 | 5.22 | 4.375 | 3.522 | Primary
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NPg Best View | 7.434 | 7.352 | 7.207 | 7.042 | 6.922 | 6.824 | 6.71 | 6.211 | 4.634 | 3.415 | 2.179 | Primary
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NPg Best View | 13.202 | 13.043 | 12.779 | 12.495 | 12.238 | 11.994 | 11.714 | 10.545 | 6.526 | 2.963 | -0.422 | Primary
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 22.256 | 21.932 | 21.455 | 20.996 | 20.662 | 20.375 | 20.025 | 18.507 | 14.999 | 12.351 | 9.627 | Primary
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NPg Best View | 29.816 | 28.934 | 28.897 | 28.86 | 28.816 | 28.766 | 28.702 | 28.365 | 28.004 | 27.736 | 27.493 | Primary
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NPg Best View | 5.832 | 5.422 | 5.399 | 5.371 | 5.349 | 5.33 | 5.306 | 5.2 | 4.758 | 4.4 | 4.049 | Primary
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NPg Best View | 11.739 | 11.806 | 11.822 | 11.815 | 11.823 | 11.836 | 11.832 | 11.812 | 10.162 | 8.762 | 7.434 | Primary

## EISD Transmission
Earliest in Service Dates (EISDs) for new applications to the transmission network - to accompany a DNO's Network Headroom Report
IMPORTANT: Unlike the rest of the DNO Network Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output. Keeping customers informed continues to be Northern Powergrid's priority as the number of connection applications remains high meaning that availability of transmission capacity changes quickly. We are working with customers and the ESO to accelerate connection dates.
2024-03-28 | Transmission Owner's freeze date
Northern Powergrid (Northeast) | DNO Licence area
NGET | Transmission Owner providing
2024-03-28 | Last update (version, date)
| Generation |  | Demand
GSP | EISD | Under review at freeze date? | EISD | Under review at freeze date? | Comments (optional)
Blyth 132kV | 2032 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process | Under active review
Blyth 66kV | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process | To be reviewed with next application to transmission
Fourstones | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Hartmoor | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Hawthorn Pit | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Knaresborough | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Lackenby | 2031 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Norton | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Offerton | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Osbaldwick | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Poppleton | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Saltholme | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
South Shields | 2032 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Spennymoor | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Stella North | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Stella South | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Tynemouth | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
West Boldon | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Bradford West | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Camblesforth | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Creyke Beck | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Drax | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Elland | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Ferrybridge A | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Ferrybridge B | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Grimsby West | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Jordanthorpe | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Keadby | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Kirkstall | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Neepsend | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Norton Lees | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Pitsmoor | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Saltend North | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Sheffield City | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Skelton Grange C | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Templeborough (values assumed by NPg) | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Thorpe Marsh | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Thurcroft | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
West Melton | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Wincobank | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.nationalgrid.com/electricity-transmission/connections/regional-customer-connections-update
Purpose
To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
To accompany a DNO's Network Scenario Headroom Report of unused substation capacity at primary substations and Bulk Supply Points
To address stakeholder feedback that information in the Network Headroom Reports requires context of potential transmission restrictions to connecting at the distribution network.
Notes
1 | Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output. Keeping customers informed continues to be Northern Powergrid's priority as the number of connection applications remains high meaning that availability of transmission capacity changes quickly.
Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
2 | Northern Powergrid are undertaking numerous projects in collaboration with the other network companies to accelerate these connection dates where possible. More information will be released in 2023 and current and future customers are being kept informed.
3 | For storage, both the demand and generation EISDs may be relevant.
Where an EISD has not been established for a GSP, this is shown as N/A.
4 | There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connection, this is shown as "no date restriction identified".
5 | Where the transmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
6 | The EISDs reflect both works at a Grid Supply Point and in wider transmission network.
7 | The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long-Term Development Statement Table 3. Future GSPs may not be included.