## Conditions of use
May 2024 Northern Powergrid Capacity Heat Maps
Date Last Updated : 28/05/2024
Whilst all reasonable care has been taken in the preparation of the information and data presented within these demand and generation availability maps, Northern Powergrid are not responsible for any loss that may be attributed to the use of the data.
The classification should be used for generation connections back to the primary, and not generation that can be embedded in the network.
These are indicative and intended as a guide only for connections to the Northern Powergrid network.
The worst-case Tap Studies to determine the remaining taps for the voltage constraint were based on primary bars operating at 11.1 or 20.1kV.
If the minimum demand figure under the power flow column is negative that indicates there is existing reverse power flow through the transformers.
Upstream and physical constraints have been included only where issues are known; others have been assumed to have no issues.
The Reverse Power Flow constraint might show Red/Amber but the overall classification might still be Amber/Green as there might be enough minimum demand with reverse power flow capability.
As of the August 2022 Update, we have altered the heat maps to better reflect constraints/congestion on the transmission network, which have introduced long delays on connections at certain GSPs within Northern Powergrids network. These can be seen in the GSP Constraint tabs for each licence area. The final column in these tables give a date for connections at the GSPs which have these congestion/constraint issues. For more information please view https://customer.nationalgridet.com/s/pre-application .
We have developed these demand and generation heat maps to assist you with connections applications in constrained areas. They give a general illustration of demand and generation constraints only and cannot be relied upon to assess the terms of connection for specific premises.
Nothing in this disclaimer limits or excludes our liability for (a) death or personal injury caused by our negligence; (b) fraud or fraudulent misrepresentation; or (c) any other liability which cannot be limited or excluded by applicable law.
Subject to the above, we shall not be liable to you in tort (including negligence) or otherwise, arising under or in connection with your use of the demand and generation heat maps for: (a) loss of profits; (b) loss of sales or business; (c) loss of agreements or contracts; (d) loss of anticipated savings; (e) loss of or damage to goodwill; or (g) any indirect or consequential loss.

## Northeast Generation
Substation ID | Substation Name | Summary | Nominal Voltage |  | Transformer Capacity |  | Firm Capacity | Demand |  | Existing Generation |  | Fault Level |  |  |  | Known Constraints (Downstream) | [6 empty] | Known Constraints (Upstream) | [5 empty] | Is this an Active Network Management (ANM) area? | Additional Information | [7 empty] | Substation Class
[12 empty] | Break |  | Make
|  |  | Upstream | Downstream | [5 empty] | Upstream | Downstream
|  | Overall Primary Classification | (kV) | (kV) | OFAF (MVA) | ONAN (MVA) | Load (MVA) | Max (MVA) | Min (MVA) | (MVA) | (MVA) | Duty (kA) | Rating (kA) | Duty (kA) | Rating (kA) | Fault Level (%) | Worst Case Tap Position | Reverse Power Flow |  | Downstream Voltage Constraints | Local Physical Constraints | Downstream Substation Classification | Upstream Voltage Constraints | Generation Headroom without reinforcement for New EHV Feeder (MVA) | Generation Headroom without reinforcement for New Substation (MVA) | NGESO Statement of Works Threshold (MVA) | Upstream Constraint Levels (NPg/NGET) (MVA) | Upstream Substation Classification |  | Quoted Generation Connections (MVA) | Valid Until: | Number of Valid Quotes | Contracted Generation Connections (MVA) | Connection Date | Number of Accepted Quotes | Related Substations (Upstream) | Related Substations (Downstream) | GSP, BSP or Primary
[18 empty] | % | MVA
9832 | Foss Islands | RED | 33 | 11 | 30 | 15 | 36 | 27.6261 | 4.0883 | -14.149 | -1.222 | 8.99 | 13.1 | 29.42 | 32.8 | 89.6951 | 7 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -0.357 | N/A | N/A | 9838-33 |  | Primary
9891-11 | Harrogate 132/11kV | RED | 132 | 11 | 30 | 15 | 36 | 32.243 | 4.35 | -89.389 | -0.363 | 14.43 | 25 | 43.53 | 62.5 | 69.648 | Not Used | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 34.35 | >1.000 | >0.000 | NOT USED | No | None | N/A | N/A | N/A | N/A | N/A | 2810936 |  | BSP
9901 | Oatlands | RED | 33 | 11 | 18.75 | 15 | 22.9 | 9.7962 | 1.2483 | -17.944 | -0.123 | 8.7697 | 13.1 | 25.9974 | 33.4 | 77.8365 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.2718 | 19.2718 | >1.000 | 19.2718 | RED | No | None | N/A | N/A | -0.632 | N/A | N/A | 9891-33 |  | Primary
9903 | Starbeck | RED | 33 | 11 | 18.75 | 15 | 22.9 | 20.1596 | 3.5244 | -17.944 | -0.921 | 8.74 | 13.1 | 24.91 | 33.4 | 74.5808 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | VOLTAGE OUT OF STATUTORY LIMIT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.496 | N/A | N/A | 9891-33 |  | Primary
7490443 | Barden Friar | RED | 33 | 20 | 7.5 | 7.5 | 5 | 0.9375 | 0.157 | -29.03 | 0 | 3.58 | 25 | 7.4 | 62.5 | 14.32 | 5 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9875 |  | Primary
9877 | Bedale | RED | 33 | 11 | 24 | 12 | 22 | 17.55 | 3.7485 | -29.03 | -2.542 | 9.03 | 13.1 | 24.06 | 32.8 | 73.3537 | 8 | 62.5% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9875 |  | Primary
9878 | Catterick Camp | RED | 33 | 11 | 18.75 | 15 | 24 | 16.8154 | 1.1702 | -29.03 | -0.095 | 10.42 | 25 | 27.01 | 62.5 | 43.216 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.263 | N/A | N/A | 9875 |  | Primary
9881 | Northallerton | RED | 33 | 11 | 18.75 | 15 | 24 | 17.7604 | 3.1038 | -29.03 | -10.363 | 9.28 | 25 | 24.58 | 62.5 | 39.328 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.677 | N/A | N/A | 9875 |  | Primary
2826869 | Romanby | RED | 33 | 11 | 10.1 | 10.1 | 8 | 6.0633 | 0.46308 | -29.03 | 0 | 4.15 | 25 | 10.17 | 62.5 | 16.6 | 6 | 100% | 10.1 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.421 | N/A | N/A | 9875 |  | Primary
9882-2 | Richmond T2 | RED | 33 | 11 | 24 | 12 | 24 | 3.5 | 0.090829 | -35.132 | -1.626 | 8.07 | 13.1 | 20.98 | 33.4 | 62.8144 | 1 | 50% | 6 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9819 |  | Primary
9883 | Thirsk | RED | 33 | 11 | 14 | 10 | 14 | 13.1114 | 0.75517 | -29.03 | -5.813 | 5.6 | 13.1 | 13.7 | 33.4 | 42.7481 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.174 | N/A | N/A | 9875 |  | Primary
9884 | Wensleydale | RED | 33 | 11 | 14 | 10 | 19 | 10.5021 | 1.3942 | -29.03 | -0.743 | 5.29 | 13.1 | 12.7 | 32.8 | 40.3817 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.158 | N/A | N/A | 9875 |  | Primary
9845 | Kirbymoorside | RED | 66 | 11 | 24 | 12 | 24 | 9.86 | 1.3911 | -7.162 | -0.08 | 7.34 | 13.1 | 20.18 | 32.8 | 61.5244 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9835 |  | Primary
9846 | Malton | RED | 66 | 11 | 32 | 16 | 32 | 23.9172 | 3.6676 | -7.162 | -0.575 | 8.13 | 20 | 25.96 | 50 | 51.92 | 2 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9835 |  | Primary
9849 | Sheriff Hutton | RED | 66 | 11 | 18.75 | 15 | 24 | 11.6194 | 0.23029 | -7.162 | -5.016 | 7.7469 | 13.1 | 20.1812 | 32.8 | 61.528 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9835 |  | Primary
9865 | Thornton Dale | RED | 66 | 11 | 24 | 12 | 19.5 | 11.6409 | 1.1473 | -7.162 | -1.053 | 8.72 | 20 | 24.24 | 50 | 48.48 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9835 |  | Primary
2522850 | Yedingham | RED | 66 | 11 | 24 | 12 | 8 | 2.8839 | 0.68714 | -7.162 | -0.438 | 4.42 | 25 | 12.4 | 62.5 | 19.84 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -10.421 | N/A | N/A | 9835 |  | Primary
9841 | Campleshon Road | RED | 33 | 11 | 18.75 | 15 | 24 | 16.5051 | 2.0673 | -14.149 | 0 | 9.83 | 13.1 | 28.9 | 33.4 | 86.5269 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -0.095 | N/A | N/A | 9838-33 |  | Primary
2524256 | Elvington | RED | 33 | 11 | 24 | 12 | 20 | 12.23 | 2.7935 | -14.149 | -0.355 | 8.87 | 25 | 22.68 | 62.5 | 36.288 | 2 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -0.453 | N/A | N/A | 9838-33 |  | Primary
9843 | Haxby Road T2 T3 | RED | 33 | 11 | 15 | 11.25 | 14 | 11.2 | 1.5077 | -14.149 | 0 | 8.77 | 13.1 | 25.12 | 33.4 | 75.2096 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9838-33 |  | Primary
9844 | Huntington New Lane | RED | 33 | 11 | 24 | 12 | 24 | 17.7512 | 5.1399 | -14.149 | -0.078 | 9.54 | 20 | 30.46 | 50 | 60.92 | 4 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -1 | N/A | N/A | 9838-33 |  | Primary
9838-11 | Melrosegate 33/11kV | RED | 33 | 11 | 30 | 15 | 32 | 27.5772 | 0.96804 | -14.149 | 0 | 8.48 | 25 | 25.52 | 62.5 | 40.832 | 4 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -6.721 | N/A | N/A | 9838-33 |  | Primary
9847 | Rawcliffe Lane | RED | 33 | 11 | 18.75 | 15 | 24 | 20.111 | 3.7379 | -14.149 | -0.21 | 11.27 | 13.1 | 31.19 | 33.4 | 93.3832 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -0.091 | N/A | N/A | 9838-33 |  | Primary
9851 | York University | RED | 33 | 11 | 24 | 12 | 24 | 13.2087 | 1.5101 | -14.149 | -3.284 | 10.17 | 13.1 | 31.12 | 33.4 | 93.1737 | 4 | 100% | 24 | NO VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 1.3557 | 1.3557 | >1.000 | 1.3557 | RED | No | None | N/A | N/A | -2.105 | N/A | N/A | 9838-33 |  | Primary
9861 | Eastfield | RED | 33 | 11 | 32 | 16 | 30.3 | 19.1214 | 4.7938 | -5.781 | -3.52 | 11.75 | 12.5 | 35.67 | 31.3 | 113.9617 | 5 | 100% | 32 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.5289 | 24.5289 | >1.000 | 24.5289 | RED | No | None | N/A | N/A | -0.293 | N/A | N/A | 9858 |  | Primary
9862 | Newby | RED | 33 | 11 | 24 | 12 | 24 | 11.9458 | 1.7279 | -5.781 | -0.422 | 9.48 | 13.1 | 26.1 | 32.8 | 79.5732 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 21.2907 | 1.6149 | >1.000 | 21.2907 | RED | No | None | N/A | N/A | -0.113 | N/A | N/A | 9858 |  | Primary
9863 | North Street | RED | 33 | 11 | 24 | 12 | 24 | 11.3235 | 1.6664 | -5.781 | 0 | 9.33 | 13.1 | 25.54 | 32.8 | 77.8659 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 21.9672 | 1.6664 | >1.000 | 21.9672 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9858 |  | Primary
3363742 | Ravenscar | RED | 33 | 11 | 10 | 10 | 8 | 1.7 | 0.22905 | -5.781 | -0.18 | 4.74 | 25 | 13.5 | 62.5 | 21.6 | 1 | 100% | 10 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 32.4208 | 10.229 | >1.000 | 32.4208 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9858 |  | Primary
9864 | Scarborough 33/11kV | RED | 33 | 11 | 32 | 16 | 32 | 18.82 | 5.325 | -5.781 | -1.659 | 11.92 | 20 | 33.99 | 50 | 67.98 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 28.8435 | 5.325 | >1.000 | 28.8435 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9858 |  | Primary
9866-1 | Whitby T1 | RED | 33 | 11 | 24 | 12 | 19.1 | 4.11 | 0.083138 | -5.781 | 0 | 7.68 | 20 | 19.13 | 50 | 38.4 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 16.8458 | 12.0831 | >1.000 | 16.8458 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9858 |  | Primary
9867-1 | Whitby West T1 | RED | 33 | 11 | 24 | 12 | 24 | 4.75 | 0.069914 | -5.781 | 0 | 7.21 | 13.1 | 18.27 | 32.8 | 55.7012 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 16.5854 | 12.0699 | >1.000 | 16.5854 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9858 |  | Primary
9898 | Boroughbridge | RED | 33 | 11 | 15 | 7.5 | 15 | 9.9331 | 1.36 | -31.459 | -0.06 | 6.74 | 20 | 17.49 | 50 | 34.98 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9897-33 |  | Primary
2822141 | Roecliffe Industrial | RED | 33 | 11 | 24 | 12 | 15 | 9.9331 | 1.35 | -31.459 | 0 | 6.82 | 25 | 17.87 | 62.5 | 28.592 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 2.756 | 2.756 | >1.000 | 2.756 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9897-33 |  | Primary
9899 | Coneythorpe | RED | 33 | 11 | 24 | 12 | 22 | 12.5169 | 1.3746 | -31.459 | -5.872 | 9.25 | 13.1 | 25.29 | 32.8 | 77.1037 | 1 | 50% | 12 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 2.756 | 2.756 | >1.000 | 2.756 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9897-33 |  | Primary
7129903 | Darley | RED | 33 | 11 | 10 | 10 | 8 | 4.1773 | 0 | -31.459 | 0 | 3.68 | 25 | 9.12 | 62.5 | 14.72 | 2 | 100% | 10 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | SOME VOLTAGE CONSTRAINT | 2.756 | 2.756 | >1.000 | 2.756 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9897-33 |  | Primary
9902 | Ripon | RED | 33 | 11 | 24 | 12 | 24 | 23.3692 | 5.0299 | -31.459 | -0.58 | 7.27 | 13.1 | 19.57 | 32.8 | 59.6646 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 2.756 | 2.756 | >1.000 | 2.756 | RED | No | None | N/A | N/A | -0.126 | N/A | N/A | 9897-33 |  | Primary
9897-11 | Wormald Green 132/11kV | RED | 132 | 11 | 30 | 15 | 36 | 8.41 | 1.278 | -89.389 | -0.446 | 13.98 | 20 | 37.94 | 50 | 75.88 | Not Used | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 22.857 | >1.000 | >0.000 | NOT USED | No | None | N/A | N/A | -8.421 | N/A | N/A | 2810936 |  | BSP
9893-11 | Husthwaite 33/11kV | RED | 33 | 11 | 15 | 7.5 | 15 | 10.5112 | 0.49883 | -39.177 | -6.505 | 6.56 | 25 | 18.25 | 62.5 | 29.2 | 4 | 100% | 15 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -5.499 | N/A | N/A | 9893-33 |  | Primary
2530198 | Sessay Bridge | RED | 33 | 11 | 24 | 12 | 12 | 9.7469 | 2.2 | -39.177 | -4.251 | 5.0626 | 25 | 12.8284 | 62.5 | 20.5254 | 1 | 100% | 12 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.211 | N/A | N/A | 9893-33 |  | Primary
2541519 | Sowerby | RED | 33 | 11 | 24 | 12 | 12 | 9.7469 | 0.22 | -39.177 | 0 | 4.66 | 25 | 10.54 | 62.5 | 18.64 | 1 | 100% | 12 | OUT OF TAPS | High Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9893-33 |  | Primary
9760 | Acklam | RED | 33 | 11 | 24 | 12 | 22.8 | 17.5401 | 5.6854 | -18.878 | 0 | 8.32 | 13.1 | 24.78 | 32.8 | 75.5488 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 37.1544 | 16.8004 | >1.000 | 37.1544 | RED | No | None | N/A | N/A | -0.885 | N/A | N/A | 9785-33 |  | Primary
9785-33-11 | Bowesfield 33/11kV | RED | 33 | 11 | 32 | 16 | 32 | 13.1477 | 2.253 | -18.878 | 0 | 11.31 | 13.1 | 33.91 | 33.4 | 101.5269 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 28.9665 | 0 | >1.000 | 28.9665 | RED | No | None | N/A | N/A | -14.39 | N/A | N/A | 9785-33 |  | Primary
9768 | Millbank Lane | RED | 33 | 11 | 18.75 | 15 | 22.8 | 18.078 | 2.9982 | -18.878 | -0.032 | 11.22 | 13.1 | 33.04 | 32.8 | 100.7317 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 35.8108 | 21.5742 | >1.000 | 35.8108 | RED | No | None | N/A | N/A | -0.174 | N/A | N/A | 9785-33 |  | Primary
9771 | Rudby | RED | 33 | 11 | 15 | 7.5 | 8.38 | 4.6524 | 0.84793 | -18.878 | 0 | 6.03 | 13.1 | 14.87 | 32.8 | 46.0305 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 16.0606 | 0.84793 | >1.000 | 16.0606 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9785-33 |  | Primary
9774 | Stokesley | RED | 33 | 11 | 24 | 12 | 13.11 | 7.4555 | 0.20805 | -18.878 | -4.151 | 8.06 | 25 | 20.71 | 62.5 | 33.136 | 2 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.276 | N/A | N/A | 9785-33 |  | Primary
9796 | Urlay Nook | RED | 33 | 11 | 24 | 12 | 48 | 17.8535 | 0.70159 | -18.878 | -3.895 | 11.37 | 13.1 | 32.9 | 32.8 | 100.3049 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.6641 | 0.64859 | >1.000 | 20.6641 | RED | No | None | N/A | N/A | -0.053 | N/A | N/A | 9785-33 |  | Primary
9803 | Belmont | RED | 66 | 11 | 32 | 16 | 32 | 22.2016 | 4.2635 | -14.631 | -6.331 | 10.929 | 13.1 | 32.1271 | 32.8 | 97.9485 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.811 | N/A | N/A | 9810-66 |  | Primary
9805 | Durham East | RED | 66 | 11 | 18.75 | 12 | 22.5 | 18.9093 | 3.8938 | -14.631 | -0.221 | 9.3 | 13.1 | 28.02 | 32.8 | 85.4268 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.137 | N/A | N/A | 9810-66 |  | Primary
9743 | High Flatts | RED | 66 | 11 | 18.75 | 15 | 24 | 16.0183 | 3.9202 | -14.631 | -0.079 | 8.67 | 13.1 | 23.65 | 32.8 | 72.1037 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.105 | N/A | N/A | 9810-66 |  | Primary
9810-20 | Potter House T1 T3 | RED | 66 | 20 | 25 | 20.5 | 28 | 15.9665 | 1.7521 | -14.631 | -8 | 6.55 | 20 | 19.54 | 50 | 39.08 | 1 | 100% | 25 | OUT OF TAPS | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9810-66 |  | Primary
9804 | Brancepeth | RED | 66 | 20 | 40 | 20 | 28 | 14.04 | 0.82927 | -69.96 | -14.131 | 6.92 | 9.2 | 19.82 | 23.5 | 84.3404 | 5 | 100% | 40 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9811-66 |  | Primary
9807 | Fishburn | RED | 66 | 20 | 25 | 20 | 28 | 17.4162 | 0.85989 | -69.96 | -27.091 | 6.7 | 25 | 20.19 | 62.5 | 32.304 | 1 | 100% | 25 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.263 | N/A | N/A | 9811-66 |  | Primary
9808 | Low Spennymoor | RED | 66 | 11 | 24 | 12 | 24 | 0 | 1.3954 | -69.96 | 0 | 8.79 | 13.1 | 25.98 | 32.8 | 79.2073 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9811-66 |  | Primary
9809 | Meadowfield | RED | 66 | 11 | 24 | 12 | 24 | 12.8797 | 0.34315 | -69.96 | -8.151 | 8.97 | 20 | 26 | 50 | 52 | 2 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9811-66 |  | Primary
9826 | Skerneside | RED | 66 | 20 | 40 | 20 | 34 | 19.8652 | 4.6376 | -69.96 | -2.536 | 8.11 | 20 | 25.29 | 50 | 50.58 | 1 | 0% | 0 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.158 | N/A | N/A | 9811-66 |  | Primary
9811-20 | Spennymoor 66/20kV | RED | 66 | 20 | 44 | 22 | 44 | 16.7797 | 3.1377 | -69.96 | -1.209 | 6.79 | 9.2 | 21.08 | 23.5 | 89.7021 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9811-66 |  | Primary
9783 | Amberton Road | RED | 66 | 11 | 40 | 20 | 40 | 23.2551 | 6.1849 | -103.774 | -2 | 9.07 | 25 | 28.05 | 62.5 | 44.88 | 3 | 100% | 40 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9787-66 |  | Primary
9786 | Brenda Trading | RED | 66 | 11 | 32 | 16 | 29.4 | 22.5843 | 0.15824 | -103.774 | 0 | 9.96 | 13.1 | 29.23 | 32.8 | 89.1159 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.105 | N/A | N/A | 9787-66 |  | Primary
9787-20 | Hartmoor 66/20kV | RED | 66 | 20 | 25 | 18.75 | 28 | 22.3607 | 0.8653 | -103.774 | -5.831 | 6.82 | 20 | 20.45 | 50 | 40.9 | 2 | 100% | 25 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -8.853 | N/A | N/A | 9787-66 |  | Primary
2569052 | Peterlee West | RED | 66 | 11 | 32 | 16 | 32 | 10.6192 | 0.18879 | -103.774 | -14.826 | 9.87 | 25 | 29.47 | 62.5 | 47.152 | 3 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9787-66 |  | Primary
2541255 | Wynyard | RED | 66 | 11 | 40 | 20 | 40 | 38.2 | 0.19364 | -103.774 | -28.597 | 10.45 | 25 | 28.99 | 62.5 | 46.384 | 1 | 100% | 40 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -6.316 | N/A | N/A | 9787-66 |  | Primary
9806 | Eastgate Cement | RED | 66 | 20 | 25 | 20 | 26 | 9.7628 | 0.14023 | -29.097 | 0 | 4.9 | 9.2 | 13.15 | 23.5 | 55.9574 | 1 | 100% | 25 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 2.111 | 2.111 | >1.000 | 2.111 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9812-66 |  | Primary
9821 | Fylands Bridge | RED | 66 | 11 | 18.75 | 15 | 25.2 | 20.3149 | 3.1396 | -29.097 | -0.3 | 9.29 | 13.1 | 28.11 | 32.8 | 85.7012 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 2.111 | 2.111 | >1.000 | 2.111 | RED | No | None | N/A | N/A | -0.087 | N/A | N/A | 9812-66 |  | Primary
9822 | Harmire Bridge | RED | 66 | 20 | 40 | 20 | 28 | 13.6235 | 2.7074 | -29.097 | -2.426 | 5.23 | 9.2 | 14.68 | 23.5 | 62.4681 | 2 | 100% | 40 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 2.111 | 2.111 | >1.000 | 2.111 | RED | No | None | N/A | N/A | -7.368 | N/A | N/A | 9812-66 |  | Primary
9812-20 | Toronto 66/20kV | RED | 66 | 20 | 40 | 20 | 40 | 16.0611 | 2.9298 | -29.097 | -2.371 | 6.43 | 9.2 | 20.88 | 23.5 | 88.8511 | 6 | 100% | 40 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 2.111 | 2.111 | >1.000 | 2.111 | RED | No | None | N/A | N/A | -14.211 | N/A | N/A | 9812-66 |  | Primary
9741 | Hawthorn Pit | RED | 66 | 20 | 25 | 20 | 28 | 20.93 | 40 | -72.3 | -12.95 | 6.98 | 9.2 | 20.17 | 23.5 | 85.8298 | 1 | 100% | 25 | OUT OF TAPS | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.751 | N/A | N/A | 9918 |  | Primary
9745 | Houghton | RED | 66 | 11 | 24 | 12 | 24 | 16.54 | 1.6991 | -72.3 | -7.1 | 8.37 | 13.1 | 23.9 | 32.8 | 72.8659 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.143 | N/A | N/A | 9918 |  | Primary
9746 | Peterlee Industrial | RED | 66 | 11 | 24 | 12 | 20 | 8.43 | 0.11238 | -72.3 | -43.12 | 8.93 | 13.1 | 26.55 | 32.8 | 80.9451 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -4 | N/A | N/A | 9918 |  | Primary
9747 | Shotton | RED | 66 | 11 | 18.75 | 15 | 24.6 | 14.3729 | 4.3257 | -72.3 | 0 | 10.0621 | 13.1 | 28.9621 | 33.4 | 86.7129 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.411 | N/A | N/A | 9918 |  | Primary
9748 | Stoney Cut | RED | 66 | 20 | 25 | 18.75 | 31.9 | 17.0575 | 1.1262 | -72.3 | -8.895 | 7.06 | 20 | 20.2 | 50 | 40.4 | 1 | 100% | 25 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -11.747 | N/A | N/A | 9918 |  | Primary
9726 | Tunstall | RED | 66 | 11 | 25 | 18.75 | 30.5 | 19.2565 | 5.0299 | -72.3 | -0.235 | 12.13 | 13.1 | 33.36 | 32.8 | 101.7073 | 2 | 100% | 25 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.221 | N/A | N/A | 9918 |  | Primary
9721 | Mount Road | RED | 33 | 11 | 24 | 12 | 24 | 20.84 | 3.5645 | -1.852 | -1.852 | 9.98 | 13.1 | 29.8 | 32.8 | 90.8537 | 2 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 26.1122 | 26.1122 | >50.632 | 26.1122 | RED | No | None | N/A | N/A | -0.421 | N/A | N/A | 9717-33 |  | Primary
9717-11 | Offerton 33/11kV | RED | 33 | 11 | 32 | 16 | 32 | 17.61 | 3.7577 | -1.852 | 0 | 10.37 | 25 | 30.52 | 62.5 | 48.832 | 2 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 29.5728 | 29.5728 | >50.632 | 29.5728 | RED | No | None | N/A | N/A | -0.714 | N/A | N/A | 9717-33 |  | Primary
9724 | Pallion Trading | RED | 33 | 11 | 24 | 12 | 24 | 18.072 | 3.3748 | -1.852 | 0 | 10 | 13.1 | 29.01 | 33.4 | 86.8563 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 23.3187 | 15.3748 | >50.632 | 23.3187 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9717-33 |  | Primary
9842 | Gale Lane | RED | 33 | 11 | 24 | 12 | 24 | 9.17 | 0.9245 | -9.251 | -8.263 | 9.94 | 25 | 27.98 | 62.5 | 44.768 | 4 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9839 |  | Primary
2537397 | Moor Monkton Pumps | RED | 33 | 11 | 24 | 12 | 8 | 5.9444 | 1.6819 | -9.251 | -0.2 | 4.76 | 25 | 12.36 | 62.5 | 19.776 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9839 |  | Primary
9848 | Severus Hill | RED | 33 | 11 | 24 | 12 | 24 | 12.71 | 2.1026 | -9.251 | -0.788 | 9.5699 | 13.1 | 27.6339 | 32.8 | 84.2497 | 6 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9839 |  | Primary
9850 | Skeldergate | RED | 33 | 11 | 32 | 16 | 32 | 14.5104 | 2.3279 | -9.251 | 0 | 10.75 | 13.1 | 30.92 | 32.8 | 94.2683 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9839 |  | Primary
9879 | Cowton | RED | 33 | 11 | 7.5 | 7.5 | 7.5 | 1.4185 | 0.28992 | -8.472 | 0 | 2.75 | 6 | 6.65 | 15 | 45.8333 | 6 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 14.637 | 7.7899 | >1.000 | 14.637 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9928-33 |  | Primary
9927-11 | Darlington 33/11kV | RED | 33 | 11 | 18.75 | 15 | 24 | 15.21 | 3.3634 | -8.472 | 0 | 9.7 | 13.1 | 28.78 | 32.8 | 87.7439 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 14.637 | 14.637 | >1.000 | 14.637 | RED | No | None | N/A | N/A | -3.579 | N/A | N/A | 9928-33 |  | Primary
9928-11 | Darlington Central 33/11kV | RED | 33 | 11 | 32 | 16 | 32 | 9.6 | 1.1432 | -8.472 | -0.179 | 9.86 | 25 | 29.1 | 62.5 | 46.56 | 2 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 14.637 | 14.637 | >1.000 | 14.637 | RED | No | None | N/A | N/A | -5.421 | N/A | N/A | 9928-33 |  | Primary
9818 | Darlington East | RED | 33 | 11 | 24 | 12 | 24 | 17.1191 | 1.7085 | -8.472 | -8.293 | 8.9 | 13.1 | 26.44 | 32.8 | 80.6098 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 14.637 | 13.4985 | >1.000 | 14.637 | RED | No | None | N/A | N/A | -0.21 | N/A | N/A | 9928-33 |  | Primary
9646 | Ashington | RED | 66 | 11 | 18.75 | 15 | 24 | 17.2504 | 1.5171 | -139.267 | -7.66 | 10.41 | 13.1 | 30.55 | 32.8 | 93.1402 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
9607 | Benton Square | RED | 66 | 11 | 18.75 | 15 | 24 | 17.6374 | 2.941 | -139.267 | -0.189 | 9.45 | 13.1 | 27.45 | 33.4 | 82.1856 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.169 | N/A | N/A | 9915-66 |  | Primary
9610-1 | Cramlington T1 T3 | RED | 66 | 11 | 18.75 | 15 | 24 | 11.7211 | 3.2823 | -139.267 | 0 | 10.1 | 13.1 | 30.49 | 33.4 | 91.2874 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
9628-1 | Fawdon T1 | RED | 66 | 20 | 25 | 18.75 | 25 | 19.8601 | 1.8 | -139.267 | -2.335 | 5.34 | 9.2 | 13.41 | 23.5 | 58.0435 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
9611 | Seaton Burn T1 | RED | 66 | 20 | 25 | 18.75 | 25 | 19.8601 | 1.8 | -139.267 | 0 | 5.66 | 9.2 | 14.67 | 23.5 | 62.4255 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.347 | N/A | N/A | 9915-66 |  | Primary
9649 | Maddison Street | RED | 66 | 11 | 24 | 12 | 24 | 16.7691 | 2.5556 | -139.267 | -0.016 | 9.14 | 13.1 | 28.92 | 33.4 | 86.5868 | 4 | 50% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.055 | N/A | N/A | 9915-66 |  | Primary
9650 | Morpeth | RED | 66 | 20 | 30 | 15 | 28 | 16.86 | 0.94173 | -139.267 | -15.151 | 6.73 | 9.2 | 18.3 | 23.5 | 77.8723 | 1 | 100% | 30 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -1.723 | N/A | N/A | 9915-66 |  | Primary
9653 | Reservoir | RED | 66 | 20 | 30 | 15 | 30 | 19.1831 | 3.4502 | -139.267 | -0.583 | 6.97 | 9.2 | 20.32 | 23.5 | 86.4681 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
7189886 | Seghill | RED | 66 | 11 | 32 | 16 | 32 | 10.26 | 4.1573 | -139.267 | -4.084 | 11.55 | 25 | 30.67 | 62.5 | 49.072 | 3 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.737 | N/A | N/A | 9915-66 |  | Primary
9655 | Wansbeck | RED | 66 | 11 | 36 | 18 | 32 | 0.31049 | 0.15297 | -139.267 | 0 | 11.39 | 13.1 | 30.84 | 32.8 | 94.0244 | 3 | 50% | 18 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
2771500 | West Hartford | RED | 66 | 11 | 24 | 12 | 16 | 4.62 | 0.22988 | -139.267 | -4 | 11.4 | 25 | 29.09 | 62.5 | 46.544 | 3 | 100% | 24 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
9662 | Denwick | RED | 66 | 20 | 25 | 20 | 30 | 22.5222 | 1.9852 | -81.642 | -0.559 | 5.48 | 9.2 | 16.67 | 23.5 | 70.9362 | 1 | 100% | 25 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 8.528 | 8.528 | >1.000 | 8.528 | RED | No | None | N/A | N/A | -0.189 | N/A | N/A | 9645-66 |  | Primary
9645-20 | Linton 66/20kV | AMBER | 66 | 20 | 24 | 12 | 28 | 10.188 | 1.1213 | -81.642 | 0 | 6.28 | 9.2 | 18.57 | 23.5 | 79.0213 | 3 | 100% | 24 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 8.528 | 8.528 | >1.000 | 8.528 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9645-66 |  | Primary
9648 | Lynemouth | RED | 66 | 20 | 37.5 | 30 | 38 | 2.3 | 0.01 | -81.642 | -2.42 | 6.65 | 9.2 | 18.23 | 23.5 | 77.5745 | 1 | 100% | 37.5 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 8.528 | 8.528 | >1.000 | 8.528 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9645-66 |  | Primary
9663 | Warkworth | RED | 66 | 20 | 25 | 18.75 | 25 | 17.22 | 2.3697 | -81.642 | -0.084 | 6.04 | 10.1 | 17.72 | 25.8 | 68.6822 | 1 | 100% | 25 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 8.528 | 8.528 | >1.000 | 8.528 | RED | No | None | N/A | N/A | -0.053 | N/A | N/A | 9645-66 |  | Primary
9629 | Fossway 33/11kV | RED | 33 | 11 | 24 | 12 | 24 | 16.1345 | 3.8429 | -8.531 | -0.9 | 9.5095 | 20 | 28.7094 | 50 | 57.4188 | 4 | 50% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 21.611 | 15.8429 | >1.000 | 21.611 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9623-33 |  | Primary
9623-11 | Gosforth 33/11kV | RED | 33 | 11 | 32 | 16 | 32 | 18.06 | 6.5541 | -8.531 | 0 | 9.24 | 25 | 27.37 | 62.5 | 43.792 | 2 | 100% | 32 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 31.117 | 31.117 | >1.000 | 31.117 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9623-33 |  | Primary
9614 | Killingworth | RED | 33 | 11 | 24 | 12 | 24 | 18.6058 | 6.72 | -8.531 | -6 | 9.52 | 13.1 | 29.31 | 32.8 | 89.3598 | 1 | 50% | 12 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.9913 | 17.773 | >1.000 | 24.9913 | RED | No | None | N/A | N/A | -0.947 | N/A | N/A | 9623-33 |  | Primary
9631 | Longbenton | RED | 33 | 11 | 18.75 | 15 | 24 | 17.3167 | 3.8442 | -8.531 | -1.631 | 10.76 | 18 | 31.85 | 45 | 70.7778 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.7384 | 22.5212 | >1.000 | 22.7384 | RED | No | None | N/A | N/A | -0.073 | N/A | N/A | 9623-33 |  | Primary
9612 | Flatworth Central | RED | 33 | 11 | 32 | 16 | 32 | 16.751 | 2.1513 | -30.737 | 0 | 9.51 | 20 | 28.71 | 50 | 57.42 | 4 | 100% | 32 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.204 | 24.204 | >1.000 | 24.204 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9910 |  | Primary
9613 | Howdon | RED | 33 | 11 | 18.75 | 15 | 24 | 7.5448 | 1.5917 | -30.737 | -12.316 | 10.82 | 13.1 | 29.79 | 33.4 | 89.1916 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 16.4435 | 16.4435 | >1.000 | 16.4435 | RED | No | None | N/A | N/A | -1.052 | N/A | N/A | 9910 |  | Primary
9617 | Willington | RED | 33 | 11 | 18.75 | 15 | 24 | 12.8499 | 2.983 | -30.737 | 0 | 10.66 | 13.1 | 28.73 | 33.4 | 86.018 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.1392 | 20.1392 | >1.000 | 20.1392 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9910 |  | Primary
9608 | Billy Mill | RED | 33 | 11 | 18.75 | 15 | 24 | 17.1105 | 4.0964 | -4.382 | -2.58 | 9.17 | 13.1 | 27.52 | 33.4 | 82.3952 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.1209 | 20.1209 | >1.000 | 20.1209 | RED | No | None | N/A | N/A | -0.989 | N/A | N/A | 9605 |  | Primary
9615 | Monkseaton | RED | 33 | 11 | 18.75 | 15 | 24 | 17.1186 | 4.2271 | -4.382 | -1.802 | 8.54 | 13.1 | 24.65 | 33.4 | 73.8024 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.7612 | 20.7612 | >1.000 | 20.7612 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9605 |  | Primary
9616 | Tynemouth Central | RED | 33 | 11 | 18.75 | 15 | 24 | 15.7555 | 3.9816 | -4.382 | 0 | 8.49 | 20 | 23.5 | 50 | 47 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.6385 | 20.6385 | >1.000 | 20.6385 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9605 |  | Primary
9693 | Garwood Street | RED | 33 | 11 | 32 | 16 | 32 | 17.5762 | 4.6724 | -37.208 | -0.206 | 11.81 | 12.5 | 35.14 | 31.25 | 112.448 | 4 | 100% | 32 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 23.1516 | 23.1516 | >15.789 | 23.1516 | RED | No | None | N/A | N/A | -0.242 | N/A | N/A | 9690 |  | Primary
9697 | Jarrow | RED | 33 | 11 | 18.75 | 15 | 24 | 6.8014 | 0.11577 | -37.208 | 0 | 10.1408 | 13.1 | 27.3277 | 33.4 | 81.8195 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 18.7056 | 18.7056 | >15.789 | 18.7056 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9690 |  | Primary
9698 | Simonside | RED | 33 | 11 | 24 | 12 | 24 | 13.1803 | 2.4441 | -37.208 | -0.16 | 9.51 | 13.1 | 27.28 | 32.8 | 83.1707 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.0274 | 13.1181 | >15.789 | 22.0274 | RED | No | None | N/A | N/A | -1.326 | N/A | N/A | 9690 |  | Primary
9701 | Westoe | RED | 33 | 11 | 24 | 12 | 24 | 10.816 | 2.479 | -37.208 | 0 | 9.26 | 13.1 | 25.58 | 32.8 | 77.9878 | 1 | 50% | 12 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 31.6895 | 14.479 | >15.789 | 31.6895 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9690 |  | Primary
9739-20 | Annfield 66/20kV | RED | 66 | 20 | 25 | 18.75 | 28 | 21.0004 | 1.5347 | -34.124 | -11.631 | 6.14 | 9.2 | 17.58 | 23.5 | 74.8085 | 2 | 100% | 25 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.122 | N/A | N/A | 9739-66 |  | Primary
2707936 | Consett | RED | 66 | 20 | 40 | 20 | 40 | 22.9647 | 0.41464 | -34.124 | -22.493 | 6.86 | 25 | 18.99 | 62.5 | 30.384 | 4 | 100% | 40 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.192 | N/A | N/A | 9739-66 |  | Primary
9749 | Tanfield | RED | 66 | 11 | 32 | 16 | 32 | 13.41 | 2.2822 | -34.124 | 0 | 9.08 | 13.1 | 26.44 | 32.8 | 80.6098 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.756 | N/A | N/A | 9739-66 |  | Primary
2841083 | Newburn Haugh | RED | 132 | 11 | 30 | 22.5 | 38.1 | 6.6068 | 1.3434 | -34.613 | 0 | 9.58 | 25 | 26.81 | 62.5 | 42.896 | Not Used | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 20.8174 | >1.000 | 0 | RED | No | None | N/A | N/A | -10.526 | N/A | N/A | 9912 |  | BSP
9621-11 | Blucher 33/11kV | RED | 33 | 11 | 24 | 12 | 24 | 14.8805 | 3.7742 | -3.579 | 0 | 12.05 | 17.5 | 35.12 | 44.6 | 78.7444 | 1 | 50% | 12 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.322 | N/A | N/A | 9621-33 |  | Primary
9630 | Kenton | RED | 33 | 11 | 24 | 12 | 24 | 15.85 | 5.8361 | -3.579 | -0.842 | 8.65 | 13.1 | 24.95 | 32.8 | 76.0671 | 5 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.802 | N/A | N/A | 9621-33 |  | Primary
2805930 | Newcastle Airport | RED | 33 | 11 | 24 | 12 | 24 | 12.0024 | 5.8426 | -3.579 | -2.737 | 9.25 | 25 | 25.74 | 62.5 | 41.184 | 2 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.142 | N/A | N/A | 9621-33 |  | Primary
9636 | Westerhope | RED | 33 | 11 | 18.75 | 15 | 24 | 11.6893 | 2.4094 | -3.579 | 0 | 8.86 | 13.1 | 24.66 | 33.4 | 73.8323 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.664 | N/A | N/A | 9621-33 |  | Primary
9626 | Corporation Street | RED | 33 | 11 | 18.75 | 15 | 24 | 15.2 | 3.2445 | -19.329 | -0.842 | 9.07 | 13.1 | 25.85 | 33.4 | 77.3952 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.0588 | 20.8055 | >1.000 | 22.0588 | RED | No | None | N/A | N/A | -1.189 | N/A | N/A | 9620 |  | Primary
9627 | Educational Precinct | RED | 33 | 11 | 18.75 | 15 | 22.8 | 16.2693 | 4.3519 | -19.329 | 0 | 9.06 | 13.1 | 26.47 | 33.4 | 79.2515 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 25.1499 | 22.6489 | >1.000 | 25.1499 | RED | No | None | N/A | N/A | -0.453 | N/A | N/A | 9620 |  | Primary
9676 | Gateshead Central | RED | 33 | 11 | 18.75 | 15 | 22.1 | 13.9116 | 3.6275 | -19.329 | -1.087 | 10.39 | 13.1 | 30.16 | 33.4 | 90.2994 | 1 | 100% | 18.75 | OUT OF TAPS | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 17.1848 | 17.1848 | >1.000 | 17.1848 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9620 |  | Primary
9633 | Pilgrim | RED | 33 | 11 | 32 | 16 | 32 | 19.1608 | 4.1602 | -19.329 | -0.268 | 11.417 | 13.1 | 34.0945 | 32.8 | 103.9466 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 28.5492 | 4.1602 | >1.000 | 28.5492 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9620 |  | Primary
9634 | University | RED | 33 | 11 | 32 | 16 | 32 | 21.8302 | 6.3932 | -19.329 | -17.132 | 10.19 | 13.1 | 35.79 | 32.8 | 109.1159 | 2 | 100% | 32 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 27.1757 | 27.1757 | >1.000 | 27.1757 | RED | No | None | N/A | N/A | -5.146 | N/A | N/A | 9620 |  | Primary
9672 | Bensham | RED | 66 | 11 | 32 | 16 | 32 | 21.4786 | 2.2863 | -11.705 | 0 | 11.61 | 13.1 | 35.32 | 33.4 | 105.7485 | 2 | 50% | 16 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9671-66 |  | Primary
9625 | Benwell | RED | 66 | 11 | 40 | 20 | 29 | 18.11 | 5.342 | -11.705 | 0 | 9.37 | 25 | 27.94 | 62.5 | 44.704 | 1 | 100% | 40 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9671-66 |  | Primary
9674 | Blaydon Burn | RED | 66 | 11 | 18.75 | 15 | 24 | 11 | 0.11348 | -11.705 | -11.337 | 10.81 | 13.1 | 31.53 | 33.4 | 94.4012 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9671-66 |  | Primary
9913 | Close | RED | 66 | 11 | 32 | 16 | 32 | 25.2368 | 8.4946 | -11.705 | -0.263 | 8.99 | 13.1 | 27.45 | 32.8 | 83.689 | 3 | 100% | 32 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.274 | N/A | N/A | 9671-66 |  | Primary
9671-20 | Dunston 66/20kV | RED | 66 | 20 | 30 | 15 | 28 | 14.9051 | 2.3839 | -11.705 | 0 | 6.63 | 9.2 | 18.59 | 23.5 | 79.1064 | 1 | 100% | 30 | OUT OF TAPS | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9671-66 |  | Primary
9706 | Hexham | RED | 66 | 20 | 37.5 | 30 | 36 | 21.9026 | 7.0597 | -6.592 | -3.643 | 6.33 | 9.2 | 17.11 | 23.5 | 72.8085 | 1 | 100% | 37.5 | OUT OF TAPS | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9670 |  | Primary
9709 | West Wylam | RED | 66 | 20 | 30 | 15 | 30 | 18.9615 | 5.1064 | -6.592 | -2.949 | 5.92 | 12.5 | 23.85 | 31.2 | 76.4423 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.579 | N/A | N/A | 9670 |  | Primary
9716 | Harraton | RED | 132 | 11 | 30 | 15 | 36 | 19.5921 | 10.2 | -45.016 | -0.1 | 10.6788 | 13.1 | 33.0713 | 32.8 | 100.8271 | Not Used | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.344 | N/A | N/A | 301538 |  | BSP
9673-20 | Birtley Grove 66/20kV | RED | 66 | 20 | 30 | 15 | 28 | 9.5897 | 1.267 | -4.2 | -4.2 | 6.48 | 9.2 | 19.07 | 23.5 | 81.1489 | 1 | 100% | 30 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -4.031 | N/A | N/A | 2594836 |  | Primary
9679 | Team Valley | RED | 66 | 20 | 42 | 30 | 41 | 31.3647 | 5.8329 | -4.2 | 0 | 8.6677 | 9.2 | 26.3594 | 23.5 | 112.1677 | 2 | 100% | 42 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.926 | N/A | N/A | 2594836 |  | Primary
9705-20 | Spadeadam 20kV | RED | 11 | 20 | 15 | 7.5 | 12 | 0 | 2.0212 | ENWL | 0 | 2.08 | 2.08 | 5.65 | 5.65 | 100 | 10 | 50% | 0 |  | High Physical Constraint | RED | NOT USED | 0 | 2.0212 | >50 | 0 | NOT USED | No | None | N/A | N/A | N/A | N/A | N/A | ENWL |  | BSP
2868348-20 | Fourstones 20kV | RED | NGET | 20 | 40 | 40 | 48 | 15.68 | -54.25 | Not Used | -92.842 | 10.44 | 16 | 30.55 | 40 | 76.375 | Not Used | 100% | 40 | NO VOLTAGE CONSTRAINT | No Physical Constraint | Red | NOT USED | Not Used | 0 | >50 | 50 | NOT USED | No | None | N/A | N/A | N/A | N/A | N/A | NGET |  | BSP
9817 | Aycliffe Industrial | RED | 33 | 11 | 24 | 12 | 19 | 0.45 | 1.1592 | -35.132 | -0.244 | 8.44 | 13.1 | 23.38 | 32.8 | 71.2805 | 1 | 0% | 0 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.58 | N/A | N/A | 9819 |  | Primary
9820 | Darlington West | RED | 33 | 11 | 18.75 | 15 | 24 | 13.6911 | 5.3732 | -35.132 | -4.343 | 9.12 | 13.1 | 27.82 | 33.4 | 83.2934 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -3.263 | N/A | N/A | 9819 |  | Primary
9823 | Heighington | RED | 33 | 11 | 32 | 16 | 29 | 14.0992 | 2.1455 | -35.132 | -2.499 | 11.33 | 12.5 | 35.26 | 31.25 | 112.832 | 5 | 100% | 32 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9819 |  | Primary
9824 | Newton Aycliffe South | RED | 33 | 11 | 18.75 | 15 | 23 | 14.86 | 0.11452 | -35.132 | -13.473 | 10.19 | 13.1 | 29.74 | 32.8 | 90.6707 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.087 | N/A | N/A | 9819 |  | Primary
9825 | Rise Carr | RED | 33 | 6 | 18.75 | 15 | 23 | 10.3231 | 1.6087 | -35.132 | 0 | 13.56 | 21.9 | 41.48 | 55.8 | 74.3369 | 1 | 100% | 18.75 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9819 |  | Primary
3357866-11 | Norton 132/11kV | RED | 132 | 11 | 40 | 20 | 38.1 | 30.8 | 0.77768 | -198.545 | -15.216 | 11.0144 | 25 | 35.9806 | 62.5 | 57.569 | Not Used | 100% | 40 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 31.0647 | >1.000 | 0 | RED | No | None | N/A | N/A | -9.713 | N/A | N/A | 3357866-132 |  | BSP
9692 | Boldon Downhill | RED | 66 | 20 | 19 | 15 | 25.3 | 10.68 | 2.1325 | -38.505 | -0.224 | 6.73 | 9.2 | 17.96 | 23.5 | 76.4255 | 2 | 100% | 19 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 20.9575 | >1.000 | 22.8 | AMBER | No | None | N/A | N/A | -0.175 | N/A | N/A | 9691 |  | Primary
7377944 | Breamish Street | RED | 66 | 11 | 30 | 15 | 18 | 10.5385 | 2.3556 | -38.505 | -0.2 | 9.64 | 20 | 27.51 | 50 | 55.02 | 2 | 100% | 30 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 22.8 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
9718 | Carley Hill | RED | 66 | 11 | 18.75 | 15 | 24 | 16.9914 | 2.278 | -38.505 | 0 | 10.56 | 13.1 | 29.5 | 32.8 | 89.939 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 20.512 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -0.516 | N/A | N/A | 9691 |  | Primary
9675 | Carr Hill | RED | 66 | 11 | 18.75 | 15 | 22 | 17.8889 | 3.0479 | -38.505 | 0 | 9.16 | 13.1 | 27.39 | 33.4 | 82.006 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 21.7979 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
2889655 | Gateshead East | RED | 66 | 11 | 32 | 16 | 34.13 | 9.32 | 0.38363 | -38.505 | -6.9 | 11.04 | 25 | 27.91 | 62.5 | 44.656 | 4 | 100% | 32 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.8 | 22.8 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -6.316 | N/A | N/A | 9691 |  | Primary
9677 | Harlow Green | RED | 66 | 11 | 24 | 12 | 18 | 16.08 | 4.1451 | -38.505 | -0.474 | 9.07 | 13.1 | 26.02 | 32.8 | 79.3293 | 3 | 50% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 15.6711 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -0.474 | N/A | N/A | 9691 |  | Primary
9694 | Hebburn | RED | 66 | 5.75 | 10 | 10 | 12 | 3.8131 | 0.2348 | -38.505 | -0.16 | 14.8905 | 13.1 | 41.4428 | 33.4 | 124.0802 | 3 | 50% | 5 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.8 | 5.2348 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
9695 | Hebburn West | RED | 66 | 11 | 24 | 12 | 24 | 2.8064 | 0.11368 | -38.505 | 0 | 8.79 | 13.1 | 23.41 | 32.8 | 71.372 | 4 | 0% | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.8 | 0.11368 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
9696 | Hedworth | RED | 66 | 11 | 32 | 16 | 32 | 10.8988 | 1.3693 | -38.505 | -0.126 | 10.78 | 13.1 | 29.62 | 33.4 | 88.6826 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.8 | 0.05029 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -1.319 | N/A | N/A | 9691 |  | Primary
9720 | High Barmston | RED | 66 | 11 | 18.75 | 15 | 24 | 23.3333 | 5.9981 | -38.505 | -0.105 | 9.94 | 13.1 | 28.65 | 33.4 | 85.7784 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 22.8 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -0.424 | N/A | N/A | 9691 |  | Primary
9725-1 | Sunderland T1 T2 | RED | 66 | 11 | 24 | 12 | 24 | 17.79 | 4.1483 | -38.505 | 0 | 10.1 | 25 | 27.21 | 62.5 | 43.536 | 3 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 20.9793 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -7.169 | N/A | N/A | 9691 |  | Primary
9699 | Temple Park | RED | 66 | 11 | 18.75 | 15 | 24 | 15.6883 | 3.7944 | -38.505 | 0 | 9.97 | 13.1 | 27.96 | 33.4 | 83.7126 | 3 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 22.4394 | >1.000 | 22.8 | AMBER | No | None | N/A | N/A | -0.105 | N/A | N/A | 9691 |  | Primary
9727 | Usworth | RED | 66 | 11 | 24 | 12 | 24 | 15.8154 | 3.7645 | -38.505 | -5.999 | 9.11 | 20 | 27.82 | 50 | 55.64 | 3 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 22.8 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -2.267 | N/A | N/A | 9691 |  | Primary
9635 | Walker | RED | 66 | 11 | 20 | 12 | 24 | 15.2131 | 5.4119 | -38.505 | -0.632 | 8.38 | 13.1 | 24.22 | 32.8 | 73.8415 | 3 | 50% | 10 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 15.4119 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
9700 | Wardley | RED | 66 | 5.75 | 15 | 11.25 | 19 | 8.1603 | 1.7354 | -38.505 | -0.106 | 15.52 | 13.1 | 39.2 | 33.4 | 118.4733 | 1 | 100% | 15 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.8 | 16.7354 | >1.000 | 22.8 | AMBER | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
9729 | West Southwick | RED | 66 | 11 | 32 | 16 | 32 | 10.9 | 2.3279 | -38.505 | -0.421 | 9.07 | 25 | 27.01 | 62.5 | 43.216 | 3 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8 | 22.8 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | -0.221 | N/A | N/A | 9691 |  | Primary
9784 | Billingham Marsh House | RED | 66 | 11 | 24 | 12 | 24 | 14.6224 | 0.11509 | -91.817 | -11.4 | 10.21 | 13.1 | 29.97 | 32.8 | 91.372 | 2 | 50% | 12 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 16.2211 | 12.1151 | >1.000 | 16.2211 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9780-66 |  | Primary
9763 | Faraday Street | RED | 66 | 11 | 18.75 | 15 | 22 | 18.867 | 0.11681 | -91.817 | -5.275 | 11.59 | 15.2 | 33.8 | 38 | 88.9474 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 33.9334 | 18.8668 | >1.000 | 33.9334 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9780-66 |  | Primary
9792 | Malleable | RED | 66 | 11 | 32 | 16 | 32 | 17.1621 | 3.6379 | -91.817 | -0.525 | 11.21 | 13.1 | 33.48 | 32.8 | 102.0732 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 56.5859 | 3.4489 | >1.000 | 56.5859 | RED | No | None | N/A | N/A | -0.189 | N/A | N/A | 9780-66 |  | Primary
9780-1 | North Tees T1 T2 | RED | 66 | 11 | 30 | 15 | 34 | 16.53 | 2.7207 | -91.817 | -0.501 | 13.53 | 20 | 40.37 | 50 | 80.74 | 2 | 100% | 30 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.8334 | 22.8334 | >1.000 | 22.8334 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9780-66 |  | Primary
9795 | Tees Industrial T1 T2 | RED | 66 | 11 | 18.75 | 15 | 20 | 13.6575 | 2.3279 | -101.479 | 0 | 10.7186 | 13.1 | 32.1207 | 32.8 | 97.929 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9782 |  | Primary
9778 | Greatham | RED | 132 | 11 | 30 | 15 | 35 | 21.918 | 1.2354 | -278.504 | -12.288 | 12.77 | 20 | 38.86 | 50 | 77.72 | Not Used | 0% | 0 | NOT USED | No Physical Constraint |  | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.516 | N/A | N/A | 9926 |  | BSP
9761 | Carlin How T3 T4 | RED | 66 | 11 | 24 | 12 | 24 | 13.75 | 1.3811 | -109.353 | -2.483 | 9.57 | 20 | 25.65 | 50 | 51.3 | 1 | 0% | 0 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 9759 |  | Primary
9764 | Grangetown | RED | 66 | 11 | 24 | 12 | 24 | 17.4246 | 1.9399 | -109.353 | -14.087 | 10.26 | 25 | 31.49 | 62.5 | 50.384 | 2 | 100% | 24 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9759 |  | Primary
9765 | Guisborough T1 T2 | RED | 66 | 11 | 24 | 12 | 24 | 16.266 | 1.166 | -109.353 | -4.411 | 8.86 | 13.1 | 25.22 | 32.8 | 76.8902 | 1 | 50% | 12 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.243 | N/A | N/A | 9759 |  | Primary
9769 | Prissick | RED | 66 | 11 | 18.75 | 15 | 22.8 | 20.6441 | 4.9677 | -109.353 | -1.127 | 10.72 | 13.1 | 30.76 | 33.4 | 92.0958 | 2 | 100% | 18.75 | SOME VOLTAGE CONSTRAINT | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.332 | N/A | N/A | 9759 |  | Primary
9770 | Redcar | RED | 66 | 11 | 45 | 22.5 | 38.1 | 27.4509 | 4.0244 | -109.353 | -0.5 | 11.68 | 13.1 | 33.15 | 32.8 | 101.0671 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.705 | N/A | N/A | 9759 |  | Primary
9773 | Spencerbeck | RED | 66 | 11 | 40 | 20 | 38.11 | 20.7112 | 10.1647 | -109.353 | -5.587 | 14.11 | 18.4 | 40.97 | 46.8 | 87.5427 | 1 | 100% | 40 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9759 |  | Primary
9839 | Poppleton | RED | NGET | 33 | 120 | 120 | 120 | 37.5533 | 12.41 | NGET | -9.251 | 11.22 | 17.5 | 32.53 | 44.6 | 72.9372 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | >52.632 | NOT USED | No | None | N/A | N/A | -291.789 | N/A | N/A | NGET | 9842,2537397,9848,9850 | BSP
9690 | South Shields | RED | NGET | 33 | 100 | 100 | 130 | 47.91 | -8.79 | NGET | -37.208 | 16.02 | 17.5 | 46.51 | 44.6 | 104.2825 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 89.642 | >15.789 | >52.632 | NOT USED | No | None | N/A | N/A | -1.568 | N/A | N/A | NGET | 9693,9697,9698,9701 | BSP
9717-33 | Offerton | RED | NGET | 33 | 100 | 100 | 114 | 37.8048 | 17.75 | NGET | -1.852 | 17.97 | 17.5 | 51.16 | 44.6 | 114.7085 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 76.615 | >50.632 | >52.632 | NOT USED | No | None | N/A | N/A | -41.135 | N/A | N/A | NGET | 9721,9717-11,9724 | BSP
2810936 | Knaresborough | RED | NGET | 132 | 240 | 240 | 240 | 151.12 | 24.63 | NGET | -89.389 | 7.77 | 31.5 | 21.52 | 80 | 26.9 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.000 | RED | No | None | N/A | N/A | -681.9 | N/A | N/A | NGET | 9893-33,9891-33,9891-11,9897-33,9897-11 | GSP
3357866-132 | Norton | RED | NGET | 132 | 240 | 240 | 864 | 364.93 | 84.89 | NGET | -198.545 | 17.8841 | 31.5 | 47.2672 | 78.7 | 60.06 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.000 | RED | No | None | N/A | N/A | -1468.222 | N/A | N/A | NGET | 9928-33,9875,9785-33,9819,9780-66,3357866-11,9927-6 | GSP
9926 | Saltholme | RED | NGET | 132 | 240 | 240 | 288 | 78.41 | -127.02 | NGET | -278.504 | 14.04 | 20 | 38.66 | 50 | 77.32 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -316.884 | N/A | N/A | NGET | 9782,9778 | GSP
9912 | Stella North | RED | NGET | 132 | 120 | 120 | 720 | 186.36 | 44.8545 | NGET | -34.613 | 18.19 | 25 | 52.72 | 62.5 | 84.352 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -794.675 | N/A | N/A | NGET | 9621-33,9620,9671-66,2841083 | GSP
301538 | Stella South | RED | NGET | 132 | 240 | 240 | 720 | 251.61 | 3.93 | NGET | -45.016 | 18.25 | 20 | 52.96 | 50 | 105.92 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.19 | RED | No | None | N/A | N/A | -1175.631 | N/A | N/A | NGET | 9716,2594836,9739-66,9670 | GSP
9811-132 | Spennymoor GSP | RED | NGET | 132 | 240 | 240 | 576 | 197.63 | -2.9 | NGET | -113.688 | 10.42 | 15.3 | 31.24 | 39 | 80.1026 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -1159.876 | N/A | N/A | NGET | 9810-66,9812-66,9811-66 | GSP
9929 | Osbaldwick | RED | NGET | 132 | 240 | 240 | 576 | 261.37 | 58.69 | NGET | -79.618 | 10.72 | 15.3 | 31.65 | 46.9 | 70.0654 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -710.596 | N/A | N/A | NGET | 9838-33,9858,9835 | GSP
9915-132 | Blyth 132kV | RED | NGET | 132 | 240 | 240 | 288 | 23.32 | -442.2 | NGET | -513.142 | 12.6 | 15.3 | 36.86 | 39 | 94.5128 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >10.526 | RED | Yes | None | N/A | N/A | -0.242 | N/A | N/A | NGET | 9645-66 | GSP
7494777 | Tynemouth | RED | NGET | 132 | 240 | 240 | 576 | 152.22 | 46.41 | NGET | -43.65 | 14.64 | 40 | 39.41 | 100 | 39.41 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.000 | RED | No | None | N/A | N/A | -379.481 | N/A | N/A | NGET | 9605,9910,9623-33 | GSP
9785-33 | Bowesfield | RED | 132 | 33 | 90 | 45 | 108 | 88.0182 | 9 | -198.545 | -18.878 | 12.35 | 17.5 | 37.46 | 44.6 | 83.991 | Not Used | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 37.959 | >1.000 | 0 | RED | No | None | N/A | N/A | -61.041 | N/A | N/A | 3357866-132 | 9785-33-11,9768,9771,9774,9796,9760 | BSP
9819 | Darlington North | RED | 132 | 33 | 90 | 45 | 109 | 62.7481 | 9.5803 | -198.545 | -35.132 | 12.5 | 17.5 | 37.8 | 44.6 | 84.7534 | Not Used | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -111.088 | N/A | N/A | 3357866-132 | 9817,9820,9823,9824,9882-2,9825 | BSP
9875 | Leeming Bar | RED | 132 | 33 | 90 | 45 | 141 | 115.7791 | 4.5 | -198.545 | -29.03 | 14.39 | 17.5 | 35.84 | 44.6 | 82.2286 | Not Used | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -246.641 | N/A | N/A | 3357866-132 | 7490443,9877,9878,9881,2826869,9882-1,9883,9884 | BSP
9605 | Chirton Grange | RED | 132 | 33 | 60 | 30 | 72 | 48 | 7.14 | -43.65 | -4.382 | 10.59 | 17.5 | 30.52 | 44.6 | 68.4305 | Not Used | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 48.783 | >1.000 | 0 | RED | No | None | N/A | N/A | -18.357 | N/A | N/A | 7494777 | 9608,9615,9616 | BSP
9621-33 | Blucher | RED | 132 | 33 | 90 | 45 | 114 | 87.213 | 11.18 | -34.613 | -3.579 | 9.18 | 13.1 | 26.25 | 32.8 | 80.0305 | Not Used | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -121.193 | N/A | N/A | 9912 | 9630,2805930,9636,9621-11 | BSP
9897-33 | Wormald Green 132/33kV | RED | 132 | 33 | 60 | 30 | 72 | 48.1386 | 6.25 | -89.389 | -31.459 | 9.9 | 17.5 | 26.49 | 44.6 | 59.3946 | Not Used | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 2.756 | >1.000 | 0 | RED | No | None | N/A | N/A | -63.494 | N/A | N/A | 2810936 | 9898,2822141,9899,7129903,9902 | BSP
9838-33 | Melrosegate 132/33kV | RED | 132 | 33 | 90 | 45 | 180 | 119.2118 | 12.1777 | -79.618 | -14.149 | 15.8 | 25 | 50.23 | 62.5 | 80.368 | Not Used | 0% | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 1.3557 | >1.000 | 0 | RED | No | None | N/A | N/A | -10.822 | N/A | N/A | 9929 | 9832,9841,2524256,9843,9844,9838-11,9847,9851 | BSP
9620 | Barrack Road | RED | 132 | 33 | 120 | 60 | 114 | 75.0959 | 15.37 | -34.613 | -19.329 | 13.27 | 17.5 | 39.04 | 44.6 | 87.5336 | Not Used | 100% | 120 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 128.582 | >1.000 | 0 | RED | No | None | N/A | N/A | -6.788 | N/A | N/A | 9912 | 9626,9627,9676,9633,9634 | BSP
9928-33 | Darlington Central | RED | 132 | 33 | 60 | 30 | 72 | 43.8 | 4.9 | -198.545 | -8.472 | 11.3 | 17.5 | 30.9 | 44.6 | 69.2825 | Not Used | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 14.637 | >1.000 | 0 | RED | No | None | N/A | N/A | -50.263 | N/A | N/A | 3357866-132 | 9879,9927-11,9928-11,9818 | BSP
9858 | Scarborough Grid | RED | 132 | 33 | 120 | 60 | 100 | 76.27 | 9.87 | -79.618 | -5.781 | 13.18 | 17.5 | 35.01 | 44.6 | 78.4978 | Not Used | 100% | 120 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 37.885 | >1.000 | 0 | RED | No | None | N/A | N/A | -91.985 | N/A | N/A | 9929 | 9861,9862,9863,3363742,9864,9866-1,9867-1 | BSP
9910 | Flatworth | RED | 132 | 33 | 60 | 30 | 72 | 41.9039 | 4.73 | -43.65 | -30.737 | 12.3 | 17.5 | 34.87 | 44.6 | 78.1839 | Not Used | 100% | 60 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 24.204 | >1.000 | >0.000 | NOT USED | No | None | N/A | N/A | -40.526 | N/A | N/A | 7494777 | 9612,9613,9617 | BSP
9623-33 | Gosforth | RED | 132 | 33 | 90 | 45 | 108 | 93.0948 | 11.2 | -43.65 | -8.531 | 10.44 | 17.5 | 31.25 | 44.6 | 70.0673 | Not Used | 100% | 90 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 100.18 | >1.000 | >0.000 | NOT USED | No | None | N/A | N/A | -1.02 | N/A | N/A | 7494777 | 9629,9623-11,9614,9631 | BSP
9893-33 | Husthwaite | RED | 132 | 33 | 45 | 22.5 | 54 | 27.3359 | 0.81 | -89.389 | -39.177 | 7.86 | 25 | 20.12 | 62.5 | 32.192 | Not Used | 100% | 45 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -105.173 | N/A | N/A | 2810936 | 9893-11,2530198,2541519 | BSP
9891-33 | Harrogate 132/33kV | RED | 132 | 33 | 60 | 30 | 120 | 68.7938 | 6.6 | -89.389 | -17.944 | 10.25 | 31.5 | 30.48 | 77.75 | 39.2026 | Not Used | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 65.472 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.128 | N/A | N/A | 2810936 | 9901,9903 | BSP
9739-66 | Annfield | RED | 132 | 66 | 75 | 37.5 | 90.8 | 57.78 | 3.28 | -45.016 | -34.124 | 6.59 | 13.1 | 18.22 | 33.4 | 54.5509 | Not Used | 100% | 75 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -257.805 | N/A | N/A | 301538 | 9739-20,2707936,9749 | BSP
2594836 | Ravensworth | RED | 132 | 66 | 75 | 37.5 | 90 | 85.1506 | 8.174 | -45.016 | -4.2 | 7.42 | 25 | 20.81 | 62.5 | 33.296 | Not Used | 100% | 75 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -9.06 | N/A | N/A | 301538 | 9673-20,9679 | BSP
9670 | Coalburns | RED | 132 | 66 | 75 | 37.5 | 91.3 | 63.3058 | 7.6 | -45.016 | -6.592 | 7.07 | 31.5 | 21.34 | 77.75 | 27.4469 | Not Used | 100% | 75 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -132.684 | N/A | N/A | 301538 | 9706,9709 | BSP
9810-66 | Potter House 132/66kV | RED | 132 | 66 | 120 | 60 | 86.25 | 75.8377 | 12.8 | -113.688 | -14.631 | 5.72 | 31.5 | 16.53 | 78.8 | 20.9772 | Not Used | 100% | 120 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -150 | N/A | N/A | 9811-132 | 9803,9805,9743,9810-20 | BSP
9812-66 | Toronto | RED | 132 | 66 | 90 | 45 | 108 | 92.0589 | 3.25 | -113.688 | -29.097 | 6.21 | 31.5 | 18.48 | 77.75 | 23.7685 | Not Used | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 2.111 | >1.000 | 0 | RED | No | None | N/A | N/A | -91.139 | N/A | N/A | 9811-132 | 9806,9821,9822,9812-20 | BSP
9811-66 | Spennymoor 132/66kV | RED | 132 | 66 | 75 | 37.5 | 188 | 80.555 | 9.14 | -113.688 | -69.96 | 10.13 | 21.9 | 30.6 | 55.8 | 54.8387 | Not Used | 0% | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -47.79 | N/A | N/A | 9811-132 | 9804,9807,9808,9809,9826,9811-20 | BSP
9835 | Malton Grid | RED | 132 | 66 | 75 | 37.5 | 82 | 69.5072 | 6.14 | -79.618 | -7.162 | 5.74 | 25 | 16.2 | 62.5 | 25.92 | Not Used | 0% | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -68.316 | N/A | N/A | 9929 | 9845,9846,9849,9865,2522850,9866-2,9867-2 | BSP
9645-66 | Linton | RED | 132 | 66 | 60 | 30 | 72 | 56.3848 | -51.23 | -513.142 | -81.642 | 5.78 | 31.5 | 16.79 | 77.75 | 21.5949 | Not Used | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 8.528 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.242 | N/A | N/A | 9915-132 | 9662,9645-20,9648,9663 | BSP
9671-66 | Dunston | RED | 132 | 66 | 150 | 75 | 195 | 88.9764 | 13.2 | -34.613 | -11.705 | 13.26 | 21.9 | 37.71 | 55.8 | 67.5806 | Not Used | 0% | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -31.853 | N/A | N/A | 9912 | 9672,9625,9674,9913,9671-20 | BSP
9782 | Seal Sands | RED | 132 | 66 | 90 | 45 | 112 | 35.39 | -135.75 | -278.504 | -101.479 | 9.0745 | 21.9 | 39.6673 | 55.8 | 71.0884 | Not Used | 100% | 90 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | >52.632 | NOT USED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9926 | 9795 | BSP
9780-66 | North Tees | RED | 132 | 66 | 150 | 75 | 150.6 | 105.18 | 6.5069 | -198.545 | -91.817 | 14.99 | 31.5 | 44.97 | 77.75 | 57.8392 | Not Used | 100% | 150 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 108.4209 | >1.000 | 0 | RED | No | None | N/A | N/A | -48.086 | N/A | N/A | 3357866-132 | 9784,9763,9792,9780-1,9785 | BSP
9787-66 | Hartmoor | RED | NGET | 66 | 120 | 120 | 120 | 88.54 | -19.67 | NGET | -103.774 | 10.92 | 21.9 | 32.23 | 55.8 | 57.7599 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | >52.632 | NOT USED | No | None | N/A | N/A | -682.01 | N/A | N/A | NGET | 9783,9786,9787-20,2569052,2541255 | BSP
9915-66 | Blyth 66kV | RED | NGET | 66 | 120 | 120 | 309 | 127.2095 | -48.49 | NGET | -139.267 | 13.05 | 21.9 | 38.83 | 55.8 | 69.5878 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | >10.526 | NOT USED | Yes | None | N/A | N/A | -515.767 | N/A | N/A | NGET | 9646,9607,9610,9628-1,9611,9649,9650,9653,7189886,9655,2771500 | BSP
9691 | West Boldon | RED | NGET | 66 | 120 | 120 | 388 | 212.7558 | 65.84 | NGET | -38.505 | 17.04 | 21.9 | 51.95 | 55.8 | 93.1004 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NOT USED | NOT USED | 27.486 | >1.000 | >52.632 | NOT USED | No | None | N/A | N/A | -158.354 | N/A | N/A | NGET | 9692,7377944,9718,9675,2889655,9677,9694,9695,9696,9720,9725,9699,9727,9635,9700,9729 | BSP
9759 | Lackenby | RED | NGET | 66 | 120 | 120 | 306 | 151.1513 | 20.43 | NGET | -109.353 | 17.22 | 21.9 | 48.67 | 55.8 | 87.2222 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | >15.789 | NOT USED | No | None | N/A | N/A | -410.374 | N/A | N/A | NGET | 9761,9764,9765,9769,9770,9773 | BSP
9918 | Hawthorn Pit Grid | RED | NGET | 66 | 180 | 180 | 234 | 90.4 | 11.88 | NGET | -72.3 | 12.28 | 21.9 | 35.88 | 55.8 | 64.3011 | Not Used | 100% | 180 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | >52.632 | NOT USED | No | None | N/A | N/A | -768.43 | N/A | N/A | NGET | 9741,9745,9746,9747,9748,9726 | BSP
9610-2 | Cramlington T2 T4 | RED | 66 | 11 | 19 | 12 | 24 | 13.7927 | 3.1202 | -139.267 | -0.126 | 9.76 | 13.1 | 28.57 | 32.8 | 87.1037 | 3 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 9915-66 |  | Primary
9671-11 | Dunston 66/11kV | RED | 66 | 11 | 24 | 12 | 24 | 15.4575 | 1.8723 | -11.705 | -0.105 | 9.68 | 13.1 | 28.59 | 32.8 | 87.1646 | 2 | 0% | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9671-66 |  | Primary
9673-11 | Birtley Grove 66/11kV | RED | 66 | 11 | 32 | 16 | 30 | 14.1706 | 3.0691 | -4.2 | 0 | 8.52 | 25 | 16.41 | 62.5 | 34.08 | 3 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -4.103 | N/A | N/A | 2594836 |  | Primary
9780-2 | North Tees T3 T4 | RED | 66 | 11 | 30 | 15 | 36 | 18.59 | 0.76141 | -91.817 | -9.116 | 17.81 | 20 | 51.9 | 50 | 103.8 | 2 | 100% | 30 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.1647 | 20.1647 | >1.000 | 20.1647 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9780-66 |  | Primary
9785-66-11 | Bowesfield 66/11kV | RED | 66 | 11 | 32 | 16 | 32 | 14.2103 | 8.6831 | -91.817 | 0 | 10.89 | 20 | 30.16 | 50 | 60.32 | 2 | 100% | 32 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 50.1916 | 40.1551 | >1.000 | 50.1916 | RED | No | None | N/A | N/A | -0.528 | N/A | N/A | 9780-66 |  | Primary
9927-6 | Darlington 132/6kV | RED | 132 | 6 | 30 | 15 | 12 | 3.5355 | 0.62038 | -198.545 | 0 | 18.2761 | 13.1 | 50.9732 | 32.8 | 155.4061 | Not Used | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 30.6204 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 3357866-132 |  | BSP
9866-2 | Whitby T2 | RED | 33 | 11 | 24 | 12 | 19.1 | 5.75 | 0.083138 | -7.162 | 0 | 7.68 | 20 | 19.13 | 50 | 38.4 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -4.211 | N/A | N/A | 9835 |  | Primary
9867-2 | Whitby West T2 | RED | 33 | 11 | 24 | 12 | 24 | 5.77 | 0.22614 | -7.162 | 0 | 7.21 | 13.1 | 18.27 | 32.8 | 55.7012 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9835 |  | Primary
9882-1 | Richmond T1 | RED | 33 | 11 | 24 | 12 | 24 | 10.5627 | 0.083138 | -29.03 | 0 | 8.07 | 13.1 | 20.98 | 33.4 | 62.8144 | 1 | 50% | 6 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9875 |  | Primary
7753909 | Harrogate West | RED | 33 | 11 | 30 | 15 | 30 | 12.97 | 3.065 | -17.944 | 0 | 9.04 | 25 | 27.41 | 62.5 | 43.856 | 10 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 36.3325 | 33.065 | >1.000 | 36.3325 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9891-33 |  | Primary
9810-11 | Potter House T4 T5 | RED | 66 | 11 | 30 | 15 | 30 | 6.3161 | 0.96648 | -14.631 | 0 | 8.99 | 25 | 56.88 | 62.5 | 91.008 | 5 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9810-66 |  | Primary
9725-5 | Sunderland T5 T6 | RED | 66 | 11 | 30 | 15 | 30 | 0 | 0 | -38.505 | 0 | 10.31 | 25 | 30.61 | 62.5 | 48.976 | 10 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.8 | 22.8 | >1.000 | 22.8 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 9691 |  | Primary
7344629 | Skeeby | RED | 132 | 33 | 90 | 57 | 90 | 115.7791 | 4.5 | -198.545 | 0 | 11.68 | 25 | 26.1 | 62.5 | 46.72 | Not Used | 100% | 57 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -123.506 | N/A | N/A | 3357866-132 | 9882-1 | BSP
7775573 | Aycliffe Forrest | RED | 33 | 11 | 30 | 15 | 30 | 0 | 0 | -35.132 | 0 | 1 | 1 | 1 | 1 | TBC | 5 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 9819 |  | Primary
3337559 | Kielder | RED | 33 | 20 | 4 | 4 | 4 | 0 | 0.2 | ENWL | 0 | 1 | 1 | 1 | 1 | 100 | 1 | 100% | 4 | OUT OF TAPS | Some Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 4.2 | >50 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | ENWL |  | Primary

## Yorkshire Generation
Substation ID | Substation Name | Summary | Nominal Voltage |  | Transformer Capacity |  | Firm Capacity | Demand |  | Existing Generation |  | Fault Level |  |  |  | Known Constraints (Downstream) | [6 empty] | Known Constraints (Upstream) | [5 empty] | Is this an Active Network Management (ANM) area? | Additional Information | [7 empty] | Substation Class
[12 empty] | Break |  | Make
|  |  | Upstream | Downstream | [5 empty] | Upstream | Downstream
|  | Overall Primary Classification | (kV) | (kV) | OFAF (MVA) | ONAN (MVA) | Load (MVA) | Max (MVA) | Min (MVA) | (MVA) | (MVA) | Duty (kA) | Rating (kA) | Duty (kA) | Rating (kA) | Fault Level (%) | Worst Case Tap Position | Reverse Power Flow |  | Downstream Voltage Constraints | Local Physical Constraints | Downstream Substation Classification | Upstream Voltage Constraints | Generation Headroom without reinforcement for New EHV Feeder (MVA) | Generation Headroom without reinforcement for New Substation (MVA) | NGESO Statement of Works Threshold (MVA) | Upstream Constraint Levels (NPg/NGET) (MVA) | Upstream Substation Classification |  | Quoted Generation Connections (MVA) | Valid Until: | Number of Valid Quotes | Contracted Generation Connections (MVA) | Connection Date | Number of Accepted Quotes | Related Substations (Upstream) | Related Substations (Downstream) | GSP, BSP or Primary
[18 empty] | % | MVA
4038567 | Darnall | RED | 33 | 11 | 24 | 12 | 23 | 15.6712 | 3.8471 | -21.469 | -0.474 | 10.3891 | 19.9973 | 28.2943 | 49.9933 | 56.5962 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -5.342 | N/A | N/A | 4038847 |  | Primary
4038610 | Orgreave | RED | 33 | 11 | 23 | 15 | 23 | 9.3642 | 2.366 | -21.469 | -0.251 | 7.9162 | 13.1216 | 20.8592 | 32.804 | 63.5873 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038847 |  | Primary
4038573 | Revill Lane | RED | 33 | 11 | 23 | 15 | 23 | 7.2159 | 1.5564 | -21.469 | -0.428 | 7.7952 | 13.1216 | 20.306 | 32.804 | 61.9011 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038847 |  | Primary
4038565 | Shirland Lane | RED | 33 | 11 | 24 | 12 | 24 | 9.5818 | 1.696 | -21.469 | 0 | 10.0768 | 13.1216 | 26.8059 | 32.804 | 81.7153 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038847 |  | Primary
4038562 | Stoke Street | RED | 33 | 11 | 24 | 12 | 24 | 13.0091 | 1.0064 | -21.469 | 0 | 10.5039 | 13.1216 | 28.1558 | 32.804 | 85.8305 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038847 |  | Primary
4038575 | Barnsley | RED | 66 | 11 | 18.75 | 15 | 21.5 | 14.2451 | 3.8597 | -12.053 | 0 | 9.3295 | 13.1216 | 24.9986 | 32.804 | 76.206 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038849 |  | Primary
4038788 | Barugh 66/11kV | RED | 66 | 11 | 30 | 15 | 30 | 18.9 | 3.34 | -12.053 | -10.638 | 9.7312 | 19.9973 | 27.5104 | 49.9933 | 55.0282 | 5 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.158 | N/A | N/A | 4038849 |  | Primary
4038792-1 | Elmhirst Lane 1 | RED | 66 | 11 | 24 | 12 | 24 | 12.5839 | 0.65119 | -12.053 | 0 | 11.115 | 13.1216 | 28.981 | 32.804 | 88.3459 | 9 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038849 |  | Primary
4038531 | Scissett | RED | 66 | 11 | 18.75 | 15 | 23 | 16.5567 | 3.9364 | -12.053 | -0.362 | 9.19 | 13.12 | 24.8 | 32.8 | 75.6098 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.084 | N/A | N/A | 4038849 |  | Primary
4038576 | Smithy Green | RED | 66 | 11 | 7.5 | 7.5 | 7.5 | 7.0272 | 1.2448 | -12.053 | 0 | 4.8968 | 13.1216 | 12.233 | 32.804 | 37.3184 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038849 |  | Primary
4038574 | Woolley | RED | 66 | 11 | 18.75 | 15 | 23 | 9.1964 | 1.2907 | -12.053 | -1.053 | 9.173 | 13.1216 | 24.2347 | 32.804 | 73.8773 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -7.053 | N/A | N/A | 4038849 |  | Primary
4038661-1 | Beeston Royds 33/11kV | RED | 33 | 11 | 18.75 | 15 | 23 | 5.9285 | 1.0365 | -8.568 | -0.12 | 11.4554 | 13.1216 | 29.9181 | 32.804 | 91.2026 | 4 | 50% | 9.375 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 38.9968 | 10.4115 | >1.000 | 38.9968 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096967 |  | Primary
4038654 | Gildersome | RED | 33 | 11 | 23 | 11.5 | 23 | 15.9776 | 1.2899 | -8.568 | 0 | 7.7311 | 13.1216 | 21.3823 | 32.804 | 65.182 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 25.2599 | 0 | >1.000 | 25.2599 | GREEN | No | None | N/A | N/A | -6.39 | N/A | N/A | 7096967 |  | Primary
4038665 | Hedley Chase | RED | 33 | 11 | 23 | 11.5 | 23 | 7.18 | 1.4168 | -8.568 | 0 | 8.5455 | 13.1216 | 22.9568 | 32.804 | 69.9819 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 19.0577 | 12.9168 | >1.000 | 19.0577 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096967 |  | Primary
4038668 | Middleton Town Street | RED | 33 | 11 | 18.75 | 15 | 23 | 22.4528 | 1.283 | -8.568 | -1.922 | 10.4758 | 13.1216 | 27.6465 | 32.804 | 84.2779 | 4 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.9338 | 17.77 | >1.000 | 23.9338 | GREEN | No | None | N/A | N/A | -2.263 | N/A | N/A | 7096967 |  | Primary
4038658 | Morley | RED | 33 | 11 | 18.75 | 15 | 23 | 12.4838 | 3.81 | -8.568 | -1.558 | 10.2621 | 13.1216 | 26.0161 | 32.804 | 79.3076 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.4477 | 22.385 | >1.000 | 22.4477 | GREEN | No | None | N/A | N/A | -0.175 | N/A | N/A | 7096967 |  | Primary
4038664 | Tingley | RED | 33 | 11 | 24 | 12 | 24 | 14.1837 | 3.8736 | -8.568 | -2.632 | 9.3851 | 13.1216 | 24.2105 | 32.804 | 73.8034 | 9 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 22.3138 | 3.8736 | >1.000 | 22.3138 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096967 |  | Primary
4038629 | Whitehall Road 4/5 | RED | 33 | 11 | 18.75 | 15 | 19 | 7.7271 | 1.6541 | -8.568 | -0.105 | 11.055 | 13.1216 | 28.0739 | 32.804 | 85.5807 | 4 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 18.7289 | 18.7289 | >1.000 | 18.7289 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096967 |  | Primary
4038707 | Endike Lane | RED | 33 | 11 | 23 | 15 | 23 | 11.614 | 0.71038 | -72.742 | -6.831 | 10.3798 | 13.1216 | 26.0329 | 32.804 | 79.359 | 5 | 100% | 23 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.549 | N/A | N/A | 4038873 |  | Primary
4038711 | First Avenue | RED | 33 | 11 | 24 | 12 | 24 | 18.4168 | 3.057 | -72.742 | -2.2 | 10.2212 | 13.1216 | 26.5678 | 32.804 | 80.9894 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.221 | N/A | N/A | 4038873 |  | Primary
4038821 | Holme Upon Spalding Moor | RED | 33 | 11 | 24 | 12 | 8 | 6.56 | 0.63145 | -72.742 | -3.239 | 3.4963 | 19.9973 | 7.7088 | 49.9933 | 17.4838 | 1 | TBC | 0 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.948 | N/A | N/A | 4038873 |  | Primary
4038701 | Norwood | RED | 33 | 11 | 23 | 11.5 | 23 | 13.7458 | 1.5913 | -72.742 | -3.004 | 8.4586 | 13.1216 | 23.1499 | 32.804 | 70.5702 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.626 | N/A | N/A | 4038873 |  | Primary
4038767 | Southgate | RED | 33 | 11 | 23 | 11.5 | 8 | 5.466 | 0.47359 | -72.742 | -3.407 | 4.8496 | 13.1216 | 12.0555 | 32.804 | 36.9587 | 1 | TBC | 0 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038873 |  | Primary
4038702 | Southwood Road | RED | 33 | 11 | 23 | 11.5 | 23 | 15.4743 | 4.2505 | -72.742 | -1.978 | 8.8436 | 13.1216 | 23.3287 | 32.804 | 71.1155 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | SOME VOLTAGE CONSTRAINT | 0 | 3.7455 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.505 | N/A | N/A | 4038873 |  | Primary
4038703 | Spark Mill Lane | RED | 33 | 11 | 23 | 11.5 | 23 | 15.2939 | 2.3102 | -72.742 | -4.042 | 9.6287 | 13.1216 | 26.5175 | 32.804 | 80.8363 | 6 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 0 | 12.1562 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.654 | N/A | N/A | 4038873 |  | Primary
4038502 | Airedale Road | RED | 33 | 11 | 18.75 | 15 | 23 | 10.2585 | 1.97 | -2.024 | -0.495 | 8.0487 | 25 | 19.0916 | 62.5 | 32.195 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 14.2476 | 14.2476 | >1.000 | 14.2476 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038841 |  | Primary
4038796 | Bingley 33/11kV | RED | 33 | 11 | 24 | 12 | 23.8 | 14.8384 | 3.8037 | -2.024 | -0.5 | 11.0724 | 16.0083 | 29.4337 | 40.0209 | 73.5458 | 5 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 14.2476 | 14.2476 | >1.000 | 14.2476 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038841 |  | Primary
4038503 | Harden | RED | 33 | 11 | 23 | 11.5 | 8 | 4.2563 | 0.72025 | -2.024 | -0.2 | 4.6404 | 13.1216 | 12.4219 | 32.804 | 37.867 | 5 | 50% | 5.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 14.2476 | 6.4703 | >1.000 | 14.2476 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038841 |  | Primary
4038497-1 | Haworth 1 | RED | 33 | 11 | 30 | 15 | 30 | 9.0761 | 0.43412 | -2.024 | -0.489 | 7.5515 | 19.9973 | 18.689 | 49.9933 | 37.7627 | 6 | 100% | 15 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 14.2476 | 14.2476 | >1.000 | 14.2476 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038841 |  | Primary
4038505 | Nabwood | RED | 33 | 11 | 23 | 11.5 | 23 | 12.4103 | 2.7231 | -2.024 | -0.137 | 7.9385 | 13.1216 | 21.5076 | 32.804 | 65.5639 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 14.2476 | 14.2231 | >1.000 | 14.2476 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038841 |  | Primary
4038499 | South Street | RED | 33 | 11 | 23 | 11.5 | 23 | 9.9323 | 2.2195 | -2.024 | -0.203 | 7.3898 | 13.1216 | 19.1085 | 32.804 | 58.2506 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 8.2679 | 8.2679 | >1.000 | 8.2679 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038841 |  | Primary
4038570 | Blackburn Meadows 33/11kV | RED | 132 | 33 | 24 | 12 | 24 | 14.28 | 3.1966 | -267.182 | -3.474 | 11.5704 | 13.1216 | 31.6807 | 32.804 | 96.5757 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -1.158 | N/A | N/A | 7096988-1 |  | Primary
4038607 | BOC Brinsworth | RED | 33 | 11 | 18.75 | 15 | 23 | 5.137 | 1.0756 | -49.692 | 0 | 11.4182 | 13.1216 | 28.5964 | 32.804 | 87.1734 | 4 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038848 |  | Primary
4038609 | Templeborough 33/11kV | RED | 33 | 11 | 18.75 | 15 | 23 | 12.3166 | 2.4428 | -49.692 | -0.737 | 11.634 | 13.1216 | 30.5272 | 32.804 | 93.0594 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | VOLTAGE OUT OF STATUTORY LIMIT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038848 |  | Primary
4038569 | Tinsley Wire Industries | RED | 33 | 11 | 24 | 12 | 24 | 5.2095 | 1.324 | -49.692 | -1.271 | 10.4248 | 13.1216 | 27.4676 | 32.804 | 83.7324 | 9 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.6 | N/A | N/A | 4038848 |  | Primary
4038776 | Corringham Road | RED | 33 | 11 | 23 | 11.5 | 23 | 14.0379 | 1.369 | -27.981 | -4.27 | 8.9718 | 13.1216 | 23.9638 | 32.804 | 73.0515 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038891 |  | Primary
4038601 | Epworth | RED | 33 | 11 | 24 | 12 | 10 | 7.6556 | 1.1245 | -27.981 | -1.291 | 3.6111 | 18.3702 | 8.7103 | 45.9256 | 19.6575 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038891 |  | Primary
4038778 | Harpswell | RED | 33 | 11 | 24 | 12 | 8 | 7.82 | -3.3349 | -27.981 | -6.948 | 5.4843 | 13.1216 | 13.4166 | 32.804 | 41.7961 | 8 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038891 |  | Primary
4038605 | Haxey | RED | 33 | 11 | 12 | 12 | 8 | 5.34 | 0.77945 | -27.981 | -0.5 | 4.0991 | 16.0083 | 9.7857 | 40.0209 | 25.6058 | 6 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.191 | N/A | N/A | 4038891 |  | Primary
4038775 | Lea Road | RED | 33 | 11 | 23 | 11.5 | 15.8 | 10.46 | 2.3284 | -27.981 | -1.527 | 7.636 | 13.1216 | 20.9738 | 32.804 | 63.9368 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038891 |  | Primary
4038783 | Normanby | RED | 33 | 11 | 12 | 12 | 8 | 5.89 | 0.85838 | -27.981 | -0.561 | 2.825 | 13.1216 | 6.3772 | 32.804 | 21.5295 | 7 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.095 | N/A | N/A | 4038891 |  | Primary
4038777 | Stow | RED | 33 | 11 | 24 | 12 | 6.5 | 5.3467 | -9.087 | -27.981 | -12.884 | 5.2214 | 13.1216 | 12.6155 | 32.804 | 39.7926 | 10 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038891 |  | Primary
4038470 | Balme Street | RED | 33 | 11 | 24 | 12 | 24 | 14.7759 | 3.5386 | -1.601 | 0 | 10.7455 | 13.1216 | 28.852 | 32.804 | 87.9528 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 18.9252 | 3.5386 | >1.000 | 18.9252 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038463 | Gaisby Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 14.2414 | 3.748 | -1.601 | 0 | 11.3379 | 13.1216 | 29.3939 | 32.804 | 89.6045 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 25.2699 | 3.748 | >1.000 | 25.2699 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038471 | Idle | RED | 33 | 11 | 18.75 | 15 | 23 | 14.7209 | 3.3851 | -1.601 | 0 | 11.5163 | 13.1216 | 29.3493 | 32.804 | 89.4685 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 28.5452 | 3.3851 | >1.000 | 28.5452 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038477 | Killinghall Road | RED | 33 | 11 | 24 | 12 | 7.5 | 0.66121 | 0.0098664 | -1.601 | 0 | 5.661 | 13.1216 | 14.1423 | 32.804 | 43.143 | 9 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 23.2424 | 0.0098664 | >1.000 | 23.2424 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038468 | Manchester Road | RED | 33 | 11 | 23 | 11.5 | 23 | 8.8896 | 3.1827 | -1.601 | 0 | 10.5547 | 13.1216 | 27.909 | 32.804 | 85.078 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 18.1505 | 3.1827 | >1.000 | 18.1505 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038473 | Moorside Road | RED | 33 | 11 | 18.75 | 15 | 23 | 12.3725 | 2.0659 | -1.601 | 0 | 11.3552 | 13.1216 | 29.2358 | 32.804 | 89.1227 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.2754 | 20.8159 | >1.000 | 24.2754 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038472 | Mount Street | RED | 33 | 11 | 18.75 | 15 | 23 | 22.7105 | 2.715 | -1.601 | -1.601 | 11.4079 | 13.1216 | 28.7531 | 32.804 | 87.6511 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.2375 | 21.265 | >1.000 | 23.2375 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038834 |  | Primary
4038462 | Shipley | RED | 33 | 11 | 24 | 12 | 23 | 10.615 | 3.0319 | -1.601 | 0 | 9.7073 | 16.0083 | 25.3194 | 40.0209 | 63.2656 | 6 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.3795 | 26.3795 | >1.000 | 26.3795 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038834 |  | Primary
4038648 | Audby Lane | RED | 33 | 11 | 23 | 11.5 | 23 | 17.7916 | 4.6344 | -30.349 | -0.913 | 6.716 | 13.1216 | 17.9428 | 32.804 | 54.697 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.147 | N/A | N/A | 4038861 |  | Primary
4038635 | Dunkeswick | RED | 33 | 11 | 12 | 12 | 8 | 6.9288 | 1.2223 | -30.349 | -0.26 | 3.5992 | 16.0083 | 8.6518 | 40.0209 | 22.4831 | 11 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.621 | N/A | N/A | 4038861 |  | Primary
4038694 | Fenton Lane | RED | 33 | 11 | 23 | 11.5 | 23 | 7.3546 | 0.94718 | -30.349 | -6.737 | 6.2298 | 13.1216 | 19.4431 | 32.804 | 59.2704 | 9 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038861 |  | Primary
4038647 | Leeds Road | RED | 33 | 11 | 24 | 12 | 8 | 5.6158 | 1.0365 | -30.349 | 0 | 4.6527 | 12.5 | 11.563 | 31.25 | 37.2219 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038861 |  | Primary
4038814 | Sherburn | RED | 33 | 11 | 25 | 12.5 | 25 | 14.4884 | -1.7365 | -30.349 | -8.514 | 12.3213 | 24.9835 | 32.3797 | 62.4588 | 51.8416 | 2 | 100% | 25 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.526 | N/A | N/A | 4038861 |  | Primary
4038650 | Tadcaster | RED | 33 | 11 | 23 | 11.5 | 23 | 13.4694 | 4.6623 | -30.349 | -2.456 | 8.9601 | 13.1216 | 24.2904 | 32.804 | 74.0471 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038861 |  | Primary
4038649 | Warren Lane | RED | 33 | 11 | 23 | 11.5 | 8 | 4.4977 | -0.35519 | -30.349 | -1.263 | 5.311 | 16.0083 | 14.614 | 40.0209 | 36.516 | 8 | 50% | 5.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038861 |  | Primary
4038720 | Holderness | RED | 33 | 11 | 18.75 | 15 | 23 | 12.1155 | 2.4875 | -56.55 | -0.613 | 10.6899 | 13.1216 | 27.3636 | 32.804 | 83.4155 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038878 |  | Primary
4038718 | Saltshouse Road | RED | 33 | 11 | 18.75 | 15 | 23 | 11.5938 | 3.6712 | -56.55 | -0.2 | 11.4607 | 13.1216 | 29.5166 | 32.804 | 89.9785 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.474 | N/A | N/A | 4038878 |  | Primary
4038715 | Tiverton Road | RED | 33 | 11 | 23 | 11.5 | 23 | 14.0054 | 3.0151 | -56.55 | 0 | 8.6846 | 13.1216 | 24.1601 | 32.804 | 73.6499 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.326 | N/A | N/A | 4038878 |  | Primary
4038714 | Wawne Road | RED | 33 | 11 | 24 | 12 | 24 | 8.5736 | 1.2516 | -56.55 | -8.632 | 11 | 18.3702 | 29.8924 | 45.9256 | 65.0887 | 9 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038878 |  | Primary
4038523 | Bailiff Bridge | RED | 33 | 11 | 24 | 12 | 24 | 7.999 | 1.8845 | -1.695 | -0.095 | 9.4457 | 13.1216 | 24.8569 | 32.804 | 75.7741 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.2446 | 1.8845 | >40.227 | 19.2446 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038846 |  | Primary
4038525 | Brighouse 33/11kV | RED | 33 | 11 | 12 | 12 | 12 | 10.9842 | 1.5997 | -1.695 | 0 | 9.9406 | 13.1216 | 27.0581 | 32.804 | 82.4841 | 10 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | VOLTAGE OUT OF STATUTORY LIMIT | 0 | 0 | >40.227 | 0 | RED | No | None | N/A | N/A | -0.463 | N/A | N/A | 4038846 |  | Primary
4038528 | Deighton | RED | 33 | 11 | 18.75 | 15 | 23 | 19.47 | 5.0462 | -1.695 | 0 | 10.1574 | 13.1216 | 26.5219 | 32.804 | 80.8497 | 7 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.5468 | 19.3922 | >40.227 | 25.5468 | RED | No | None | N/A | N/A | -4.404 | N/A | N/A | 4038846 |  | Primary
4038787 | Lowfields | RED | 33 | 11 | 24 | 12 | 19 | 5.0175 | 1.332 | -1.695 | 0 | 9.3875 | 13.1216 | 24.0226 | 32.804 | 73.2308 | 6 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.6181 | 25.332 | >40.227 | 27.6181 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038846 |  | Primary
4038795 | Millroyd Street | RED | 33 | 11 | 12.5 | 10 | 15.3 | 11.5572 | 2.9817 | -1.695 | 0 | 8.139 | 13.1216 | 21.9659 | 32.804 | 66.961 | 6 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 18.6467 | 15.4817 | >40.227 | 18.6467 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038846 |  | Primary
4038474 | Snelsins Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 11.1226 | 0.62159 | -1.695 | -1.6 | 10.7416 | 13.1216 | 27.3922 | 32.804 | 83.5027 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.8607 | 19.3716 | >40.227 | 26.8607 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038846 |  | Primary
4038480 | Spenborough | RED | 33 | 11 | 30 | 15 | 30 | 12.986 | 2.3868 | -1.695 | 0 | 8.8834 | 19.9973 | 23.3618 | 49.9933 | 46.7299 | 8 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 17.7525 | 17.7525 | >40.227 | 17.7525 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038846 |  | Primary
4038757 | Drax Primary | RED | 66 | 11 | 7.5 | 7.5 | 8 | 7.97 | 0.39466 | -139.391 | -10.611 | 5.0262 | 13.1216 | 13.0258 | 32.804 | 39.7081 | 8 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096998 |  | Primary
4038602 | Crowle | RED | 66 | 11 | 7.5 | 7.5 | 6.5 | 5.05 | 0.76958 | -139.391 | -0.768 | 4.7004 | 13.1216 | 12.2771 | 32.804 | 37.4257 | 8 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.827 | N/A | N/A | 7096998 |  | Primary
4038761 | Goole | RED | 66 | 11 | 18.75 | 15 | 23 | 16.2887 | 5.1433 | -139.391 | -0.211 | 11.2815 | 13.1216 | 30.4972 | 32.804 | 92.9679 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.46 | N/A | N/A | 7096998 |  | Primary
4038828 | Guardian Glass | RED | 66 | 11 | 30 | 15 | 30 | 3.9727 | 2.4339 | -139.391 | 0 | 10.0287 | 19.9973 | 26.8218 | 49.9933 | 53.6509 | 4 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.947 | N/A | N/A | 7096998 |  | Primary
4038759 | Rawcliffe | RED | 66 | 11 | 18.75 | 15 | 8 | 4.2814 | 1.3819 | -139.391 | -0.2 | 5.3578 | 16 | 13.3325 | 40 | 33.4865 | 3 | 100% | 15 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -6.316 | N/A | N/A | 7096998 |  | Primary
4038877 | Cornwall Street | RED | 132 | 11 | 30 | 15 | 39 | 16.9576 | 3.1827 | -633.218 | -0.107 | 9.9077 | 13.1216 | 28.551 | 32.804 | 87.0352 | 0 | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 33.0607 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.122 | N/A | N/A | 7096969 |  | BSP
4038598 | Armthorpe | RED | 66 | 11 | 18.75 | 15 | 12 | 11.0056 | -2.5653 | -132.742 | -6.323 | 8.083 | 19.9448 | 21.3455 | 49.8621 | 42.809 | 5 | 100% | 15 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.579 | N/A | N/A | 4038899 |  | Primary
4038696 | Askern | RED | 66 | 11 | 23 | 11.5 | 23 | 9.3765 | -1.401 | -132.742 | -7.144 | 10.3796 | 13.1216 | 27.7279 | 32.804 | 84.526 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038623 | Austerfield | RED | 66 | 11 | 12.5 | 10 | 8 | 4.5808 | 0.67092 | -132.742 | 0 | 4.0353 | 16.0083 | 10.4754 | 40.0209 | 26.1748 | 5 | 100% | 10 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038591 | Balby | RED | 66 | 11 | 18.75 | 15 | 22.86 | 11.6155 | 1.4517 | -132.742 | -1.308 | 11.8603 | 13.1216 | 30.6376 | 32.804 | 93.396 | 5 | 50% | 9.375 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.199 | N/A | N/A | 4038899 |  | Primary
4038586 | Barnburgh | RED | 66 | 11 | 24 | 12 | 24 | 9.5314 | -5.7127 | -132.742 | -8.421 | 11.5867 | 25 | 29.5693 | 62.5 | 47.311 | 5 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.163 | N/A | N/A | 4038899 |  | Primary
4038587 | Brodsworth | RED | 66 | 11 | 18.75 | 15 | 23 | 14.3275 | 1.2557 | -132.742 | -0.526 | 11.9142 | 13.1216 | 31.0814 | 32.804 | 94.7488 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -3.728 | N/A | N/A | 4038899 |  | Primary
4038585 | Hickleton | RED | 66 | 11 | 18.75 | 15 | 23 | 6.1387 | -2.7626 | -132.742 | -7.5 | 11.5025 | 13.1216 | 29.2191 | 32.804 | 89.0718 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038593 | ICI Fibres | RED | 66 | 11 | 18.75 | 15 | 23 | 10.2633 | -2.0128 | -132.742 | -8.515 | 14.7972 | 19.9973 | 37.9406 | 49.9933 | 75.8913 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038596 | Kirk Sandall | RED | 66 | 11 | 24 | 12 | 24 | 11.5184 | 2.1706 | -132.742 | 0 | 11.7273 | 13.1216 | 31.9391 | 32.804 | 97.3633 | 8 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.244 | N/A | N/A | 4038899 |  | Primary
4038597 | Markham Gates | RED | 66 | 11 | 18.75 | 15 | 23 | 15.8404 | 3.8387 | -132.742 | 0 | 11.1007 | 18.3702 | 29.3 | 45.9256 | 63.7988 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.547 | N/A | N/A | 4038899 |  | Primary
4038595 | Rockware | RED | 66 | 11 | 18.75 | 15 | 23 | 19.3797 | 6.95 | -132.742 | -3 | 12.1926 | 13.1216 | 32.7102 | 32.804 | 99.7142 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038599 | Stainforth | RED | 66 | 11 | 18.75 | 15 | 23 | 7.2026 | 0.55252 | -132.742 | -1.331 | 12.1428 | 13.1216 | 31.2329 | 32.804 | 95.2108 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.631 | N/A | N/A | 4038899 |  | Primary
4038600 | Thorne | RED | 66 | 11 | 18.75 | 15 | 23 | 16.61 | 1.5355 | -132.742 | -4.719 | 10.6086 | 13.1216 | 27.8357 | 32.804 | 84.8547 | 4 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.895 | N/A | N/A | 4038899 |  | Primary
4038604 | West End Lane | RED | 66 | 11 | 18.75 | 15 | 23 | 11.7769 | 1.9832 | -132.742 | -4 | 10.6702 | 25 | 27.6776 | 62.5 | 44.2842 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 20.7332 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038801 | West Moor Park | RED | 66 | 11 | 24 | 12 | 25 | 17.7453 | 2.2446 | -132.742 | -3.745 | 12.6624 | 24.9835 | 32.7663 | 62.4588 | 52.4606 | 5 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 25.6886 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.556 | N/A | N/A | 4038899 |  | Primary
4038594 | Wheatley Park | RED | 66 | 11 | 18.75 | 15 | 23 | 8.7753 | 2.0869 | -132.742 | 0 | 11.1134 | 13.1216 | 28.8892 | 32.804 | 88.0661 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 2.0869 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038899 |  | Primary
4038589 | Belmont Avenue | RED | 33 | 11 | 23 | 11.5 | 23 | 18.3554 | 2.9402 | 0 | 0 | 8.4383 | 13.1216 | 24.1935 | 32.804 | 73.7518 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -3.158 | N/A | N/A | 4038851 |  | Primary
4038588 | Bentley | RED | 33 | 11 | 24 | 12 | 24 | 11.9009 | 2.0729 | 0 | 0 | 8.8781 | 18.3702 | 23.2125 | 45.9256 | 50.5437 | 9 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038851 |  | Primary
4038590 | Greyfriars Rd | RED | 33 | 11 | 23 | 15 | 24 | 9.7157 | 2.6718 | 0 | 0 | 8.3165 | 16.0083 | 22.9363 | 40.0209 | 57.3108 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038851 |  | Primary
7256105 | Greyfriars Road 3/4 | RED | 33 | 11 | 30 | 15 | 30 | 8.4335 | 1.8686 | 0 | 0 | 8.1106 | 19.9973 | 21.5395 | 49.9933 | 43.0849 | 9 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038851 |  | Primary
4038592 | Jarratt Street | RED | 33 | 11 | 23 | 11.5 | 23 | 20.05 | 6.9376 | 0 | 0 | 9.7394 | 13.1216 | 27.8047 | 32.804 | 84.76 | 6 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 18.4376 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038851 |  | Primary
4038763 | Belthorpe Lane | RED | 66 | 11 | 24 | 12 | 8 | 4.5466 | 0.73998 | -189.461 | -0.077 | 4.9824 | 24.9835 | 12.1525 | 62.4588 | 19.9429 | 10 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 4038872 |  | Primary
4038723 | Brett Street | RED | 66 | 11 | 24 | 12 | 24 | 19.0523 | 5.9717 | -189.461 | -1.646 | 12.0148 | 16 | 30.7341 | 40 | 76.8351 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.4 | N/A | N/A | 4038872 |  | Primary
4038725 | Burton Pidsea | RED | 66 | 11 | 24 | 12 | 9 | 4.8181 | -9.087 | -189.461 | -15.131 | 7.5349 | 13.1216 | 19.6822 | 32.804 | 59.9994 | 6 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -14.302 | N/A | N/A | 4038872 |  | Primary
4038700 | Butterwick | RED | 66 | 11 | 15 | 7.5 | 6.5 | 5.0798 | -7.3702 | -189.461 | -7.907 | 5.8821 | 13.1216 | 14.6678 | 32.804 | 44.8279 | 10 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.391 | N/A | N/A | 4038872 |  | Primary
4038790 | Driffield | RED | 66 | 11 | 24 | 12 | 24 | 16.8032 | 3.8025 | -189.461 | -4.385 | 9.2252 | 13.1216 | 26.062 | 32.804 | 79.4475 | 7 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.2 | N/A | N/A | 4038872 |  | Primary
4038822 | Hayton | RED | 66 | 11 | 12.5 | 10 | 15.3 | 13.25 | 1.7069 | -189.461 | -4.2 | 6.8775 | 19.9973 | 17.9385 | 49.9933 | 35.8819 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.116 | N/A | N/A | 4038872 |  | Primary
4038713 | Hunmanby | RED | 66 | 11 | 24 | 12 | 24 | 8.4325 | 1.8549 | -189.461 | -0.784 | 10.0193 | 24.9835 | 24.1027 | 62.4588 | 40.1037 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 4038872 |  | Primary
4038699 | Kirkburn | RED | 66 | 11 | 30 | 15 | 8 | 6.7 | -2.0128 | -189.461 | -4.108 | 6.1854 | 19.9973 | 16.6085 | 49.9933 | 33.2215 | 6 | 100% | 15 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.674 | N/A | N/A | 4038872 |  | Primary
4038724 | Martongate | RED | 66 | 11 | 12.5 | 10 | 15.3 | 12.9579 | 1.361 | -189.461 | -0.402 | 7.3772 | 13.1216 | 19.4766 | 32.804 | 59.3727 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -0.1 | N/A | N/A | 4038872 |  | Primary
4038760 | Sandhill Lane | RED | 66 | 11 | 10 | 5 | 8 | 5.0497 | 1.3517 | -189.461 | -0.92 | 4.4054 | 13.1216 | 10.7434 | 32.804 | 33.5734 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | N/A | N/A | N/A | 4038872 |  | Primary
4038826 | Seaton | RED | 66 | 11 | 20 | 10 | 20 | 16.9617 | 2.3482 | -189.461 | -3.089 | 11.6456 | 19.9973 | 30.636 | 49.9933 | 61.2802 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -4.705 | N/A | N/A | 4038872 |  | Primary
4038683 | Commonside Lane | RED | 33 | 11 | 24 | 12 | 24 | 16.6747 | -1.184 | -28.168 | -0.184 | 10.2509 | 13.1216 | 29.3852 | 32.804 | 89.5782 | 6 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 20.3076 | 12.596 | >1.000 | 20.3076 | RED | No | None | N/A | N/A | -10.22 | N/A | N/A | 4038868 |  | Primary
4038680 | Normanton | RED | 33 | 11 | 23 | 11.5 | 23 | 17.5124 | 6.1908 | -28.168 | -0.105 | 7.9862 | 13.1216 | 22.1197 | 32.804 | 67.4298 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.0895 | 5.8258 | >1.000 | 27.0895 | RED | No | None | N/A | N/A | -0.365 | N/A | N/A | 4038868 |  | Primary
4038690 | Prince of Wales | RED | 33 | 11 | 23 | 11.5 | 23 | 10.7629 | 2.3975 | -28.168 | -2.821 | 9.6024 | 13.1216 | 25.9675 | 32.804 | 79.1595 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.4428 | 13.6555 | >1.000 | 25.4428 | RED | No | None | N/A | N/A | -0.242 | N/A | N/A | 4038868 |  | Primary
4038681 | Sharlston | RED | 33 | 11 | 23 | 11.5 | 23 | 11.3658 | 2.6047 | -28.168 | -0.99 | 8.4403 | 13.1216 | 22.9734 | 32.804 | 70.0324 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 28.4491 | 14.1047 | >1.000 | 28.4491 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038868 |  | Primary
4038685 | Wellington Street | RED | 33 | 11 | 23 | 11.5 | 23 | 16.7655 | 4.7391 | -28.168 | -0.1 | 7.9202 | 13.1216 | 21.7074 | 32.804 | 66.1729 | 6 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 20.9286 | 12.9721 | >1.000 | 20.9286 | RED | No | None | N/A | N/A | -3.267 | N/A | N/A | 4038868 |  | Primary
4038461 | Crown Street | RED | 33 | 11 | 23 | 11.5 | 8 | 4.7883 | 0.85071 | -13.014 | 0 | 4.751 | 13.1216 | 12.8957 | 32.804 | 39.3115 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.9977 | 0.85071 | >1.000 | 22.9977 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038833 |  | Primary
4038456 | Four Lane Ends | RED | 33 | 11 | 23 | 11.5 | 23 | 14.3174 | 2.4847 | -13.014 | 0 | 8.2939 | 13.1216 | 23.2457 | 32.804 | 70.8624 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.1186 | 0.9057 | >1.000 | 24.1186 | RED | No | None | N/A | N/A | -1.579 | N/A | N/A | 4038833 |  | Primary
4038458 | Legrams Mill Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 9.9161 | 2.8058 | -13.014 | 0 | 11.204 | 13.1216 | 28.971 | 32.804 | 88.3155 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.4114 | 21.5558 | >1.000 | 23.4114 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038833 |  | Primary
4038467 | Rawson Road | RED | 33 | 11 | 23 | 11.5 | 23 | 10.9938 | 1.3849 | -13.014 | -0.402 | 8.9985 | 13.1216 | 24.4725 | 32.804 | 74.6021 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.3714 | 1.3849 | >1.000 | 22.3714 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038833 |  | Primary
4038459 | Saint Street | RED | 33 | 11 | 23 | 11.5 | 23 | 6.48 | 1.2516 | -13.014 | 0 | 8.0936 | 13.1216 | 21.7485 | 32.804 | 66.2985 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.0085 | 12.7516 | >1.000 | 22.0085 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038833 |  | Primary
4038457 | Toller Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 10.7585 | 2.9872 | -13.014 | -0.25 | 10.8038 | 13.1216 | 27.9302 | 32.804 | 85.1426 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.2486 | 21.7372 | >1.000 | 23.2486 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038833 |  | Primary
4038843 | Halifax 33/11kV | RED | 33 | 11 | 40 | 20 | 40 | 33.6825 | 7.1236 | 0 | 0 | 8.2867 | 25.036 | 24.3973 | 62.59 | 38.9796 | 8 | 100% | 40 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 3.3546 | 3.3546 | >40.227 | 3.3546 | RED | No | None | N/A | N/A | -1.21 | N/A | N/A | 7558610 |  | Primary
4038484 | Burnleyville | RED | 33 | 11 | 23 | 11.5 | 23 | 13.0392 | 2.9244 | -1.446 | -0.074 | 7.6034 | 13.1216 | 20.9351 | 32.804 | 63.8188 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 25.018 | 2.9244 | >1.000 | 25.018 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038837 |  | Primary
4038481 | Liversedge | RED | 33 | 11 | 18.75 | 15 | 23 | 10.8698 | 2.7639 | -1.446 | 0 | 10.3002 | 13.1216 | 26.6738 | 32.804 | 81.3127 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 20.1203 | 2.7639 | >1.000 | 20.1203 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038837 |  | Primary
4038810 | Nab Lane | RED | 33 | 11 | 25 | 12.5 | 12 | 9.3588 | 1.5096 | -1.446 | -1.372 | 5.0463 | 19.9973 | 13.1577 | 49.9933 | 26.3189 | 8 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.4075 | 14.0096 | >1.000 | 22.4075 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038837 |  | Primary
4038651 | White Lee | RED | 33 | 11 | 23 | 15 | 23 | 11.6044 | 3.2315 | -1.446 | 0 | 7.656 | 13.1216 | 21.2453 | 32.804 | 64.7643 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 26.4793 | 3.2315 | >1.000 | 26.4793 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038837 |  | Primary
4038501 | Denholme | RED | 33 | 11 | 12 | 12 | 6.5 | 3.8452 | 0.31573 | -21.213 | -0.954 | 4.8976 | 13.1216 | 11.8636 | 32.804 | 37.325 | 8 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 19.3434 | 12.3157 | >1.000 | 19.3434 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038842 |  | Primary
4038507 | Furness Avenue | RED | 33 | 11 | 23 | 11.5 | 23 | 12.2767 | 3.0389 | -21.213 | -0.332 | 4.7464 | 13.1216 | 13.7233 | 32.804 | 41.8342 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 25.4502 | 3.0389 | >1.000 | 25.4502 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038842 |  | Primary
4038508 | Gibraltar Road | RED | 33 | 11 | 24 | 12 | 24 | 15.3658 | 5.4301 | -21.213 | 0 | 9.7997 | 13.1216 | 25.4142 | 32.804 | 77.4728 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.8327 | 5.4301 | >1.000 | 26.8327 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038842 |  | Primary
4038514 | Queensbury | RED | 33 | 11 | 24 | 12 | 24 | 14.5277 | 3.1994 | -21.213 | -0.316 | 9.3017 | 13.1216 | 24.5535 | 32.804 | 74.8492 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.4691 | 27.1994 | >1.000 | 27.4691 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038842 |  | Primary
4038510 | Swan Bank Lane | RED | 33 | 11 | 24 | 12 | 24 | 12.3087 | 2.3383 | 0 | 0 | 9.9609 | 13.1216 | 26.8435 | 32.804 | 81.83 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 3.3546 | 2.3383 | >40.227 | 3.3546 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7558610 |  | Primary
4038455 | Thornton | RED | 33 | 11 | 18.75 | 15 | 23 | 12.6588 | 3.3222 | -21.213 | 0 | 8.0737 | 13.1216 | 20.4092 | 32.804 | 62.2157 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.7058 | 22.0722 | >1.000 | 25.7058 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038842 |  | Primary
4038728 | Easington | RED | 33 | 11 | 24 | 12 | 17 | 5.4446 | 1.6751 | -75.865 | -1.158 | 11.7405 | 13.1216 | 30.2494 | 32.804 | 92.2125 | 1 | 100% | 24 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 5.7502 | 5.7502 | >22.421 | 5.7502 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038879 |  | Primary
4038721 | Hedon Road | RED | 33 | 11 | 23 | 11.5 | 23 | 15.7319 | 2.2055 | -75.865 | -2.105 | 8.5393 | 13.1216 | 23.8533 | 32.804 | 72.7145 | 6 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 42.3709 | 13.7055 | >22.421 | 42.3709 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038879 |  | Primary
4038893 | Hull East 33/11kV | RED | 33 | 11 | 25 | 12.5 | 23 | 12.4933 | 2.8711 | -75.865 | -2.138 | 8.1476 | 13.1216 | 28.4661 | 32.804 | 86.7763 | 8 | 100% | 25 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.3016 | 26.3016 | >22.421 | 26.3016 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038879 |  | Primary
4038719 | King George Dock | RED | 33 | 11 | 30 | 15 | 30 | 8.3319 | 2.01 | -75.865 | -0.491 | 8.9343 | 25 | 23.8136 | 62.5 | 38.1018 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.1049 | 17.694 | >22.421 | 24.1049 | RED | No | None | N/A | N/A | -14.316 | N/A | N/A | 4038879 |  | Primary
4038807 | Ottringham Road | RED | 33 | 11 | 24 | 12 | 15 | 13.062 | -13.9807 | -75.865 | -15.789 | 11.4946 | 13.1216 | 28.6443 | 32.804 | 87.6002 | 1 | 100% | 12 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >22.421 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038879 |  | Primary
4038726 | Patrington Road | RED | 33 | 11 | 24 | 12 | 8 | 5.29 | -4.1735 | -75.865 | -6.999 | 9.6894 | 13.1216 | 23.791 | 32.804 | 73.843 | 1 | TBC | 0 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 3.6398 | 0 | >22.421 | 3.6398 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038879 |  | Primary
4038717 | Westcott Street | RED | 33 | 11 | 23 | 11.5 | 23 | 14.1893 | 2.0799 | -75.865 | -0.618 | 8.3947 | 13.1216 | 23.1543 | 32.804 | 70.5838 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 17.8666 | 2.0799 | >22.421 | 17.8666 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038879 |  | Primary
4038727 | Withernsea | RED | 33 | 11 | 24 | 12 | 10 | 5.7786 | 0.96691 | -75.865 | -8.462 | 4.9619 | 13.1216 | 12.571 | 32.804 | 38.3216 | 1 | TBC | 0 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 7.7014 | 0.96691 | >22.421 | 7.7014 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038879 |  | Primary
4038704 | Elgar Road | RED | 33 | 11 | 18.75 | 15 | 23 | 15.5115 | 4.5227 | -22.127 | 0 | 11.1863 | 13.1216 | 29.4316 | 32.804 | 89.7195 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 29.2135 | 23.2727 | >1.000 | 29.2135 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038871 |  | Primary
4038698 | Gibson Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 15.7459 | 3.4548 | -22.127 | -0.291 | 10.2886 | 13.1216 | 26.4436 | 32.804 | 80.6109 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.5896 | 17.7918 | >1.000 | 26.5896 | RED | No | None | N/A | N/A | -4.413 | N/A | N/A | 4038871 |  | Primary
4038766-1 | Newport 1 | RED | 33 | 11 | 24 | 12 | 18.4 | 16.7086 | -1.1938 | -22.127 | -9.174 | 9.8835 | 13.1216 | 26.1198 | 32.804 | 79.6238 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 3.1518 | 0 | >1.000 | 3.1518 | RED | No | None | N/A | N/A | -4.211 | N/A | N/A | 4038871 |  | Primary
4038697 | Skillings Lane | RED | 33 | 11 | 23 | 15 | 24 | 9.7078 | 0.26639 | -22.127 | -3.82 | 8.035 | 19.9448 | 20.9386 | 49.8621 | 41.993 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | SOME VOLTAGE CONSTRAINT | 17.83 | 11.5664 | >1.000 | 17.83 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038871 |  | Primary
4038797 | Eggborough | RED | 66 | 11 | 7.5 | 7.5 | 8 | 4.44 | 1.2136 | -23.421 | -0.251 | 4.6747 | 13.1216 | 11.9041 | 32.804 | 36.2886 | 7 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038692-66 |  | Primary
4038692-11 | Ferrybridge A 11kV | RED | 66 | 11 | 30 | 15 | 30 | 22.9 | 6 | -23.421 | -0.829 | 11.9384 | 13.1216 | 31.5743 | 32.804 | 96.2514 | 7 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.672 | N/A | N/A | 4038692-66 |  | Primary
7501276 | South Elmsall | RED | 66 | 11 | 30 | 15 | 30 | 14.5864 | 2.0885 | -23.421 | -2.4 | 11.3416 | 13.1216 | 27.2677 | 32.804 | 86.4348 | 7 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -4 | N/A | N/A | 4038692-66 |  | Primary
4038816 | Grimethorpe | RED | 66 | 11 | 25 | 12.5 | 25 | 8.3748 | -2.9501 | -23.421 | -5.788 | 12.9152 | 24.9835 | 32.9426 | 62.4588 | 52.7429 | 7 | 100% | 25 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038692-66 |  | Primary
4038684 | Hemsworth | RED | 66 | 11 | 12.5 | 10 | 10 | 8.5184 | 1.2728 | -23.421 | -1.302 | 4.6446 | 25 | 12.2334 | 62.5 | 19.5735 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038692-66 |  | Primary
4038686 | Ledston | RED | 66 | 11 | 18.75 | 15 | 23 | 12.1228 | 3.1178 | -23.421 | -0.325 | 10.8764 | 13.1216 | 26.8376 | 32.804 | 82.8895 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038692-66 |  | Primary
4038581 | Monckton | RED | 66 | 11 | 12.5 | 10 | 15.3 | 8.8669 | 2.038 | -23.421 | -10 | 11.3604 | 13.1216 | 29.845 | 32.804 | 90.9799 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -6.316 | N/A | N/A | 4038692-66 |  | Primary
4038689 | South Kirkby | RED | 66 | 11 | 18.75 | 15 | 23 | 19.6512 | 3.3941 | -23.421 | -2.526 | 10.8862 | 25 | 27.8221 | 62.5 | 44.5153 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.767 | N/A | N/A | 4038692-66 |  | Primary
4038738 | Convamore Road | RED | 33 | 11 | 23 | 15 | 23 | 11.295 | 2.9593 | -26.895 | 0 | 9.3479 | 13.1216 | 24.8622 | 32.804 | 75.79 | 7 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.7651 | 12.8803 | >1.000 | 23.7651 | RED | No | None | N/A | N/A | -1.579 | N/A | N/A | 4038884 |  | Primary
4038740 | Conyard Road | RED | 33 | 11 | 18.75 | 15 | 23 | 8.7008 | 1.8056 | -26.895 | 0 | 10.2002 | 13.1216 | 25.495 | 32.804 | 77.7359 | 6 | 50% | 9.375 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.2855 | 11.1806 | >1.000 | 22.2855 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038884 |  | Primary
4038741 | Wesley Crescent | RED | 33 | 11 | 23 | 11.5 | 23 | 13.1628 | 1.184 | -26.895 | -5.842 | 10.2014 | 13.1216 | 28.0807 | 32.804 | 85.6016 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.1752 | 0.15497 | >1.000 | 22.1752 | RED | No | None | N/A | N/A | -1.029 | N/A | N/A | 4038884 |  | Primary
4038580 | Burton Road | RED | 33 | 11 | 30 | 15 | 22.9 | 17.4619 | 9.8664 | -0.577 | -0.577 | 9.3921 | 13.1216 | 25.6977 | 32.804 | 78.337 | 11 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -1.601 | N/A | N/A | 4038850 |  | Primary
4038578 | Fish Dam Lane | RED | 33 | 11 | 24 | 12 | 24 | 10.0436 | 3.4409 | -0.577 | 0 | 9.5625 | 13.1216 | 25.0264 | 32.804 | 76.2906 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.211 | N/A | N/A | 4038850 |  | Primary
4038579 | Stairfoot | RED | 33 | 11 | 24 | 12 | 24 | 18.6 | 3.392 | -0.577 | 0 | 9.792 | 13.1216 | 26.5663 | 32.804 | 80.9849 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -7.368 | N/A | N/A | 4038850 |  | Primary
4038534 | Hope | RED | 66 | 11 | 18.75 | 15 | 23 | 4.8414 | 1.3819 | -9.539 | -1.136 | 8.609 | 13.1216 | 20.5743 | 32.804 | 65.6095 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038896 |  | Primary
4038533 | Penistone | RED | 66 | 11 | 24 | 12 | 24 | 13.3421 | -2.2101 | -9.539 | -6.984 | 11.7593 | 13.1216 | 30.5764 | 32.804 | 93.2093 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038896 |  | Primary
4038535 | Wheatacre Road | RED | 66 | 11 | 12.5 | 10 | 8 | 8.01 | 2.1022 | -9.539 | -1.419 | 4.9975 | 13.1216 | 13.2825 | 32.804 | 40.4904 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038896 |  | Primary
4038782 | Barrow | RED | 33 | 11 | 24 | 12 | 11.6 | 7.2688 | 1.9338 | -91.829 | -0.477 | 3.9158 | 13.1216 | 9.4122 | 32.804 | 29.8426 | 11 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.168 | N/A | N/A | 4038881 |  | Primary
4038786 | Clough Lane | RED | 33 | 11 | 24 | 12 | 8 | 3.3019 | 0.34533 | -91.829 | 0 | 4.2975 | 19.9448 | 10.0454 | 49.8621 | 21.5467 | 10 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.1 | N/A | N/A | 4038881 |  | Primary
4038730 | Eastfield Road | RED | 33 | 11 | 23 | 15 | 7 | 6.53 | 0.78932 | -91.829 | -0.746 | 9.2692 | 18.3702 | 24.1 | 45.9256 | 52.4762 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038881 |  | Primary
4038731 | Humber Road | RED | 33 | 11 | 23 | 11.5 | 23 | 11.1944 | 3.0704 | -91.829 | -0.211 | 10.8023 | 13.1216 | 28.1159 | 32.804 | 85.7089 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -4.337 | N/A | N/A | 4038881 |  | Primary
4038732 | Queens Road | RED | 33 | 11 | 40 | 20 | 37 | 21.4295 | 4.1769 | -91.829 | -2.5 | 11.8752 | 19.9973 | 32.7791 | 49.9933 | 65.567 | 4 | 100% | 40 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -4.568 | N/A | N/A | 4038881 |  | Primary
4038539 | Baslow Road | RED | 33 | 11 | 24 | 12 | 24 | 9.92 | 1.2489 | -0.186 | 0 | 10.1081 | 13.1216 | 26.1076 | 32.804 | 79.5867 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >52.632 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096996 |  | Primary
4038556 | Dronfield | RED | 33 | 11 | 24 | 12 | 24 | 10.8402 | 2.6522 | -0.186 | -0.091 | 10.8745 | 13.1216 | 28.598 | 32.804 | 87.1785 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >52.632 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096996 |  | Primary
4038547 | Greenhill | RED | 33 | 11 | 24 | 12 | 10 | 6.2416 | 1.4602 | -0.186 | 0 | 6.2235 | 13.1216 | 16.5657 | 32.804 | 50.4989 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >52.632 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096996 |  | Primary
4038544 | Millhouses | RED | 33 | 11 | 24 | 12 | 24 | 6.93 | 1.7405 | -0.186 | 0 | 10.6559 | 13.1216 | 27.9276 | 32.804 | 85.1347 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >52.632 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096996 |  | Primary
4038549 | Woodseats | RED | 33 | 11 | 24 | 12 | 24 | 15.2749 | 2.8267 | -0.186 | -0.095 | 10.9445 | 13.1216 | 29.0184 | 32.804 | 88.4601 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >52.632 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096996 |  | Primary
4038840 | Keighley | RED | 132 | 11 | 30 | 15 | 39 | 16.96 | 1.5969 | -50.123 | -0.063 | 9.4051 | 13.1216 | 26.5875 | 32.804 | 81.0495 | 0 | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 31.5079 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.089 | N/A | N/A | 7096989 |  | BSP
4038695 | Beal | RED | 33 | 11 | 30 | 15 | 16.2 | 8.21 | -8.4259 | -30.005 | -13.475 | 9.7373 | 19.9973 | 25.1045 | 49.9933 | 50.2157 | 9 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 13.0143 | 13.0143 | >1.000 | 13.0143 | RED | No | None | N/A | N/A | -2.35 | N/A | N/A | 4038869 |  | Primary
4038687 | Carr Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 13.5747 | 4.5227 | -30.005 | -1.695 | 8.9503 | 13.1216 | 23.052 | 32.804 | 70.2718 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 13.0143 | 13.0143 | >1.000 | 13.0143 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038869 |  | Primary
4038688 | Smith Street | RED | 33 | 11 | 23 | 11.5 | 23 | 7.9287 | 2.0589 | -30.005 | 0 | 7.8651 | 13.1216 | 20.6449 | 32.804 | 62.9341 | 7 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 13.0143 | 12.2959 | >1.000 | 13.0143 | RED | No | None | N/A | N/A | -1.263 | N/A | N/A | 4038869 |  | Primary
7395321 | Pollington | RED | 33 | 11 | 30 | 15 | 8.5 | 6.6758 | -6.1665 | -30.005 | -9.947 | 4.6914 | 13.1216 | 11.5675 | 32.804 | 35.7536 | 5 | 100% | 15 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | SOME VOLTAGE CONSTRAINT | 10.6312 | 8.8335 | >1.000 | 10.6312 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038869 |  | Primary
4038693 | Weeland Road | RED | 33 | 11 | 23 | 11.5 | 21.1 | 21.04 | 11.5301 | -30.005 | -4.888 | 11.3804 | 13.1216 | 32.0323 | 32.804 | 97.6476 | 14 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 13.0143 | 11.5301 | >1.000 | 13.0143 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038869 |  | Primary
4038624 | Abbey Road | RED | 33 | 11 | 23 | 11.5 | 23 | 13.1605 | 2.2683 | -1.102 | 0 | 7.9925 | 13.1216 | 22.0629 | 32.804 | 67.2568 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 25.9978 | 2.2683 | >1.000 | 25.9978 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 4038894 |  | Primary
4038656 | Bramley | RED | 33 | 11 | 18.75 | 15 | 23 | 17.7399 | 3.8178 | -1.102 | 0 | 10.2402 | 13.1216 | 26.9141 | 32.804 | 82.0451 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.9326 | 22.5678 | >1.000 | 24.9326 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 4038894 |  | Primary
4038657 | Farnley Crescent | RED | 33 | 11 | 24 | 12 | 24 | 12.6 | 1.6751 | -1.102 | -0.096 | 9.5301 | 13.1216 | 25.7822 | 32.804 | 78.5946 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 28.1375 | 1.6751 | >1.000 | 28.1375 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 4038894 |  | Primary
4038634 | Fir Tree Lane | RED | 33 | 11 | 23 | 11.5 | 23 | 16.3741 | 4.8578 | -1.102 | 0 | 7.4287 | 16.0083 | 20.8793 | 40.0209 | 52.171 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 28.0881 | 4.8578 | >1.000 | 28.0881 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 4038894 |  | Primary
4038625 | Iveson House | RED | 33 | 11 | 18.75 | 15 | 23 | 13.8485 | 3.5316 | -1.102 | -0.255 | 10.3089 | 13.1216 | 27.5622 | 32.804 | 84.021 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.2645 | 22.2816 | >1.000 | 24.2645 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 4038894 |  | Primary
4038626 | West Park | RED | 33 | 11 | 23 | 11.5 | 12 | 8.4178 | 2.0226 | -1.102 | 0 | 4.4863 | 13.1216 | 12.5484 | 32.804 | 38.2527 | 6 | 50% | 5.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 15.9295 | 7.7196 | >1.000 | 15.9295 | GREEN | No | None | N/A | N/A | -0.053 | N/A | N/A | 4038894 |  | Primary
4038659 | Whingate | RED | 33 | 11 | 18.75 | 15 | 23 | 6.9637 | 2.3591 | -1.102 | -0.751 | 8.5135 | 17.4955 | 21.0463 | 43.7387 | 48.6612 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.8256 | 21.1091 | >1.000 | 27.8256 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 4038894 |  | Primary
4038802 | Burley Street | RED | 33 | 11 | 40 | 20 | 34.8 | 22.6538 | 3.6012 | -16.389 | 0 | 8.9058 | 13.1216 | 26.4408 | 32.804 | 80.6022 | 4 | 100% | 40 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 40.2181 | 40.2181 | >1.000 | 40.2181 | GREEN | No | None | N/A | N/A | -0.242 | N/A | N/A | 7097003 |  | Primary
4038628 | Clarendon Road | RED | 33 | 11 | 23 | 11.5 | 23 | 13.8281 | 0.71038 | -16.389 | -0.6 | 7.9819 | 13.1216 | 24.549 | 32.804 | 74.8353 | 3 | TBC | 0 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 17.957 | 0.71038 | >1.000 | 17.957 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7097003 |  | Primary
4038630 | Upper Basinghall Street | RED | 33 | 11 | 24 | 12 | 24 | 14.1102 | 4.36 | -16.389 | 0 | 10.1899 | 13.1216 | 26.6436 | 32.804 | 81.2205 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 20.0818 | 3.176 | >1.000 | 20.0818 | GREEN | No | None | N/A | N/A | -1.184 | N/A | N/A | 7097003 |  | Primary
4038633-1 | Allerton Hill T1 | RED | 33 | 11 | 18.75 | 15 | 23 | 8.8574 | 0.039466 | -20.697 | 0 | 12.3568 | 13.1216 | 31.549 | 32.804 | 96.1741 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 23.0434 | 0.039466 | >1.000 | 23.0434 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038859 |  | Primary
4038637 | Burmantofts | RED | 33 | 11 | 18.75 | 15 | 23 | 14.01 | 2.1023 | -20.697 | -4.5 | 12.7903 | 19.9973 | 33.9803 | 49.9933 | 67.9698 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 34.0775 | 16.1153 | >1.000 | 34.0775 | RED | No | None | N/A | N/A | -4.737 | N/A | N/A | 4038859 |  | Primary
4038638 | Hillcrest | RED | 33 | 11 | 18.75 | 15 | 23 | 12.5209 | 4.4459 | -20.697 | -0.358 | 11.4133 | 13.1216 | 29.8514 | 32.804 | 90.9992 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 27.1652 | 4.4459 | >1.000 | 27.1652 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038859 |  | Primary
4038789 | Knostrop | RED | 33 | 11 | 24 | 12 | 24 | 6.9168 | 0.64132 | -20.697 | -1.509 | 10.5484 | 13.1216 | 27.3931 | 32.804 | 83.5054 | 6 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 20.4897 | 15.6243 | >1.000 | 20.4897 | RED | No | None | N/A | N/A | -9.017 | N/A | N/A | 4038859 |  | Primary
4038639 | Pontefract Lane 1/2 | RED | 33 | 11 | 23 | 11.5 | 23 | 12.7467 | 2.4638 | -20.697 | 0 | 8.6077 | 13.1216 | 23.8728 | 32.804 | 72.774 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.5812 | 0 | >1.000 | 19.5812 | RED | No | None | N/A | N/A | -3.694 | N/A | N/A | 4038859 |  | Primary
4038643 | Selby Road | RED | 33 | 11 | 18.75 | 15 | 23 | 14.8966 | 2.1706 | -20.697 | -0.098 | 11.5936 | 13.1216 | 30.149 | 32.804 | 91.9065 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.9153 | 20.8626 | >1.000 | 22.9153 | RED | No | None | N/A | N/A | -0.058 | N/A | N/A | 4038859 |  | Primary
4038641 | York Road | RED | 33 | 11 | 18.75 | 15 | 23 | 18.8376 | 5.2556 | -20.697 | -0.063 | 11.3498 | 13.1216 | 30.3593 | 32.804 | 92.5476 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 21.1491 | 21.1491 | >1.000 | 21.1491 | RED | No | None | N/A | N/A | -0.777 | N/A | N/A | 4038859 |  | Primary
4038632 | Buslingthorpe Green | RED | 33 | 11 | 23 | 11.5 | 23 | 12.2792 | 1.5843 | -4.358 | -2 | 9.6612 | 13.1216 | 27.0989 | 32.804 | 82.6086 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.6891 | 13.0843 | >1.000 | 27.6891 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038858 |  | Primary
4038631 | Carlton Hill | RED | 33 | 11 | 18.75 | 15 | 23 | 18.8125 | 5.6324 | -4.358 | -2.105 | 11.0392 | 13.1216 | 29.204 | 32.804 | 89.0257 | 4 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.8784 | 24.2774 | >1.000 | 26.8784 | RED | No | None | N/A | N/A | -0.105 | N/A | N/A | 4038858 |  | Primary
4038636 | Leylands Road | RED | 33 | 11 | 23 | 11.5 | 23 | 14.219 | 4.7042 | -4.358 | 0 | 8.536 | 13.1216 | 24.0927 | 32.804 | 73.4444 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 33.2642 | 16.2042 | >1.000 | 33.2642 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038858 |  | Primary
4038627 | Moor Road | RED | 33 | 11 | 18.75 | 15 | 23 | 20.0428 | 5.2346 | -4.358 | -0.253 | 11.0613 | 13.1216 | 29.3467 | 32.804 | 89.4608 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.6035 | 23.9846 | >1.000 | 27.6035 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038858 |  | Primary
4038515 | Dowker Street | RED | 33 | 11 | 23 | 15 | 24 | 12.4885 | 2.119 | -4.619 | 0 | 8.8175 | 13.1216 | 22.7722 | 32.804 | 69.4191 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 27.8622 | 1.225 | >40.227 | 27.8622 | RED | No | None | N/A | N/A | -0.894 | N/A | N/A | 4038844 |  | Primary
4038522 | Grove Street | RED | 33 | 11 | 23 | 11.5 | 23 | 10.92 | 2.3242 | -4.619 | 0 | 7.8907 | 13.1216 | 21.5486 | 32.804 | 65.6889 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.0366 | 13.8242 | >40.227 | 24.0366 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038844 |  | Primary
4038517 | Honley | RED | 33 | 11 | 24 | 12 | 24 | 10.7645 | 2.4624 | -4.619 | -0.091 | 8.6035 | 13.1216 | 21.756 | 32.804 | 66.3211 | 9 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 13.8559 | 13.8559 | >40.227 | 13.8559 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038844 |  | Primary
4038512 | Meltham | RED | 33 | 11 | 23 | 11.5 | 23 | 9.1606 | 1.2432 | -4.619 | -0.151 | 7.13 | 13.1216 | 18.5536 | 32.804 | 56.5591 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.5129 | 1.1072 | >40.227 | 24.5129 | RED | No | None | N/A | N/A | -0.136 | N/A | N/A | 4038844 |  | Primary
4038516 | Oakes Road | RED | 33 | 11 | 24 | 12 | 24 | 15.3706 | 3.6768 | -4.619 | 0 | 9.8813 | 13.1216 | 27.5056 | 32.804 | 83.8482 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 23.7184 | 3.6768 | >40.227 | 23.7184 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038844 |  | Primary
4038511 | Prospect Road | RED | 33 | 11 | 23 | 11.5 | 23 | 19.7704 | 1.1248 | -4.619 | -3.368 | 8.2483 | 13.1216 | 22.8357 | 32.804 | 69.6126 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.1951 | 1.1248 | >40.227 | 20.1951 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038844 |  | Primary
4038506 | Slaithwaite | RED | 33 | 11 | 24 | 12 | 24 | 7.3632 | 1.8579 | -4.619 | -1.009 | 7.5493 | 19.9973 | 18.6975 | 49.9933 | 37.7518 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 17.3497 | 1.8579 | >40.227 | 17.3497 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038844 |  | Primary
7096966 | Armouries Drive | RED | 33 | 11 | 30 | 15 | 30 | 9.5282 | 1.7587 | -1.039 | -0.592 | 8.8389 | 19.9973 | 23.4763 | 49.9933 | 46.959 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 7.5788 | 7.5788 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -0.454 | N/A | N/A | 4038900 |  | Primary
4038670 | Brookfield Street | RED | 33 | 11 | 23 | 11.5 | 23 | 10.2622 | 4.2645 | -1.039 | -0.111 | 9.1508 | 13.1216 | 25.2324 | 32.804 | 76.9185 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 7.5788 | 3.6595 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -0.605 | N/A | N/A | 4038900 |  | Primary
4038669 | Clarence Road | RED | 33 | 11 | 30 | 15 | 22.86 | 11.49 | 4.1834 | -1.039 | -0.2 | 7.7902 | 13.1216 | 21.4171 | 32.804 | 65.288 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 7.5788 | 7.5788 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038900 |  | Primary
4038667 | Holbeck | RED | 33 | 11 | 23 | 11.5 | 23 | 17.0384 | 4.9834 | -1.039 | 0 | 8.9963 | 16.0083 | 24.909 | 40.0209 | 62.24 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 7.5788 | 4.8364 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -0.147 | N/A | N/A | 4038900 |  | Primary
4038671 | Leasowe Road | RED | 33 | 11 | 23 | 11.5 | 23 | 11.278 | 3.6014 | -1.039 | 0 | 9.4459 | 13.1216 | 26.0052 | 32.804 | 79.2744 | 5 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 7.5788 | 7.5788 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -1.053 | N/A | N/A | 4038900 |  | Primary
4038672 | Stourton 33/11kV | RED | 33 | 11 | 18.75 | 15 | 19.4 | 15.4821 | 1.7658 | -1.039 | 0 | 11.6108 | 13.1216 | 29.0445 | 32.804 | 88.5397 | 4 | 50% | 9.375 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 7.5788 | 7.5788 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -1.609 | N/A | N/A | 4038900 |  | Primary
4038831 | Sweet Street | RED | 33 | 11 | 30 | 15 | 30 | 11.0751 | 1.7901 | -1.039 | -0.136 | 9.4343 | 19.9973 | 26.5086 | 49.9933 | 53.0244 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 7.5788 | 7.5788 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038900 |  | Primary
7322111 | Whitehall Road 2/3 | RED | 33 | 11 | 30 | 15 | 30 | 6.4404 | 1.3005 | -8.568 | 0 | 8.6529 | 19.9973 | 22.153 | 49.9933 | 44.3119 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 7.5788 | 7.5788 | >1.000 | 7.5788 | RED | No | None | N/A | N/A | -0.35 | N/A | N/A | 7096967 |  | Primary
4038488 | Bramhope | RED | 33 | 11 | 24 | 12 | 8 | 3.391 | 1.0261 | -8.425 | 0 | 4.3812 | 13.1216 | 10.4384 | 32.804 | 33.3892 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 14.2378 | 1.0261 | >1.000 | 14.2378 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038836 |  | Primary
4038475 | Chevin End | RED | 33 | 11 | 30 | 15 | 30 | 7.9272 | 1.2234 | -8.425 | 0 | 8.1712 | 19.9973 | 21.5133 | 49.9933 | 43.0325 | 7 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.9835 | 23.9835 | >1.000 | 23.9835 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038836 |  | Primary
4038478 | Hallam Street | RED | 33 | 11 | 24 | 12 | 23 | 10.7484 | 0.75972 | -8.425 | -4.8 | 11.251 | 13.1216 | 29.6562 | 32.804 | 90.4041 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.1094 | 0.75972 | >1.000 | 22.1094 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038836 |  | Primary
4038464 | Kirk Drive | RED | 33 | 11 | 23 | 11.5 | 23 | 19.9158 | 3.7394 | -8.425 | -2.166 | 7.9175 | 13.1216 | 20.452 | 32.804 | 62.3462 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 21.4622 | 3.7394 | >1.000 | 21.4622 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038836 |  | Primary
4038483 | North Avenue | RED | 33 | 11 | 18.75 | 15 | 23 | 12.0455 | 2.5196 | -8.425 | -1.364 | 8.8651 | 13.1216 | 22.0135 | 32.804 | 67.5614 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 22.4398 | 21.0836 | >1.000 | 22.4398 | RED | No | None | N/A | N/A | -0.186 | N/A | N/A | 4038836 |  | Primary
4038823 | Pool | RED | 33 | 11 | 24 | 12 | 23.3 | 8.1653 | 1.2591 | -8.425 | -0.095 | 7.5798 | 19.9973 | 19.7219 | 49.9933 | 39.4491 | 7 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 16.7625 | 16.7625 | >1.000 | 16.7625 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038836 |  | Primary
4038736 | Doughty Road | RED | 33 | 11 | 24 | 12 | 20.9 | 17.5 | 5.1718 | -4.328 | 0 | 9.9017 | 13.1216 | 27.8554 | 32.804 | 84.9146 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 19.7418 | 5.1718 | >1.000 | 19.7418 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038883 |  | Primary
4038737 | Grimsby Docks | RED | 33 | 6.6 | 18.75 | 15 | 23 | 2.2466 | 0.63145 | -4.328 | 0 | 13.2559 | 13.1216 | 34.423 | 32.804 | 104.9353 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 18.6651 | 0.63145 | >1.000 | 18.6651 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038883 |  | Primary
4038739 | Marsden Road | RED | 33 | 11 | 24 | 12 | 18 | 15.2 | 5.4789 | -4.328 | -4.328 | 9.422 | 13.1216 | 25.6434 | 32.804 | 78.1717 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 20.5812 | 0.2159 | >1.000 | 20.5812 | RED | No | None | N/A | N/A | -5.263 | N/A | N/A | 4038883 |  | Primary
4038550 | Blue Boy Street | RED | 33 | 11 | 24 | 12 | 24 | 10.345 | 1.5355 | -3.061 | 0 | 10.5013 | 13.1216 | 27.7181 | 32.804 | 84.4961 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.2408 | 1.4445 | >52.632 | 24.2408 | GREEN | No | None | N/A | N/A | -0.091 | N/A | N/A | 7096975 |  | Primary
4038542 | Claywheels Lane | RED | 33 | 11 | 24 | 12 | 24 | 20.4374 | 4.6735 | -3.061 | -0.151 | 9.3212 | 13.1216 | 26.8959 | 32.804 | 81.9896 | 9 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.8931 | 23.8931 | >52.632 | 23.8931 | GREEN | No | None | N/A | N/A | -2.737 | N/A | N/A | 7096975 |  | Primary
4038545 | Crookesmoor Road | RED | 33 | 11 | 23 | 11.5 | 24 | 16.6523 | 4.1807 | -3.061 | 0 | 10.3592 | 13.1216 | 28.279 | 32.804 | 86.2059 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 26.4567 | 4.1807 | >52.632 | 26.4567 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096975 |  | Primary
4038537 | Loxley Road | RED | 33 | 11 | 24 | 12 | 8 | 3.0585 | 0.42426 | -3.061 | 0 | 5.2924 | 13.1216 | 12.8618 | 32.804 | 40.3338 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 25.0757 | 0.42426 | >52.632 | 25.0757 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096975 |  | Primary
4038546 | Penistone Road | RED | 33 | 11 | 23 | 11.5 | 20.2 | 8.3203 | 0.18746 | -3.061 | -2.91 | 11.5532 | 13.1216 | 30.9796 | 32.804 | 94.4385 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 25.5477 | 0.18746 | >52.632 | 25.5477 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096975 |  | Primary
4038543 | Rawson Spring Road | RED | 33 | 11 | 23 | 11.5 | 20.2 | 12.5014 | 4.1738 | -3.061 | 0 | 10.0775 | 13.1216 | 27.7985 | 32.804 | 84.7413 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 29.1622 | 3.9208 | >52.632 | 29.1622 | GREEN | No | None | N/A | N/A | -0.253 | N/A | N/A | 7096975 |  | Primary
4038540 | Stannington Road | RED | 33 | 11 | 23 | 11.5 | 24 | 15.4328 | 3.1896 | -3.061 | 0 | 10.1883 | 13.1216 | 27.9308 | 32.804 | 85.1445 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 20.7398 | 3.1896 | >52.632 | 20.7398 | GREEN | No | None | N/A | N/A | N/A | N/A | N/A | 7096975 |  | Primary
4038561 | Gleadless Valley | RED | 33 | 11 | 24 | 12 | 24 | 10.3744 | 2.387 | -0.248 | -0.105 | 10.9931 | 13.1216 | 29.0167 | 32.804 | 88.4548 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 22.0269 | 2.387 | >52.632 | 22.0269 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096976 |  | Primary
4038541 | Marmion Road | RED | 33 | 11 | 24 | 12 | 24 | 22.89 | 3.8108 | -0.248 | 0 | 10.9284 | 13.1216 | 29.571 | 32.804 | 90.1444 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 27.5646 | 3.8108 | >52.632 | 27.5646 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096976 |  | Primary
4038559 | Norfolk Park | RED | 33 | 11 | 24 | 12 | 24 | 15.465 | 1.2694 | -0.248 | -0.143 | 10.8481 | 13.1216 | 28.5008 | 32.804 | 86.8822 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.7047 | 1.2694 | >52.632 | 19.7047 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096976 |  | Primary
4038805 | Saxon Road | RED | 33 | 11 | 24 | 12 | 24 | 10.99 | 2.9312 | -0.248 | 0 | 11.2447 | 13.1216 | 30.3292 | 32.804 | 92.4558 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 27.7595 | 2.9312 | >52.632 | 27.7595 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096976 |  | Primary
4038538 | Snaithing Park Road | RED | 33 | 11 | 24 | 12 | 24 | 11.0101 | 1.5913 | -0.248 | 0 | 10.7415 | 13.1216 | 28.2311 | 32.804 | 86.06 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.9133 | 1.5913 | >52.632 | 24.9133 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096976 |  | Primary
4038753 | Olympia Mills | RED | 33 | 11 | 30 | 15 | 30 | 15.94 | 2.7951 | -66.857 | -5.07 | 9.1287 | 19.9973 | 25.0682 | 49.9933 | 50.1432 | 2 | 100% | 30 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -5.263 | N/A | N/A | 4038886 |  | Primary
4038752 | Selby | RED | 33 | 11 | 30 | 15 | 29 | 23.2 | 2.4271 | -66.857 | -6.527 | 8.7971 | 19.9973 | 24.0702 | 49.9933 | 48.1468 | 4 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -8.947 | N/A | N/A | 4038886 |  | Primary
4038762 | Thorpe Road | RED | 33 | 11 | 24 | 12 | 24 | 17.8987 | 2.6941 | -66.857 | -4.126 | 9.4143 | 13.1216 | 24.1282 | 32.804 | 73.5525 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.784 | N/A | N/A | 4038886 |  | Primary
4038853 | Park Street | RED | 132 | 11 | 30 | 15 | 39 | 13.5384 | 3.6963 | -267.182 | -10.105 | 10.24 | 13.1216 | 28.5088 | 32.804 | 86.9064 | 0 | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096988-1 |  | BSP
7256106 | Barnsley Road | RED | 33 | 11 | 30 | 15 | 30 | 9.9439 | 3.1562 | -0.256 | 0 | 8.8376 | 19.9973 | 23.264 | 49.9933 | 46.5342 | 7 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >21.053 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096977 |  | Primary
4038560 | Bellhouse Road | RED | 33 | 11 | 23 | 11.5 | 23 | 11.231 | 1.7937 | -0.256 | -0.111 | 10.2915 | 13.1216 | 27.5058 | 32.804 | 83.8489 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >21.053 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096977 |  | Primary
4038563 | Newhall Road | RED | 33 | 11 | 24 | 12 | 24 | 17.1893 | 1.9403 | -0.256 | -0.145 | 11.2716 | 13.1216 | 31.1628 | 32.804 | 94.9969 | 13 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >21.053 | 0 | RED | No | None | N/A | N/A | -0.632 | N/A | N/A | 7096977 |  | Primary
4038555 | Stanley Street | RED | 33 | 11 | 24 | 12 | 24 | 14.5206 | 3.3013 | -0.256 | 0 | 10.9815 | 13.1216 | 29.7938 | 32.804 | 90.8238 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >21.053 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096977 |  | Primary
4038564 | Stevenson Road | RED | 33 | 11 | 24 | 12 | 19.4 | 9.5038 | 1.1832 | -0.256 | 0 | 11.3438 | 13.1216 | 30.5848 | 32.804 | 93.235 | 13 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >21.053 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096977 |  | Primary
4038854 | Rawmarsh Road 1_2 | RED | 132 | 11 | 30 | 30 | 39 | 23.2389 | 6.9683 | -267.182 | -0.384 | 9.8905 | 13.1216 | 28.718 | 32.804 | 87.5443 | 0 | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096988-1 |  | BSP
4038898 | Rawmarsh Road 3_4 | RED | 132 | 11 | 30 | 30 | 39 | 28.16 | 4.23 | -267.182 | -0.158 | 9.7365 | 13.1216 | 28.3032 | 32.804 | 86.2796 | 0 | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096988-1 |  | BSP
4038482 | Rawdon | RED | 33 | 11 | 30 | 15 | 23 | 12.8095 | 4.0452 | -0.368 | -0.063 | 9.0389 | 25 | 22.4538 | 62.5 | 36.1555 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.6426 | 24.6426 | >1.000 | 24.6426 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038838 |  | Primary
4038486 | Rodley Lane | RED | 33 | 11 | 12.5 | 10 | 15.3 | 13.4276 | 1.4992 | -0.368 | -0.2 | 8.1676 | 16.0083 | 22.0839 | 40.0209 | 55.181 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.5459 | 1.4992 | >1.000 | 19.5459 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038838 |  | Primary
4038653 | Swinnow Moor | RED | 33 | 11 | 18.75 | 15 | 23 | 14.096 | 3.4423 | -0.368 | 0 | 10.3673 | 19.9448 | 27.406 | 49.8621 | 54.9635 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 43.3925 | 3.1793 | >1.000 | 43.3925 | RED | No | None | N/A | N/A | -0.263 | N/A | N/A | 4038838 |  | Primary
4038479 | Thornbury | RED | 33 | 11 | 18.75 | 15 | 23 | 14.0849 | 5.3533 | -0.368 | 0 | 9.2271 | 13.1216 | 23.267 | 32.804 | 70.9272 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 21.026 | 5.0373 | >1.000 | 21.026 | RED | No | None | N/A | N/A | -0.316 | N/A | N/A | 4038838 |  | Primary
4038485 | Varley Street | RED | 33 | 11 | 18.75 | 15 | 23 | 14.4775 | 4.6344 | -0.368 | -0.105 | 11.589 | 16.0083 | 32.1766 | 40.0209 | 80.3996 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.0669 | 23.3844 | >1.000 | 25.0669 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038838 |  | Primary
4038815 | Ellifoot Lane | RED | 33 | 11 | 25 | 12.5 | 2.1 | 2.38 | -1.628 | -16.264 | -10.579 | 8.0852 | 24.9835 | 21.6252 | 62.4588 | 34.6231 | 4 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >22.421 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038880 |  | Primary
4038809 | Yorkshire Water Hull Road | RED | 33 | 11 | 24 | 12 | 23 | 6.6863 | -0.41439 | -16.264 | -5.685 | 8.8785 | 24.9835 | 24.9775 | 62.4588 | 39.9904 | 6 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >22.421 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038880 |  | Primary
4038773 | Firth Brown | RED | 33 | 11 | 24 | 12 | 24 | 11.2712 | 1.9347 | -60.871 | -0.08 | 13.4927 | 16.0083 | 34.5149 | 40.0209 | 86.2423 | 11 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038889 |  | Primary
4038779 | Hibaldstow | RED | 33 | 11 | 12.5 | 10 | 15.3 | 9.7595 | 1.5355 | -60.871 | -2.032 | 6.0828 | 13.1216 | 14.7302 | 32.804 | 46.3569 | 7 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.274 | N/A | N/A | 4038889 |  | Primary
4038781 | Pasture Road South | RED | 33 | 11 | 24 | 12 | 20 | 9.6322 | 1.3517 | -60.871 | -1.308 | 6.3502 | 13.1216 | 14.5645 | 32.804 | 48.3948 | 9 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038889 |  | Primary
4038774 | South Ferriby | RED | 33 | 11 | 30 | 15 | 21 | 15.2528 | 1.2728 | -60.871 | -2.9 | 9.8245 | 20 | 28.4031 | 50 | 56.8061 | 9 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -12.063 | N/A | N/A | 4038889 |  | Primary
7378946 | Wrawby | RED | 33 | 11 | 30 | 15 | 30 | 17.5982 | 4.6637 | -60.871 | -4.024 | 9.8442 | 13.1216 | 26.0825 | 32.804 | 79.5101 | 5 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -2.901 | N/A | N/A | 4038889 |  | Primary
4038875 | Sculcoates A | RED | 132 | 11 | 30 | 15 | 39 | 24.5848 | 6.6892 | -633.218 | -1.123 | 12.5896 | 18.3702 | 36.5943 | 45.9256 | 79.6818 | 0 | 100% | 30 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 36.4622 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.227 | N/A | N/A | 7096969 |  | BSP
4038791 | Billet Lane | RED | 33 | 11 | 24 | 12 | 24 | 12.1518 | 2.1 | -74.211 | -0.8 | 11.4844 | 24.9835 | 30.127 | 62.4588 | 48.2349 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -8 | N/A | N/A | 4038887 |  | Primary
4038768 | Flixborough | RED | 33 | 11 | 24 | 12 | 24 | 17.885 | 3.2734 | -74.211 | -4.211 | 11.2433 | 13.1216 | 29.9714 | 32.804 | 91.3652 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -2.715 | N/A | N/A | 4038887 |  | Primary
4038770 | Foxhills | RED | 33 | 11 | 24 | 12 | 18 | 15.8435 | 3.63 | -74.211 | -0.14 | 12.1038 | 13.1216 | 33.8569 | 32.804 | 103.2097 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -1.41 | N/A | N/A | 4038887 |  | Primary
4038771 | Station Road | RED | 33 | 11 | 30 | 15 | 24.8 | 21.1337 | 6.8259 | -74.211 | -1.353 | 8.4778 | 13.1216 | 23.2663 | 32.804 | 70.9253 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038887 |  | Primary
4038772 | Bottesford | RED | 33 | 11 | 18.75 | 18.75 | 22.86 | 12.2909 | 6.7289 | -73.962 | 0 | 11.6146 | 13.1216 | 30.3174 | 32.804 | 92.4197 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.816 | N/A | N/A | 4038888 |  | Primary
4038769 | Bridges Road | RED | 33 | 11 | 23 | 11.5 | 23 | 14.1253 | 2.7429 | -73.962 | -1.052 | 8.204 | 13.1216 | 22.7814 | 32.804 | 69.4471 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038888 |  | Primary
4038554 | Arundel Street | RED | 33 | 11 | 24 | 12 | 24 | 17.6921 | 4.4878 | -0.173 | 0 | 11.0943 | 13.1216 | 30.7277 | 32.804 | 93.6707 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 33.8232 | 4.4878 | >43.526 | 33.8232 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096980 |  | Primary
4038551 | Ellin Street 1/3 | RED | 33 | 11 | 24 | 12 | 40.8 | 15.0758 | 5.0588 | -0.173 | -0.173 | 11.4156 | 16.0083 | 31.3131 | 40.0209 | 78.242 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 32.0467 | 5.0588 | >43.526 | 32.0467 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096980 |  | Primary
4038568-1 | Mansfield Road | RED | 33 | 11 | 24 | 12 | 16 | 11.2406 | 2.5056 | -0.173 | 0 | 5.9883 | 13.1216 | 15.4529 | 32.804 | 47.1069 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.6519 | 2.5056 | >43.526 | 19.6519 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096980 |  | Primary
4038557 | Park Hill | RED | 33 | 11 | 24 | 12 | 24 | 13.2059 | 1.9942 | -0.173 | 0 | 10.9953 | 25 | 29.7006 | 62.5 | 47.521 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.0208 | 1.9942 | >43.526 | 24.0208 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096980 |  | Primary
4038553 | Silver Street | RED | 33 | 11 | 24 | 12 | 24 | 12.6353 | 2.8063 | -0.173 | 0 | 11.1924 | 13.1216 | 29.9834 | 32.804 | 91.4017 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 28.7531 | 2.8063 | >43.526 | 28.7531 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096980 |  | Primary
4038548 | Victoria Street | RED | 33 | 11 | 24 | 12 | 24 | 19.1234 | 7.3424 | -0.173 | 0 | 10.1181 | 15.3085 | 22.7056 | 39 | 66.0949 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 27.1462 | 4.7104 | >43.526 | 27.1462 | RED | No | None | N/A | N/A | -2.632 | N/A | N/A | 7096980 |  | Primary
4038489 | Barnoldswick | RED | 33 | 11 | 12.5 | 10 | 15.3 | 10.1292 | 2.8546 | -3.783 | 0 | 5.6394 | 13.1216 | 13.1014 | 32.804 | 42.9782 | 9 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038839 |  | Primary
4038498 | Bolton Road | RED | 33 | 11 | 12.5 | 10 | 15.3 | 6.9672 | 1.9124 | -3.783 | -0.164 | 8.7509 | 13.1216 | 22.7663 | 32.804 | 69.4011 | 5 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038839 |  | Primary
4038500 | Chelker Reservoir | RED | 33 | 11 | 24 | 12 | 8 | 4.041 | 0.88798 | -3.783 | -0.213 | 5.0407 | 12.5 | 12.9748 | 31.25 | 41.5194 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038839 |  | Primary
4038493 | Cracoe | RED | 33 | 11 | 10 | 10 | 12.5 | 6.9924 | 1.4657 | -3.783 | -0.345 | 5.6495 | 13.1216 | 12.6903 | 32.804 | 43.0546 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038839 |  | Primary
4038496 | Crosshills | RED | 33 | 11 | 12.5 | 10 | 15.3 | 10.9804 | 2.4358 | -3.783 | -1.33 | 7.4984 | 13.1216 | 19.4052 | 32.804 | 59.1551 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.67 | N/A | N/A | 4038839 |  | Primary
4038504 | Ilkley | RED | 33 | 11 | 18.75 | 15 | 23 | 12.8094 | 3.1617 | -3.783 | 0 | 9.2353 | 13.1216 | 22.7823 | 32.804 | 70.3824 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038839 |  | Primary
4038491 | Ings Lane | RED | 33 | 11 | 23 | 11.5 | 8 | 6.36 | 1.6427 | -3.783 | 0 | 4.6019 | 13.1216 | 11.3648 | 32.804 | 35.0713 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.24 | N/A | N/A | 4038839 |  | Primary
4038490 | Salterforth | RED | 33 | 11 | 12.5 | 10 | 15.3 | 10.1052 | 1.9068 | -3.783 | 0 | 5.9321 | 13.1216 | 14.4504 | 32.804 | 45.2088 | 10 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.105 | N/A | N/A | 4038839 |  | Primary
7096982 | Skipton | RED | 33 | 11 | 30 | 15 | 19.2 | 13.6769 | 1.6331 | -3.783 | -1.64 | 7.7435 | 19.9973 | 19.4222 | 49.9933 | 38.8495 | 8 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.689 | N/A | N/A | 4038839 |  | Primary
4038513 | Elland 33/11kV | RED | 33 | 11 | 18.75 | 15 | 18.21 | 14.2125 | 3.2315 | -24.362 | -1.229 | 9.4288 | 13.1216 | 23.5492 | 32.804 | 71.8573 | 1 | 100% | 18.75 | OUT OF TAPS | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.0254 | 21.7875 | >40.227 | 24.0254 | RED | No | None | N/A | N/A | -0.194 | N/A | N/A | 4038897 |  | Primary
4038492 | Hebden Bridge | RED | 33 | 11 | 7.5 | 7.5 | 7.5 | 3.2131 | 0.31573 | -24.362 | 0 | 3.8024 | 18.3702 | 9.4969 | 45.9256 | 20.6988 | 5 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 18.0858 | 7.8157 | >40.227 | 18.0858 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038897 |  | Primary
4038495 | Mytholmroyd | RED | 33 | 11 | 12.5 | 10 | 15.3 | 9.8221 | 2.0031 | -24.362 | -0.084 | 7.1919 | 13.1216 | 18.0035 | 32.804 | 54.882 | 5 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 14.6843 | 14.5031 | >40.227 | 14.6843 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038897 |  | Primary
4038793 | Salterhebble | RED | 33 | 11 | 24 | 12 | 24 | 17.5882 | 5.0516 | -24.362 | -1.156 | 8.9807 | 13.1216 | 24.0765 | 32.804 | 73.395 | 7 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 29.922 | 27.6836 | >40.227 | 29.922 | RED | No | None | N/A | N/A | -1.368 | N/A | N/A | 4038897 |  | Primary
4038806 | Sowerby Bridge 33/11kV | RED | 33 | 11 | 24 | 12 | 23 | 17.0646 | 1.8592 | -24.362 | -0.736 | 10.3369 | 13.1216 | 28.4876 | 32.804 | 86.842 | 6 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 39.0761 | 25.8592 | >40.227 | 39.0761 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038897 |  | Primary
4038804 | Todmorden | RED | 33 | 11 | 24 | 12 | 23 | 12.7671 | 1.4787 | -24.362 | -0.105 | 7.8032 | 13.1216 | 19.5187 | 32.804 | 59.5011 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | SOME VOLTAGE CONSTRAINT | 13.465 | 13.465 | >40.227 | 13.465 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038897 |  | Primary
4038520 | Birkby | RED | 33 | 11 | 24 | 12 | 24 | 12.0962 | 1.5145 | -33.268 | 0 | 9.9827 | 13.1216 | 26.373 | 32.804 | 80.3956 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 18.6591 | 1.5145 | >1.000 | 18.6591 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038845 |  | Primary
4038527 | Dalton | RED | 33 | 11 | 24 | 12 | 24 | 14.22 | 4.11 | -33.268 | -0.171 | 9.9958 | 13.1216 | 26.8756 | 32.804 | 81.9278 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 25.3608 | 4.11 | >1.000 | 25.3608 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038845 |  | Primary
4038521 | Folly Hall | RED | 33 | 11 | 24 | 12 | 24 | 13.4105 | 3.6517 | -33.268 | -0.939 | 9.9057 | 12.5 | 26.4946 | 31.25 | 84.7827 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 27.3741 | 3.1457 | >1.000 | 27.3741 | RED | No | None | N/A | N/A | -0.506 | N/A | N/A | 4038845 |  | Primary
4038524 | Saint Andrews Road 33/11kV | RED | 33 | 11 | 23 | 11.5 | 23 | 12.5005 | 1.7728 | -33.268 | 0 | 8.4835 | 13.1216 | 23.1509 | 32.804 | 70.5734 | 7 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.75 | 13.2728 | >1.000 | 25.75 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038845 |  | Primary
4038518 | Yew Green Road | RED | 33 | 11 | 24 | 12 | 23 | 11.5991 | 2.052 | -33.268 | 0 | 10.0433 | 13.1216 | 25.9724 | 32.804 | 79.1746 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 23.9005 | 2.052 | >1.000 | 23.9005 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038845 |  | Primary
4038812 | Dudley Hill | RED | 33 | 11 | 25 | 15 | 30 | 17.3149 | 4.1735 | -12.522 | -0.737 | 9.1864 | 24.9835 | 24.5866 | 62.4588 | 39.3645 | 7 | 100% | 25 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.8038 | 24.8735 | >1.000 | 25.8038 | RED | No | None | N/A | N/A | -4.3 | N/A | N/A | 7240601 |  | Primary
4038466 | Low Moor | RED | 33 | 11 | 23 | 11.5 | 23 | 17.3841 | -2.0325 | -12.522 | -10.105 | 9.7102 | 13.1216 | 26.8817 | 32.804 | 81.9464 | 4 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 15.8137 | 9.4675 | >1.000 | 15.8137 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7240601 |  | Primary
4038465 | Odsal | RED | 33 | 11 | 23 | 11.5 | 23 | 16.2247 | 4.5576 | -12.522 | -0.436 | 8.5074 | 13.1216 | 23.8257 | 32.804 | 72.6304 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 20.6401 | 3.9256 | >1.000 | 20.6401 | RED | No | None | N/A | N/A | -0.632 | N/A | N/A | 7240601 |  | Primary
4038469 | Spring Mill Street | RED | 33 | 11 | 23 | 11.5 | 23 | 15.2059 | 4.5228 | -12.522 | -0.972 | 9.7951 | 13.1216 | 26.7245 | 32.804 | 81.4671 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 23.995 | 4.5228 | >1.000 | 23.995 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7240601 |  | Primary
4038476 | Tong Street | RED | 33 | 11 | 18.75 | 15 | 23 | 12.296 | 4.0202 | -12.522 | -0.106 | 10.503 | 13.1216 | 26.4113 | 32.804 | 80.5124 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 20.3054 | 4.0202 | >1.000 | 20.3054 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7240601 |  | Primary
4038460 | Wibsey | RED | 33 | 11 | 18.75 | 15 | 23 | 12.6841 | 1.6123 | -12.522 | -0.166 | 10.452 | 13.1216 | 26.5107 | 32.804 | 80.8154 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.6195 | 1.6123 | >1.000 | 19.6195 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7240601 |  | Primary
4000000 | Stourton 132/11kV | RED | 132 | 11 | 30 | 15 | 12 | 11.2758 | 3.3151 | -98.293 | -12.631 | 5.3195 | 13.1216 | 15.5846 | 32.804 | 47.5081 | 0 | 100% | 15 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 18.3151 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096981 |  | BSP
4038611 | Fullerton Road | RED | 33 | 11 | 24 | 12 | 24 | 11.633 | 2.0339 | 0 | 0 | 5.4912 | 13.1216 | 14.7806 | 32.804 | 45.0574 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 2.02 | 1.5079 | >1.000 | 2.02 | RED | No | None | N/A | N/A | -0.526 | N/A | N/A | 7096955 |  | Primary
4038655 | Batley | RED | 33 | 11 | 18.75 | 15 | 22.9 | 22.664 | 5.9814 | -81.137 | -0.211 | 11.3082 | 13.1216 | 29.4008 | 32.804 | 89.6256 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 28.5449 | 5.9814 | >40.227 | 28.5449 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038862 |  | Primary
4038652 | Calder Wharf | RED | 33 | 11 | 18.75 | 15 | 23 | 14.9329 | 2.4428 | -81.137 | -0.216 | 11.9617 | 13.1216 | 31.4499 | 32.804 | 95.8722 | 4 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 24.1371 | 21.1928 | >40.227 | 24.1371 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038862 |  | Primary
4038660 | Denby Grange | RED | 33 | 11 | 23 | 15 | 8 | 3.1822 | 1.0261 | -81.137 | -0.284 | 4.8151 | 13.1216 | 11.8229 | 32.804 | 36.6961 | 8 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 18.5439 | 1.0261 | >40.227 | 18.5439 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038862 |  | Primary
4038529 | Hazlehead | RED | 33 | 11 | 24 | 12 | 24 | 10.2837 | -9.5606 | -81.137 | -13.482 | 8.0594 | 13.1216 | 19.631 | 32.804 | 61.421 | 9 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.074119 | 0.074119 | >40.227 | 0.074119 | RED | No | None | N/A | N/A | -0.247 | N/A | N/A | 4038862 |  | Primary
4038666 | Horbury | RED | 33 | 11 | 24 | 12 | 23 | 10.9349 | 1.48 | -81.137 | 0 | 7.6484 | 13.1216 | 18.3198 | 32.804 | 58.2888 | 4 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 18.9893 | 18.9893 | >40.227 | 18.9893 | RED | No | None | N/A | N/A | -0.621 | N/A | N/A | 4038862 |  | Primary
4038530 | Mirfield | RED | 33 | 11 | 24 | 12 | 23 | 14.7315 | 4.5227 | -81.137 | -2.39 | 10.3229 | 13.1216 | 27.5668 | 32.804 | 84.0349 | 9 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.19 | 23.19 | >40.227 | 23.19 | RED | No | None | N/A | N/A | -0.379 | N/A | N/A | 4038862 |  | Primary
4038799 | Park Road | RED | 33 | 11 | 18.75 | 15 | 23 | 15.7656 | 2.0518 | -81.137 | 0 | 11.6442 | 13.1216 | 30.1182 | 32.804 | 91.8126 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.3752 | 0.58883 | >40.227 | 19.3752 | RED | No | None | N/A | N/A | -1.463 | N/A | N/A | 4038862 |  | Primary
4038526 | Scholes | RED | 33 | 11 | 24 | 12 | 24 | 11.2766 | 2.2594 | -81.137 | -6.554 | 7.45 | 13.12 | 18 | 32.8 | 56.7835 | 7 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | SOME VOLTAGE CONSTRAINT | 8.3991 | 8.3991 | >40.227 | 8.3991 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038862 |  | Primary
4038819 | Beighton | RED | 66 | 11 | 25 | 12.5 | 25 | 16.3647 | 3.0685 | -171.844 | -8.594 | 9.1422 | 19.9973 | 26.3023 | 49.9933 | 52.6117 | 7 | 100% | 25 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.579 | N/A | N/A | 7096994 |  | Primary
4038621 | Costhorpe | RED | 66 | 11 | 12.5 | 10 | 10 | 6.5652 | 1.9141 | -171.844 | -1.051 | 4.0895 | 24.9835 | 11.2985 | 62.4588 | 18.0895 | 5 | 100% | 10 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.041 | N/A | N/A | 7096994 |  | Primary
4038619 | Dinnington | RED | 66 | 11 | 30 | 15 | 30 | 16.3939 | 2.6047 | -171.844 | -8.421 | 11.97 | 19.9973 | 32.17 | 50 | 64.34 | 2 | 100% | 30 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096994 |  | Primary
4038603 | Edlington | RED | 66 | 11 | 18.75 | 15 | 23 | 16.073 | 3.5735 | -171.844 | -8.125 | 10.2919 | 13.1216 | 26.424 | 32.804 | 80.5512 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.526 | N/A | N/A | 7096994 |  | Primary
4038572 | Hackenthorpe | RED | 66 | 11 | 24 | 12 | 24 | 12.8604 | 2.1636 | -171.844 | 0 | 11.5669 | 13.1216 | 30.348 | 32.804 | 92.5131 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.232 | N/A | N/A | 7096994 |  | Primary
4038622 | Harworth | RED | 66 | 11 | 30 | 15 | 30 | 10.0693 | 2.3285 | -171.844 | -4.214 | 11.3418 | 13.1216 | 28.1517 | 32.804 | 86.4362 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -8.42 | N/A | N/A | 7096994 |  | Primary
4038616 | Kiveton Park | RED | 66 | 11 | 12.5 | 10 | 15.3 | 8.9408 | -2.0424 | -171.844 | -4.106 | 8.014 | 13.1216 | 21.0919 | 32.804 | 64.2967 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096994 |  | Primary
4038615 | Mexborough 1_2 | RED | 66 | 11 | 24 | 12 | 24 | 18.0352 | 3.124 | -171.844 | -0.1 | 11.5993 | 13.1216 | 30.9109 | 32.804 | 94.229 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096994 |  | Primary
4038617 | New Orchard Lane | RED | 66 | 11 | 18.75 | 15 | 23 | 14.9976 | 3.3502 | -171.844 | 0 | 11.3882 | 13.1216 | 30.494 | 32.804 | 92.9581 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 1.9722 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.378 | N/A | N/A | 7096994 |  | Primary
4038614 | Silverwood | RED | 66 | 11 | 18.75 | 15 | 23 | 14.5453 | 2.0226 | -171.844 | -0.265 | 10.2945 | 13.1216 | 27.3201 | 32.804 | 83.2829 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 1.8226 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 7096994 |  | Primary
4038620 | Tickhill Road | RED | 66 | 11 | 30 | 15 | 23 | 10.8524 | 1.7744 | -171.844 | 0 | 10.7606 | 13.1216 | 28.4489 | 32.804 | 86.7239 | 5 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 31.7744 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096994 |  | Primary
4038676 | Denby Dale Road | RED | 33 | 11 | 24 | 12 | 24 | 10.8699 | 1.3005 | -20.437 | 0 | 9.9502 | 13.1216 | 26.767 | 32.804 | 81.5968 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038865 |  | Primary
4038674 | Durkar Low Lane | RED | 33 | 11 | 18.75 | 15 | 24 | 16.6721 | 4.1039 | -20.437 | 0 | 10.2957 | 13.1216 | 27.0933 | 32.804 | 82.5915 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038865 |  | Primary
4038678 | Woodcock Street | RED | 33 | 11 | 23 | 11.5 | 20.2 | 13.0401 | 3.2734 | -20.437 | -0.437 | 10.6956 | 13.1216 | 28.7035 | 32.804 | 87.5 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.116 | N/A | N/A | 4038865 |  | Primary
4038677 | York Street | RED | 33 | 11 | 23 | 11.5 | 23 | 17.4121 | 2.4079 | -20.437 | 0 | 9.1381 | 13.1216 | 24.4402 | 32.804 | 74.5038 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038865 |  | Primary
4038673 | Alverthorpe Road | RED | 33 | 11 | 18.75 | 15 | 23 | 14.5854 | 3.8183 | -11.964 | -0.4 | 10.7293 | 13.1216 | 28.3943 | 32.804 | 86.5574 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 43.5555 | 22.5683 | >1.000 | 43.5555 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038866 |  | Primary
4038785 | Kenmore Road | RED | 33 | 11 | 24 | 12 | 24 | 16.55 | 4.4 | -11.964 | 0 | 10.7151 | 19.9448 | 28.952 | 49.8621 | 58.0642 | 10 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.4486 | 25.479 | >1.000 | 26.4486 | RED | No | None | N/A | N/A | -2.921 | N/A | N/A | 4038866 |  | Primary
4038662 | Milton Place | RED | 33 | 11 | 18.75 | 15 | 23 | 16.1449 | 3.6573 | -11.964 | -1.912 | 9.4572 | 13.1216 | 23.9276 | 32.804 | 72.9412 | 7 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.4772 | 21.7753 | >1.000 | 26.4772 | RED | No | None | N/A | N/A | -0.632 | N/A | N/A | 4038866 |  | Primary
4038675 | Outwood | RED | 33 | 11 | 18.75 | 15 | 23 | 19.6762 | 3.0487 | -11.964 | 0 | 10.8061 | 13.1216 | 28.5981 | 32.804 | 87.1787 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 26.718 | 3.0487 | >1.000 | 26.718 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038866 |  | Primary
4038679 | Royds Lane | RED | 33 | 11 | 23 | 11.5 | 23 | 13.6006 | 2.3186 | -11.964 | -9.652 | 9.2689 | 13.1216 | 24.0928 | 32.804 | 73.4449 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 19.6229 | 0.73961 | >1.000 | 19.6229 | RED | No | None | N/A | N/A | -1.579 | N/A | N/A | 4038866 |  | Primary
4038808 | Aldham | RED | 66 | 11 | 25 | 12.5 | 25 | 13.103 | 2.1146 | -43.109 | 0 | 11.5639 | 25 | 31.9165 | 62.5 | 51.0664 | 6 | 100% | 25 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -8.421 | N/A | N/A | 4038852 |  | Primary
4038800 | Dearne Road | RED | 66 | 11 | 24 | 12 | 24 | 12.86 | 2.1022 | -43.109 | -8.389 | 12.3054 | 13.1216 | 32.3724 | 32.804 | 98.6842 | 4 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038852 |  | Primary
4038558 | Ecclesfield | RED | 66 | 11 | 18.75 | 15 | 23 | 13.3851 | 2.722 | -43.109 | -9.9 | 11.601 | 13.1216 | 30.6714 | 32.804 | 93.4991 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038852 |  | Primary
4038582 | Elsecar | RED | 66 | 11 | 18.75 | 12 | 23 | 8.4439 | 2.6442 | -43.109 | -0.095 | 11.299 | 13.1216 | 30.174 | 32.804 | 91.9827 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038852 |  | Primary
4038583 | Houghton Main | RED | 66 | 11 | 12.5 | 10 | 15.3 | 7.6552 | -9.7974 | -43.109 | -13.2 | 11 | 13.1216 | 28.9171 | 32.804 | 88.1511 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -6.842 | N/A | N/A | 4038852 |  | Primary
7393498 | Kilnhurst | RED | 66 | 11 | 30 | 15 | 30 | 16.567 | 3.1248 | -43.109 | -1.526 | 10.0263 | 19.9973 | 26.7272 | 49.9933 | 53.4615 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038852 |  | Primary
4038552 | Tankersley Park | RED | 66 | 11 | 18.75 | 15 | 23 | 19.5734 | 4.1542 | -43.109 | 0 | 10.4835 | 16.0083 | 28.294 | 40.0209 | 70.6981 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038852 |  | Primary
4038584 | Wath Upon Dearne | RED | 66 | 11 | 30 | 15 | 24 | 13.1587 | 2.9895 | -43.109 | -9.999 | 10.0801 | 13.1216 | 26.6645 | 32.804 | 81.2842 | 4 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -3.231 | N/A | N/A | 4038852 |  | Primary
4038577 | Worsbrough Park | RED | 66 | 11 | 18.75 | 15 | 23 | 15.6335 | 3.9364 | -43.109 | 0 | 6.9201 | 13.1216 | 16.2099 | 32.804 | 52.7381 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.274 | N/A | N/A | 4038852 |  | Primary
4038646 | Barwick | RED | 33 | 11 | 23 | 11.5 | 23 | 12.6638 | 2.6634 | -3.221 | 0 | 7.993 | 13.1216 | 21.9232 | 32.804 | 66.831 | 7 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 23.9399 | 13.3594 | >1.000 | 23.9399 | RED | No | None | N/A | N/A | -0.804 | N/A | N/A | 4038860 |  | Primary
4038682 | Ninelands Lane | RED | 33 | 11 | 23 | 11.5 | 23 | 13.3931 | 1.5006 | -3.221 | -2.379 | 7.8184 | 13.1216 | 19.7928 | 32.804 | 60.3366 | 6 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 18.4035 | 1.5006 | >1.000 | 18.4035 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038860 |  | Primary
4038642 | Oakwood Lane | RED | 33 | 11 | 18.75 | 15 | 23 | 9.9753 | 2.0031 | -3.221 | -0.842 | 10.1311 | 13.1216 | 25.5459 | 32.804 | 77.8744 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 25.6898 | 20.2711 | >1.000 | 25.6898 | RED | No | None | N/A | N/A | -0.482 | N/A | N/A | 4038860 |  | Primary
4038640 | Roman Avenue | RED | 33 | 11 | 18.75 | 15 | 23 | 12.3189 | 2.5266 | -3.221 | 0 | 9.892 | 13.1216 | 24.7313 | 32.804 | 75.3912 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.3755 | 21.2766 | >1.000 | 26.3755 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038860 |  | Primary
4038644 | Seacroft | RED | 33 | 11 | 23 | 11.5 | 23 | 11.0494 | 2.373 | -3.221 | 0 | 8.0261 | 13.1216 | 22.026 | 32.804 | 67.1443 | 6 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.2953 | 13.369 | >1.000 | 27.2953 | RED | No | None | N/A | N/A | -0.504 | N/A | N/A | 4038860 |  | Primary
4038645 | Sledmere Garth | RED | 33 | 11 | 18.75 | 15 | 23 | 5.2067 | 0.73998 | -3.221 | 0 | 10.5451 | 13.1216 | 27.0202 | 32.804 | 82.3685 | 5 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 26.8139 | 19.374 | >1.000 | 26.8139 | RED | No | None | N/A | N/A | -0.116 | N/A | N/A | 4038860 |  | Primary
4038606 | New Droppingwell Road | AMBER | 33 | 11 | 30 | 15 | 25.4 | 9.6571 | 2.057 | -45.736 | -0.5 | 9.3763 | 25 | 24.5997 | 62.5 | 39.3595 | 6 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 20.6522 | 20.6522 | >52.632 | 20.6522 | AMBER | No | None | N/A | N/A | -0.276 | N/A | N/A | 7097005 |  | Primary
4038566 | Tinsley Park Road | AMBER | 33 | 11 | 24 | 12 | 24 | 17.0853 | 4.1947 | -45.736 | -0.105 | 10.393 | 13.1216 | 27.9624 | 32.804 | 85.2407 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 43.2187 | 2.0467 | >52.632 | 43.2187 | AMBER | No | None | N/A | N/A | -2.148 | N/A | N/A | 7097005 |  | Primary
4038829 | Waverley Business Park | AMBER | 33 | 11 | 40 | 20 | 38 | 8.51 | 1.8372 | -45.736 | -0.131 | 8.5612 | 19.9999 | 22.4274 | 49.9998 | 44.855 | 4 | 100% | 40 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 37.34 | 37.34 | >52.632 | 37.34 | AMBER | No | None | N/A | N/A | -1.053 | N/A | N/A | 7097005 |  | Primary
7208979 | Shepcote Tinsley | AMBER | 33 | 11 | 30 | 15 | 30 | 1.7531 | 0.098664 | -45.736 | 0 | 8.6222 | 19.9973 | 21.9484 | 49.9933 | 43.9027 | 10 | 100% | 30 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 43.818 | 30.0987 | >52.632 | 43.818 | AMBER | No | None | N/A | N/A | N/A | N/A | N/A | 7097005 |  | Primary
4038744 | Belmont Covert | RED | 33 | 11 | 24 | 12 | 8 | 3.6206 | 0.18746 | -60.512 | 0 | 3.4563 | 13.1216 | 7.7558 | 32.804 | 26.3406 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.18746 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038885 |  | Primary
4038743 | Binbrook | RED | 33 | 11 | 7.5 | 7.5 | 7.5 | 1.8496 | 0.10853 | -60.512 | -0.451 | 3.7199 | 13.1216 | 8.6061 | 32.804 | 28.3493 | 7 | 100% | 7.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.137 | N/A | N/A | 4038885 |  | Primary
4038729 | Caistor | RED | 33 | 11 | 12 | 12 | 9.5 | 6.4 | 1.7266 | -60.512 | -1.268 | 4.202 | 19.9448 | 10.0949 | 49.8621 | 21.0684 | 11 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.526 | N/A | N/A | 4038885 |  | Primary
4038747 | Grainthorpe | RED | 33 | 11 | 7.5 | 7.5 | 7.5 | 5.2038 | 1.2826 | -60.512 | -0.191 | 3.2795 | 13.1216 | 7.6567 | 32.804 | 24.9934 | 1 | TBC | 0 | OUT OF TAPS | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038885 |  | Primary
4038811 | Keddington Road | RED | 33 | 11 | 25 | 12.5 | 12 | 6.79 | -3.8874 | -60.512 | -8.132 | 10.3228 | 24.9835 | 18.2844 | 62.4588 | 41.3186 | 9 | 100% | 12.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038885 |  | Primary
4038746 | Louth | RED | 33 | 11 | 23 | 11.5 | 23 | 19.8664 | 3.8471 | -60.512 | -0.579 | 10.8399 | 13.1216 | 24.3224 | 32.804 | 82.6109 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.071 | N/A | N/A | 4038885 |  | Primary
4038745 | North Thoresby | RED | 33 | 11 | 24 | 12 | 8 | 4.2112 | 0.62159 | -60.512 | 0 | 5.4289 | 13.1216 | 13.2682 | 32.804 | 41.3734 | 10 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.208 | N/A | N/A | 4038885 |  | Primary
4038748 | South Reston | RED | 33 | 11 | 24 | 12 | 8 | 3.748 | -2.6738 | -60.512 | -6.032 | 3.0907 | 13.1216 | 7.0736 | 32.804 | 23.5547 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | VOLTAGE OUT OF STATUTORY LIMIT | 0.19 | 0 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.605 | N/A | N/A | 4038885 |  | Primary
4038820 | Walesby | RED | 33 | 11 | 24 | 12 | 8 | 6.06 | 0.80905 | -60.512 | -0.28 | 3.8617 | 19.9973 | 9.0466 | 49.9933 | 19.311 | 6 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | SOME VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | -0.216 | N/A | N/A | 4038885 |  | Primary
4038734 | BTP | RED | 33 | 11 | 18.75 | 15 | 23 | 15.5727 | 2.8407 | -41.19 | -8.948 | 12.0984 | 13.1216 | 31.5978 | 32.804 | 96.3231 | 6 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 18.9287 | 18.9287 | >1.000 | 18.9287 | RED | No | None | N/A | N/A | -1.511 | N/A | N/A | 4038882 |  | Primary
4038733 | Great Coates | RED | 33 | 11 | 23 | 11.5 | 23 | 18.0139 | 2.3521 | -41.19 | -8.541 | 10.7659 | 13.1216 | 30.2954 | 32.804 | 92.3529 | 7 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 18.756 | 13.8521 | >1.000 | 18.756 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038882 |  | Primary
4038735 | Scartho | RED | 33 | 11 | 18.75 | 15 | 23 | 19.02 | 1.8007 | -41.19 | -1.681 | 7.2277 | 13.1216 | 17.5222 | 32.804 | 55.0822 | 8 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | SOME VOLTAGE CONSTRAINT | 3.0504 | 3.0504 | >1.000 | 3.0504 | RED | No | None | N/A | N/A | -2.547 | N/A | N/A | 4038882 |  | Primary
4038892 | Yarborough Road 33/11kV | RED | 33 | 11 | 24 | 12 | 23 | 13.1116 | 1.253 | -41.19 | -0.967 | 9.8951 | 18.3702 | 28.2021 | 45.9256 | 61.4082 | 8 | 100% | 24 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 19.9774 | 19.9774 | >1.000 | 19.9774 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038882 |  | Primary
4038716 | Alfred Gelder Street | RED | 33 | 11 | 24 | 12 | 24 | 13.7504 | 3.1129 | -1.951 | 0 | 10.3642 | 13.1216 | 27.2789 | 32.804 | 83.1572 | 12 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 28.9064 | 3.1129 | >1.000 | 28.9064 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038874 |  | Primary
4038712 | Clarendon Street | RED | 33 | 11 | 18.75 | 15 | 23 | 15.246 | 5.6185 | -1.951 | -1.263 | 11.7165 | 13.1216 | 30.8482 | 32.804 | 94.0378 | 7 | 100% | 18.75 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 24.7361 | 22.4835 | >1.000 | 24.7361 | RED | No | None | N/A | N/A | -1.885 | N/A | N/A | 4038874 |  | Primary
4038706 | County Road North | RED | 33 | 11 | 23 | 11.5 | 23 | 15.1037 | 3.748 | -1.951 | 0 | 8.4983 | 13.1216 | 23.6622 | 32.804 | 72.1322 | 7 | 50% | 11.5 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 27.3148 | 9.436 | >1.000 | 27.3148 | RED | No | None | N/A | N/A | -5.812 | N/A | N/A | 4038874 |  | Primary
4038705-1 | Hessle Road 1 | RED | 33 | 11 | 23 | 11.5 | 23 | 5.9628 | 1.1938 | -1.951 | 0 | 9.2286 | 13.1216 | 25.2299 | 32.804 | 76.9109 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 25.4605 | 1.1938 | >1.000 | 25.4605 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038874 |  | Primary
4038708 | National Avenue | RED | 33 | 11 | 24 | 12 | 24 | 7.9662 | 1.1544 | -1.951 | -0.179 | 10.2614 | 13.1216 | 26.6217 | 32.804 | 81.1539 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 24.1976 | 1.1544 | >1.000 | 24.1976 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038874 |  | Primary
4038709 | Plangeo | RED | 33 | 11 | 24 | 12 | 24 | 14.0412 | 4.5144 | -1.951 | 0 | 10.6298 | 13.1216 | 29.2295 | 32.804 | 89.1034 | 11 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NO VOLTAGE CONSTRAINT | 30.1787 | 4.3144 | >1.000 | 30.1787 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 4038874 |  | Primary
4038710 | West Docks | RED | 33 | 11 | 23 | 11.5 | 23 | 13.2987 | 2.9175 | -1.951 | -0.509 | 8.564 | 13.1216 | 24.2115 | 32.804 | 73.8066 | 7 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 26.121 | 1.8545 | >1.000 | 26.121 | RED | No | None | N/A | N/A | -1.063 | N/A | N/A | 4038874 |  | Primary
7096989 | Bradford West | RED | NGET | 132 | 240 | 240 | 886 | 372.04 | 138.82 | NGET | -50.123 | 14.0996 | 15.3085 | 35.0434 | 39 | 92.1028 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -1608.116 | N/A | N/A | NGET | 4038841,4038834,4038833,4038842,4038840,4038836,4038839 | GSP
7096969 | Creyke Beck | RED | NGET | 132 | 240 | 240 | 886 | 369.67 | 4.05 | NGET | -633.218 | 22.4363 | 40 | 56.4192 | 100 | 56.4192 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >1.053 | RED | No | None | N/A | N/A | -2101.312 | N/A | N/A | NGET | 4038873,4038878,4038872,4038871,4038874,4038877,4038875 | GSP
7096970 | Drax | RED | NGET | 132 | 240 | 240 | 295 | 53.98 | -10.19 | NGET | -128.962 | 8.3586 | 15.3085 | 22.5918 | 39 | 57.9277 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >26.316 | RED | No | None | N/A | N/A | -1095.193 | N/A | N/A | NGET | 4038886 | GSP
7096999 | Elland | RED | NGET | 132 | 240 | 240 | 659 | 299.1 | 76.11 | NGET | -111.813 | 12.1439 | 40.0209 | 31.8753 | 100.0522 | 31.8587 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >40.227 | >52.632 | RED | No | None | N/A | N/A | -974.01 | N/A | N/A | NGET | 4038846,4038844,4038897,4038862,7558610 | GSP
7097000 | Ferrybridge B | RED | NGET | 132 | 240 | 240 | 864 | 222.94 | 13.38 | NGET | -259.112 | 16.9688 | 20 | 45.5248 | 50 | 91.0495 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -2065.751 | N/A | N/A | NGET | 4038861,4038868,4038869,4038860 | GSP
7096972 | Grimsby West | RED | NGET | 132 | 240 | 240 | 295 | 181.36 | 6.597 | NGET | -164.242 | 11.4629 | 15.3085 | 29.2684 | 39 | 75.0472 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -1575.04 | N/A | N/A | NGET | 4038881,4038883,4038882,4038884 | GSP
7096973 | Keadby | RED | NGET | 132 | 240 | 240 | 590 | 278.08 | 12.833 | NGET | -546.38 | 29.328 | 29.328 | 80 | 80 | 100 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.19 | RED | No | None | N/A | N/A | -1834.839 | N/A | N/A | NGET | 4038891,4038889,4038887,4038885,4038888 | GSP
7096974 | Kirkstall B | RED | NGET | 132 | 240 | 240 | 590 | 226.9 | 77.29 | NGET | -26.059 | 8.71 | 15.31 | 25.6 | 39 | 65.641 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | NOT USED | 191.12 | >1.000 | >52.632 | GREEN | No | None | N/A | N/A | -126.17 | N/A | N/A | NGET | 7096967,7097003,4038894 | GSP
4038880 | Saltend 132/33kV | RED | 132 | 33 | 45 | 22.5 | 50.8 | 8.2408 | -6.1468 | -92.129 | -16.264 | 6.3082 | 24.966 | 18.3725 | 62.4151 | 29.4361 | 0 | 100% | 22.5 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >22.421 | 0 | RED | No | None | N/A | N/A | -122.895 | N/A | N/A | 7096978 | 4038815,4038809 | BSP
7096981 | Skelton Grange | RED | NGET | 132 | 240 | 240 | 915 | 504.19 | 174.52 | NGET | -98.293 | 18.2324 | 39.999 | 48.0359 | 99.9975 | 48.0371 | Not Used | 100% | 240 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >52.632 | RED | No | None | N/A | N/A | -1216.764 | N/A | N/A | NGET | 4038837,4038859,4038858,4038900,4038838,4038845,7240601,4038866,4000000 | GSP
7096988-1 | West Melton / Thorpe Marsh | RED | NGET | 132 | 120 | 120 | 696 | 381.4 | -130.31 | NGET | -267.182 | 15.31 | 15.31 | 39 | 39 | 100 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.19 | RED | No | None | N/A | N/A | -828.114 | N/A | N/A | NGET | 4038899,4038847,4038848,4038851,4038853,4038854,4038898 | GSP
7096988-3 | West Melton Section 3 | RED | NGET | 132 | 180 | 180 | 418 | 212.2 | 112.39 | NGET | -85.715 | 40 | 40 | 100 | 100 | 100 | Not Used | 100% | 180 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >1.000 | >0.19 | RED | No | None | N/A | N/A | -825.231 | N/A | N/A | NGET | 4038849,4038850,4038896,4038865,4038852 | GSP
7096998 | Camblesforth | RED | NGET | 66 | 180 | 180 | 216 | 30.7577 | -100.32 | NGET | -139.391 | 16.7671 | 25.001 | 45.583 | 62.5025 | 72.9298 | Not Used | 100% | 180 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | 50 | NOT USED | No | None | N/A | N/A | -340.866 | N/A | N/A | NGET | 4038757,4038602,4038761,4038828,4038759 | BSP
4038692-66 | Ferrybridge A | RED | NGET | 66 | 180 | 180 | 198 | 85.5 | 28.15 | NGET | -23.421 | 16.0605 | 21.8693 | 44.1555 | 54.6733 | 80.7625 | Not Used | 100% | 180 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | 50 | NOT USED | No | None | N/A | N/A | -438.019 | N/A | N/A | NGET | 4038797,4038692-11,7501276,4038816,4038684,4038686,4038581,4038689 | BSP
4038899 | Doncaster B/Thorpe Marsh | RED | 132 | 66 | 120 | 50 | 223 | 136.3406 | -36.8709 | -267.182 | -132.742 | 17.3589 | 21.8693 | 45.1338 | 54.6733 | 82.5518 | 0 | 100% | 120 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -392.594 | N/A | N/A | 7096988-1 | 4038598,4038696,4038623,4038591,4038586,4038587,4038585,4038593,4038596,4038597,4038595,4038599,4038600,4038604,4038801,4038594 | BSP
4038847 | Attercliffe | RED | 132 | 33 | 72 | 30 | 69 | 44.9105 | 4.22 | -267.182 | -21.469 | 12.3641 | 17.4955 | 33.0301 | 43.7387 | 75.517 | 0 | TBC | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -47.447 | N/A | N/A | 7096988-1 | 4038567,4038610,4038573,4038565,4038562 | BSP
4038848 | Blackburn Meadows B | RED | 33 | 11 | 60 | 30 | 78 | 31.1 | -20.9465 | -49.692 | -49.692 | 14.0569 | 17.5 | 37.524 | 43.75 | 85.769 | 0 | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -1.758 | N/A | N/A | 4038848 | 4038570,4038607,4038609,4038569 | BSP
4038851 | Doncaster Central | RED | 132 | 33 | 90 | 45 | 117 | 28.6439 | 9.0377 | -267.182 | 0 | 10.1595 | 17.4955 | 27.1562 | 43.7387 | 62.0875 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -64.21 | N/A | N/A | 7096988-1 | 4038589,4038588,4038590,7256105,4038592 | BSP
4038849 | Barugh 132/66kV | RED | 132 | 66 | 75 | 37.5 | 98 | 65.06 | 8.2414 | -85.715 | -12.053 | 6.3055 | 13.1216 | 17.6577 | 32.804 | 53.828 | 0 | TBC | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -44.137 | N/A | N/A | 7096988-3 | 4038575,4038788,4038792-1,4038531,4038576,4038574 | BSP
4038850 | Hunningley | RED | 132 | 33 | 90 | 45 | 117 | 42.515 | 6.9684 | -85.715 | -0.577 | 9.7654 | 17.4955 | 26.945 | 43.7387 | 61.6046 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -30.18 | N/A | N/A | 7096988-3 | 4038580,4038578,4038579 | BSP
4038896 | Hunshelf | RED | 132 | 66 | 60 | 30 | 156 | 73.6771 | 22.7375 | -85.715 | -9.539 | 9.0065 | 15.3085 | 20.2386 | 39 | 58.8331 | 0 | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -78.842 | N/A | N/A | 7096988-3 | 4038792-2,4038534,4038533,4038535 | BSP
4038865 | Wakefield Monckton Road | RED | 132 | 33 | 90 | 45 | 117 | 48.93 | 15.3773 | -85.715 | -20.437 | 9.7113 | 17.4955 | 26.7489 | 43.7387 | 61.1562 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.116 | N/A | N/A | 7096988-3 | 4038676,4038674,4038678,4038677 | BSP
4038852 | West Melton | RED | 132 | 66 | 108 | 45 | 141 | 132.6955 | 29.1968 | -85.715 | -43.109 | 9.8821 | 13.1216 | 28.448 | 32.804 | 86.7211 | 0 | TBC | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -88.242 | N/A | N/A | 7096988-3 | 4038808,4038800,4038558,4038582,4038583,7393498,4038552,4038584,4038577 | BSP
7096955 | Templeborough 275/33kV | RED | NGET | 33 | 75 | 75 | 98 | 27.459 | 1.23 | NGET | 0 | 12.4757 | 17.4955 | 33.9662 | 43.7387 | 77.6571 | Not Used | 100% | 75 | NO VOLTAGE CONSTRAINT | High Physical Constraint | RED | NOT USED | NOT USED | 2.02 | >1.000 | 50 | NOT USED | No | None | N/A | N/A | -74.21 | N/A | N/A | NGET | 4038611 | BSP
4038841 | Bingley 132/33kV | RED | 132 | 33 | 90 | 45 | 117 | 52.9149 | 14.4476 | -50.123 | -2.024 | 10.6653 | 17.4955 | 29.805 | 43.7387 | 68.1433 | 0 | TBC | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 14.2476 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 7096989 | 4038502,4038796,4038503,4038497-1,4038505,4038499 | BSP
4038834 | Bradford | RED | 132 | 33 | 90 | 45 | 117 | 80.7811 | 12.87 | -50.123 | -1.601 | 13.1685 | 17.4955 | 37.269 | 43.7387 | 85.2083 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 102.67 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.2 | N/A | N/A | 7096989 | 4038470,4038463,4038471,4038477,4038468,4038473,4038472,4038462 | BSP
4038833 | Girlington | RED | 132 | 33 | 90 | 60 | 117 | 51.44 | 16.8765 | -50.123 | -13.014 | 12.01 | 17.5 | 33.6531 | 43.75 | 76.9213 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 61.0865 | >1.000 | 0 | RED | No | None | N/A | N/A | -45.79 | N/A | N/A | 7096989 | 4038461,4038456,4038458,4038467,4038459,4038457 | BSP
4038842 | Holmfield | RED | 132 | 33 | 90 | 45 | 117 | 73.0966 | -2.7725 | -50.123 | -21.213 | 12.3225 | 17.5 | 33.7305 | 43.75 | 77.0983 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 87.2275 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096989 | 4038501,4038507,4038508,4038514,4038455 | BSP
4038836 | Menston | RED | 132 | 33 | 90 | 45 | 117 | 53.231 | 9.2967 | -50.123 | -8.425 | 10.6776 | 17.4955 | 28.8199 | 43.7387 | 65.8913 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 25.9537 | >1.000 | 0 | RED | No | None | N/A | N/A | -73.343 | N/A | N/A | 7096989 | 4038488,4038475,4038478,4038464,4038483,4038823 | BSP
4038839 | Silsden | RED | 132 | 33 | 54 | 22.5 | 108 | 88.1206 | 17.1529 | -50.123 | -3.783 | 13.277 | 13.1216 | 38.0842 | 32.804 | 116.0963 | 0 | 100% | 54 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 68.4489 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.704 | N/A | N/A | 7096989 | 4038489,4038498,4038500,4038493,4038496,4038504,4038491,4038490,7096982,4038497-2 | BSP
4038873 | Beverley 132/33kV | RED | 132 | 33 | 90 | 45 | 103.5 | 81.2096 | -16.8617 | -633.218 | -72.742 | 15.29 | 17.4955 | 42.31 | 43.7387 | 96.7337 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -279.187 | N/A | N/A | 7096969 | 4038707,4038711,4038821,4038701,4038767,4038702,4038703 | BSP
4038878 | Bransholme | RED | 132 | 33 | 90 | 45 | 117 | 44.9292 | 14.3723 | -633.218 | -56.55 | 13.4378 | 17.4955 | 36.7897 | 43.7387 | 84.1125 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -135.526 | N/A | N/A | 7096969 | 4038720,4038718,4038715,4038714 | BSP
4038872 | Driffield/Beverley Group | RED | 132 | 66 | 60 | 30 | 147 | 101.0346 | -5.7028 | -633.218 | -189.461 | 13.03 | 13.1216 | 31.15 | 32.804 | 99.3019 | 0 | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | Yes | None | N/A | N/A | -601.307 | N/A | N/A | 7096969 | 4038763,4038723,4038725,4038700,4038790,4038822,4038713,4038699,4038724,4038760,4038826 | BSP
4038871 | Hull West | RED | 132 | 33 | 108 | 45 | 117 | 49.0817 | 12.5212 | -633.218 | -22.127 | 13.0413 | 17.4955 | 36.1295 | 43.7387 | 82.6031 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 33.8022 | >1.000 | 0 | RED | No | None | N/A | N/A | -86.719 | N/A | N/A | 7096969 | 4038704,4038698,4038766-1,4038697,4038705-2 | BSP
4038874 | Hull South | RED | 132 | 33 | 108 | 45 | 117 | 73.5301 | 25.6289 | -633.218 | -1.951 | 12.9496 | 17.4955 | 37.4049 | 43.7387 | 85.5192 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 124.6689 | >1.000 | 0 | RED | No | None | N/A | N/A | -8.96 | N/A | N/A | 7096969 | 4038716,4038712,4038706,4038705-1,4038708,4038709,4038710 | BSP
4038886 | Osgodby 3/4 | RED | 132 | 33 | 108 | 45 | 108 | 47.289 | -21.716 | -128.962 | -66.857 | 13.6659 | 17.4955 | 37.4386 | 43.7387 | 85.5962 | 0 | 100% | 108 | NOT USED | High Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -105.52 | N/A | N/A | 7096970 | 4038753,4038752,4038762,4038766-2 | BSP
4038846 | Brighouse 132/33kV | RED | 132 | 33 | 90 | 45 | 117 | 67.37 | 18.4679 | -111.813 | -1.695 | 10.5371 | 17.4955 | 30.8913 | 43.7387 | 70.6269 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 61.4959 | >40.227 | 0 | RED | No | None | N/A | N/A | -46.972 | N/A | N/A | 7096999 | 4038523,4038525,4038528,4038787,4038795,4038474,4038480 | BSP
4038844 | Lindley | RED | 132 | 33 | 90 | 45 | 117 | 66.27 | 16.7927 | -111.813 | -4.619 | 10.258 | 17.4955 | 30.0277 | 43.7387 | 68.6526 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 105.7627 | >40.227 | 0 | RED | No | None | N/A | N/A | -1.03 | N/A | N/A | 7096999 | 4038515,4038522,4038517,4038512,4038516,4038511,4038506 | BSP
4038897 | Sowerby Bridge 132/33kV | RED | 132 | 33 | 90 | 45 | 117 | 65.5107 | 4.7234 | -111.813 | -24.362 | 10.9255 | 13.1216 | 31.3171 | 32.804 | 95.4673 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 40.5294 | >40.227 | 0 | RED | No | None | N/A | N/A | -54.194 | N/A | N/A | 7096999 | 4038513,4038492,4038495,4038793,4038806,4038804 | BSP
4038862 | Thornhill 132kV | RED | 132 | 33 | 90 | 45 | 114 | 86.8484 | 7.1729 | -111.813 | -81.137 | 13.8795 | 21.9918 | 39.183 | 54.9795 | 71.2683 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 52.3579 | >40.227 | 0 | RED | No | None | N/A | N/A | -44.815 | N/A | N/A | 7096999 | 4038655,4038652,4038660,4038529,4038666,4038530,4038799,4038526 | BSP
4038861 | Bramham | RED | 132 | 33 | 90 | 45 | 117 | 63.1307 | 13.7776 | -259.112 | -30.349 | 11.7608 | 17.4955 | 33.0512 | 43.7387 | 75.5653 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -127.821 | N/A | N/A | 7097000 | 4038648,4038635,4038694,4038647,4038814,4038650,4038649 | BSP
4038868 | Featherstone | RED | 132 | 33 | 108 | 45 | 117 | 76.4004 | 26.257 | -259.112 | -28.168 | 13.701 | 17.4955 | 40.1751 | 43.7387 | 91.8525 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 64.374 | >1.000 | 0 | RED | No | None | N/A | N/A | -69.883 | N/A | N/A | 7097000 | 4038683,4038680,4038690,4038681,4038685 | BSP
4038869 | Kirkhaw Lane | RED | 132 | 33 | 90 | 45 | 117 | 51.6142 | -31.2667 | -259.112 | -30.005 | 13.6018 | 17.4955 | 39.6208 | 43.7387 | 90.5853 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 13.0143 | >1.000 | 0 | RED | No | None | N/A | N/A | -45.719 | N/A | N/A | 7097000 | 4038688,7395321,4038693,4038695,4038687 | BSP
4038860 | Whinmoor | RED | 132 | 33 | 108 | 45 | 117 | 64.04 | 17.2953 | -259.112 | -3.221 | 9.814 | 17.4955 | 27.5877 | 43.7387 | 63.0739 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 97.0733 | >1.000 | 0 | RED | No | None | N/A | N/A | -28.222 | N/A | N/A | 7097000 | 4038646,4038682,4038642,4038640,4038644,4038645 | BSP
4038884 | Humberston | RED | 132 | 33 | 90 | 45 | 117 | 30.455 | 5.6041 | -164.242 | -26.895 | 12.5342 | 17.4955 | 34.3691 | 43.7387 | 78.5783 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 92.9961 | >1.000 | 0 | RED | No | None | N/A | N/A | -2.608 | N/A | N/A | 7096972 | 4038738,4038740,4038741 | BSP
4038881 | Immingham | RED | 132 | 33 | 90 | 45 | 117 | 68.0866 | -19.6441 | -164.242 | -91.829 | 19.1601 | 25.001 | 54.4768 | 62.5025 | 87.1594 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | -153.91 | N/A | N/A | 7096972 | 4038782,4038786,4038730,4038731,4038732 | BSP
4038883 | Moss Road | RED | 132 | 33 | 45 | 22.5 | 59 | 36.567 | 12.4124 | -164.242 | -4.328 | 10.0145 | 17.4955 | 27.564 | 43.7387 | 63.0198 | 0 | 100% | 45 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 40.7814 | >1.000 | 0 | RED | No | None | N/A | N/A | -16.631 | N/A | N/A | 7096972 | 4038736,4038737,4038739 | BSP
4038882 | Yarborough Road 132/33kV | RED | 132 | 33 | 90 | 45 | 117 | 57.3 | 7.2364 | -164.242 | -41.19 | 8.6839 | 19.9973 | 21.0518 | 49.9933 | 43.4252 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 33.9154 | >1.000 | 0 | RED | No | None | N/A | N/A | -63.321 | N/A | N/A | 7096972 | 4038734,4038733,4038735,4038892 | BSP
7096996 | Jordanthorpe | RED | NGET | 33 | 100 | 100 | 110 | 55.3636 | 12.31 | NGET | -0.186 | 15.4979 | 17.4955 | 43.3954 | 43.7387 | 99.2152 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >52.632 | 50 | NOT USED | No | None | N/A | N/A | -126.315 | N/A | N/A | NGET | 4038539,4038556,4038547,4038544,4038549 | BSP
4038891 | Blyton | RED | 132 | 33 | 60 | 30 | 78 | 47.6659 | 6.74 | -546.38 | -27.981 | 11.9021 | 13.1216 | 31.943 | 33.4601 | 95.466 | 0 | 100% | 60 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -42.591 | N/A | N/A | 7096973 | 4038776,4038601,4038778,4038605,4038775,4038783,4038777 | BSP
4038889 | Santon | RED | 132 | 33 | 90 | 45 | 117 | 41.5083 | -28.5929 | -546.38 | -60.871 | 14.5077 | 25.001 | 39.4927 | 62.5025 | 63.1858 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -36.291 | N/A | N/A | 7096973 | 4.0388e+34 | BSP
4038887 | Scunthorpe North | RED | 132 | 33 | 108 | 45 | 150 | 96.77 | 3.1405 | -546.38 | -74.211 | 20.7379 | 25.001 | 59.9443 | 62.5025 | 95.907 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -52.125 | N/A | N/A | 7096973 | 4038791,4038768,4038770,4038771 | BSP
4038885 | Wold Newton | RED | 132 | 33 | 90 | 45 | 99 | 47.169 | -17.8484 | -546.38 | -60.512 | 11.1862 | 24.9835 | 27.6076 | 62.4588 | 44.7742 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -8.079 | N/A | N/A | 7096973 | 4038744,4038743,4038729,4038747,4038811,4038746,4038745,4038748,4038820 | BSP
7096967 | Beeston Royds 132/33kV | RED | 132 | 33 | 90 | 45 | 228 | 103.97 | 14.86 | -26.059 | -8.568 | 12.8456 | 25 | 39.1352 | 62.5 | 62.6163 | 0 | 100% | 90 | NOT USED | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 101.6953 | 43.327 | >1.000 | 101.6953 | GREEN | No | None | N/A | N/A | -61.533 | N/A | N/A | 7096974 | 4038661-1,4038654,4038665,4038668,4038658,4038664,4038629,4038661-6 | BSP
7097003 | Kirkstall C 2/5 | RED | 132 | 33 | 90 | 60 | 117 | 74.7629 | 8.2282 | -26.059 | -16.389 | 10.7875 | 15.3085 | 29.1241 | 39 | 74.6773 | 0 | 100% | 90 | NOT USED | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 113.1141 | 96.8022 | >1.000 | 113.1141 | GREEN | No | None | N/A | N/A | -1.426 | N/A | N/A | 7096974 | 4038802,4038628,4038630 | BSP
7096975 | Neepsend | RED | NGET | 33 | 120 | 120 | 144 | 75.4756 | 22.32 | NGET | -3.061 | 14.231 | 17.4955 | 41.4211 | 43.7387 | 94.7014 | Not Used | 100% | 120 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NOT USED | NOT USED | 50 | >52.632 | 50 | NOT USED | No | None | N/A | N/A | -50.449 | N/A | N/A | NGET | 4038550,4038542,4038545,4038537,4038546,4038543,4038540 | BSP
7096976 | Norton Lees | RED | NGET | 33 | 100 | 100 | 110 | 57.6775 | 15.47 | NGET | -0.248 | 16.3895 | 17.4955 | 45.7096 | 43.7387 | 104.5061 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 50 | >52.632 | 50 | NOT USED | No | None | N/A | N/A | N/A | N/A | N/A | NGET | 4038561,4038541,4038559,4038805,4038538 | BSP
7096977 | Pitsmoor 3/4 | RED | NGET | 33 | 100 | 100 | 114 | 46.62 | -18.5 | NGET | -0.256 | 15.9273 | 17.4955 | 45.1876 | 43.7387 | 103.3127 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >21.053 | 50 | NOT USED | No | None | N/A | N/A | -126.421 | N/A | N/A | NGET | 7256106,4038560,4038563,4038555,4038564 | BSP
7096978 | Saltend North | RED | NGET | 132 | 180 | 180 | 216 | 98.56 | -15.69 | NGET | -92.129 | 11.4451 | 15.3085 | 30.0273 | 39 | 76.9931 | Not Used | 100% | 180 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | NOT USED | 0 | >22.421 | >52.632 | RED | No | None | N/A | N/A | -1054.244 | N/A | N/A | NGET | 4038880,4038879 | GSP
4038879 | Hull East 132/33kV | RED | 132 | 33 | 108 | 45 | 117 | 57.2671 | 23.3637 | -92.129 | -75.865 | 12.9235 | 17.4955 | 37.1915 | 43.7387 | 85.0311 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 94.7417 | >22.421 | 0 | RED | No | None | N/A | N/A | -36.622 | N/A | N/A | 7096978 | 4038728,4038721,4038893,4038719,4038807,4038726,4038717,4038727 | BSP
7096980 | Sheffield City | RED | NGET | 33 | 100 | 100 | 114 | 83.63 | 27.87 | NGET | -0.173 | 15.5308 | 17.4955 | 44.3135 | 43.7387 | 101.3143 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 50 | >43.526 | 50 | NOT USED | No | None | N/A | N/A | -2.632 | N/A | N/A | NGET | 4038554,4038551,4038568,4038557,4038553,4038548 | BSP
4038837 | Heckmondwike | RED | 132 | 33 | 90 | 45 | 52 | 48.7419 | 4.15 | -98.293 | -1.446 | 8.9936 | 26.2432 | 24.574 | 65.608 | 37.4558 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 94.15 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 7096981 | 4038484,4038481,4038810,4038651 | BSP
4038859 | Leeds East | RED | 132 | 33 | 90 | 45 | 117 | 62.7826 | 13.517 | -98.293 | -20.697 | 13.7715 | 17.4955 | 40.0736 | 43.7387 | 91.6205 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 85.234 | >1.000 | 0 | RED | No | None | N/A | N/A | -18.283 | N/A | N/A | 7096981 | 4038633-1,4038637,4038638,4038789,4038639,4038643,4038641 | BSP
4038858 | Leeds North | RED | 132 | 33 | 90 | 45 | 117 | 60.18 | 23.45 | -98.293 | -4.358 | 12.5567 | 17.5 | 36.0208 | 43.75 | 82.3332 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 60.819 | >1.000 | 0 | RED | No | None | N/A | N/A | -52.631 | N/A | N/A | 7096981 | 4038633-2,4038632,4038631,4038636,4038627 | BSP
4038900 | Low Road | RED | 132 | 33 | 120 | 50 | 228 | 81.8421 | 11.9968 | -98.293 | -1.039 | 15.7149 | 25 | 45.6097 | 62.5 | 72.9755 | 0 | TBC | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 7.5788 | >1.000 | 0 | RED | No | None | N/A | N/A | -4.418 | N/A | N/A | 7096981 | 7096966,4038670,4038669,4038667,4038671,4038672,4038831,7322111 | BSP
4038838 | Rodley | RED | 132 | 33 | 108 | 45 | 117 | 69.9987 | 18.024 | -98.293 | -0.368 | 9.6797 | 17.4955 | 27.1308 | 43.7387 | 62.0293 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 125.445 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.579 | N/A | N/A | 7096981 | 4038482,4038486,4038653,4038479,4038485 | BSP
4038845 | Saint Andrews Road 132/33kV | RED | 132 | 33 | 108 | 45 | 71 | 61.9848 | 10.3598 | -98.293 | -33.268 | 10.8218 | 17.4955 | 29.3924 | 43.7387 | 67.2 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 117.8538 | >1.000 | 0 | RED | No | None | N/A | N/A | -0.506 | N/A | N/A | 7096981 | 4038520,4038527,4038521,4038524,4038518 | BSP
7240601 | Staygate | RED | 132 | 33 | 120 | 80 | 123 | 76.8896 | 13.3787 | -98.293 | -12.522 | 11.6154 | 25.0185 | 31.5171 | 62.5463 | 50.3901 | 0 | 100% | 120 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 128.4467 | >1.000 | 0 | RED | No | None | N/A | N/A | -4.932 | N/A | N/A | 7096981 | 4038812,4038466,4038465,4038469,4038476,4038460 | BSP
4038866 | Wakefield North | RED | 132 | 33 | 90 | 45 | 104 | 71.62 | 18.81 | -98.293 | -11.964 | 11.3846 | 17.4955 | 32.6802 | 43.7387 | 74.7169 | 0 | 100% | 90 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 82.625 | >1.000 | 0 | RED | No | None | N/A | N/A | -26.185 | N/A | N/A | 7096981 | 4038673,4038785,4038662,4038675,4038679 | BSP
7096994 | Thurcroft | RED | NGET | 66 | 180 | 180 | 216 | 125.4524 | 15.34 | NGET | -171.844 | 15.9863 | 21.8693 | 46.5784 | 54.6733 | 85.194 | Not Used | 100% | 180 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NOT USED | NOT USED | 0 | >1.000 | 50 | NOT USED | No | None | N/A | N/A | -1351.164 | N/A | N/A | NGET | 4038819,4038621,4038619,4038603,4038572,4038622,4038616,4038615,4038617,4038614,4038620 | BSP
7097005 | Wincobank | AMBER | NGET | 33 | 100 | 100 | 130 | 31.7629 | -29.08 | NGET | -45.736 | 16.4339 | 17.4955 | 44.1803 | 44.6 | 99.0589 | Not Used | 100% | 100 | NO VOLTAGE CONSTRAINT | No Physical Constraint | AMBER | NOT USED | NOT USED | 50 | >52.632 | 50 | NOT USED | No | None | N/A | N/A | -3.477 | N/A | N/A | NGET | 4038606,4038566,4038829,7208979 | BSP
4038661-6 | Beeston Royds 6/7 | RED | 33 | 11 | 40 | 20 | 26 | 21.2481 | 5.9984 | -8.568 | -2.231 | 7.2538 | 19.9973 | 21.486 | 49.9933 | 42.9779 | 5 | 100% | 40 | NO VOLTAGE CONSTRAINT | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 41.1302 | 41.1302 | >1.000 | 41.1302 | GREEN | No | None | N/A | N/A | -0.073 | N/A | N/A | 7096967 |  | Primary
4038705-2 | Hessle Road 2 | RED | 33 | 11 | 23 | 11.5 | 23 | 10.6787 | 1.8635 | -22.127 | 0 | 9.2286 | 13.1216 | 25.2299 | 32.804 | 76.9109 | 5 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 26.044 | 1.8635 | >1.000 | 26.044 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038871 |  | Primary
4038792-2 | Elmhirst Lane 2 | RED | 66 | 11 | 24 | 12 | 24 | 11.5604 | 1.516 | -9.539 | 0 | 11.115 | 13.1216 | 28.981 | 32.804 | 88.3459 | 12 | 100% | 12 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0.19 | 0.19 | >1.000 | 0.19 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038896 |  | Primary
4038633-2 | Allerton Hill T2 | RED | 33 | 11 | 18.75 | 15 | 23 | 7.2117 | 0.29599 | -4.358 | 0 | 12.3568 | 13.1216 | 31.549 | 32.804 | 96.1741 | 4 | TBC | 0 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 23.1717 | 0.29599 | >1.000 | 23.1717 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038858 |  | Primary
4038766-2 | Newport 2 | RED | 33 | 11 | 24 | 12 | 18.4 | 5.8807 | -1.1938 | -66.857 | 0 | 4.0864 | 24.9835 | 11.0298 | 62.4588 | 17.6594 | 2 | 100% | 12 | SOME VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038886 |  | Primary
4038888 | Scunthorpe South | RED | 132 | 33 | 108 | 45 | 112 | 27.572 | -16.0644 | -546.38 | -73.962 | 14.7611 | 17.4955 | 39.694 | 43.7387 | 90.7527 | 0 | 100% | 108 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -21.869 | N/A | N/A | 7096973 | 4038772,4038769 | BSP
4038497-2 | Haworth 2 | RED | 33 | 11 | 30 | 15 | 30 | 3.6942 | 1.5688 | -3.783 | -0.091 | 7.5515 | 19.9973 | 18.689 | 49.9933 | 37.7627 | 8 | 100% | 15 | NO VOLTAGE CONSTRAINT | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0 | >1.000 | 0 | RED | No | None | N/A | N/A | N/A | N/A | N/A | 4038839 |  | Primary
7558610 | Halifax 132/33kV | RED | 132 | 33 | 60 | 30 | 72 | 38.6401 | 4.5646 | -111.813 | 0 | 10.4484 | 31.4918 | 28.4902 | 78.7296 | 36.1875 | 0 | TBC | 0 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 3.3546 | >40.227 | 0 | RED | No | None | N/A | N/A | -1.21 | N/A | N/A | 7096999 | 4038510,4038843 | BSP
4038894 | Kirkstall C/Ring Road Horsforth | RED | 132 | 33 | 90 | 60 | 117 | 75.4093 | 23.3045 | -26.059 | -1.102 | 9.3977 | 25.001 | 28.4697 | 62.5025 | 45.5497 | 0 | 100% | 90 | NOT USED | No Physical Constraint | GREEN | NO VOLTAGE CONSTRAINT | 130.5 | 113.2515 | >1.000 | 130.5 | GREEN | No | None | N/A | N/A | -0.053 | N/A | N/A | 7096974 | 4038624,4038656,4038657,4038634,4038625,4038626,4038659 | BSP
7733114 | Mallard Way | RED | 132 | 33 | 144 | 60 | 144 | 36.097 | 7.66 | -267.182 | -52.632 | 12.852 | 31.5 | 34 | 78.8 | 43.1472 | 0 | 100% | 144 | NOT USED | No Physical Constraint | RED | NO VOLTAGE CONSTRAINT | 0 | 0.19 | >1.000 | 0 | RED | No | None | N/A | N/A | -28.947 | N/A | N/A | 7096988-1 |  | BSP

## Northeast Demand
Substation ID | Substation Name | Nominal Voltage | Transformer Capacity |  | Firm Capacity | Demand |  | Demand Heat Map |  | Substation Class
Downstream
|  | (kV) | OFAF (MVA) | ONAN (MVA) | Load (MVA) | Maximum (MVA) | Minimum (MVA) | Accepted Demand (Diversified MVA) | Demand Classification | GSP, BSP or Primary
9832 | Foss Islands | 11 | 30 | 15 | 36 | 27.6261 | 4.0883 | 1.58 | GREEN | Primary
9891-11 | Harrogate 132/11kV | 11 | 30 | 15 | 36 | 32.243 | 4.35 | 2.491 | AMBER | BSP
9901 | Oatlands | 11 | 18.75 | 15 | 22.9 | 9.7962 | 1.2483 | 2.011 | GREEN | Primary
9903 | Starbeck | 11 | 18.75 | 15 | 22.9 | 20.1596 | 3.5244 | 3.53 | RED | Primary
7490443 | Barden Friar | 20 | 7.5 | 7.5 | 5 | 0.9375 | 0.157 | 0 | GREEN | Primary
9877 | Bedale | 11 | 24 | 12 | 22 | 17.55 | 3.7485 | 0.775 | GREEN | Primary
9878 | Catterick Camp | 11 | 18.75 | 15 | 24 | 16.8154 | 1.1702 | 0 | GREEN | Primary
9881 | Northallerton | 11 | 18.75 | 15 | 24 | 17.7604 | 3.1038 | 2.749 | GREEN | Primary
2826869 | Romanby | 11 | 10.1 | 10.1 | 8 | 6.0633 | 0.46308 | 0 | AMBER | Primary
9882-2 | Richmond T2 | 11 | 24 | 12 | 24 | 3.5 | 0.090829 | 1.25 | GREEN | Primary
9883 | Thirsk | 11 | 14 | 10 | 14 | 13.1114 | 0.75517 | 0.656 | AMBER | Primary
9884 | Wensleydale | 11 | 14 | 10 | 19 | 10.5021 | 1.3942 | 0 | GREEN | Primary
9845 | Kirbymoorside | 11 | 24 | 12 | 24 | 9.86 | 1.3911 | 0 | GREEN | Primary
9846 | Malton | 11 | 32 | 16 | 32 | 23.9172 | 3.6676 | 1.68 | GREEN | Primary
9849 | Sheriff Hutton | 11 | 18.75 | 15 | 24 | 11.6194 | 0.23029 | 0 | GREEN | Primary
9865 | Thornton Dale | 11 | 24 | 12 | 19.5 | 11.6409 | 1.1473 | 0.708 | GREEN | Primary
2522850 | Yedingham | 11 | 24 | 12 | 8 | 2.8839 | 0.68714 | 0.4 | GREEN | Primary
9841 | Campleshon Road | 11 | 18.75 | 15 | 24 | 16.5051 | 2.0673 | 1.804 | GREEN | Primary
2524256 | Elvington | 11 | 24 | 12 | 20 | 12.23 | 2.7935 | 0.75 | GREEN | Primary
9843 | Haxby Road T2 T3 | 11 | 15 | 11.25 | 14 | 11.2 | 1.5077 | 1 | AMBER | Primary
9844 | Huntington New Lane | 11 | 24 | 12 | 24 | 17.7512 | 5.1399 | 2 | GREEN | Primary
9838-11 | Melrosegate 33/11kV | 11 | 30 | 15 | 32 | 27.5772 | 0.96804 | 2.0116 | GREEN | Primary
9847 | Rawcliffe Lane | 11 | 18.75 | 15 | 24 | 20.111 | 3.7379 | 1 | GREEN | Primary
9851 | York University | 11 | 24 | 12 | 24 | 13.2087 | 1.5101 | 0.85 | GREEN | Primary
9861 | Eastfield | 11 | 32 | 16 | 30.3 | 19.1214 | 4.7938 | 0 | GREEN | Primary
9862 | Newby | 11 | 24 | 12 | 24 | 11.9458 | 1.7279 | 0.3 | GREEN | Primary
9863 | North Street | 11 | 24 | 12 | 24 | 11.3235 | 1.6664 | 0 | GREEN | Primary
3363742 | Ravenscar | 11 | 10 | 10 | 8 | 1.7 | 0.22905 | 0 | GREEN | Primary
9864 | Scarborough 33/11kV | 11 | 32 | 16 | 32 | 18.82 | 5.325 | 3.65 | GREEN | Primary
9866-1 | Whitby T1 | 11 | 24 | 12 | 19.1 | 4.11 | 0.083138 | 0 | GREEN | Primary
9867-1 | Whitby West T1 | 11 | 24 | 12 | 24 | 4.75 | 0.069914 | 0 | GREEN | Primary
9898 | Boroughbridge | 11 | 15 | 7.5 | 15 | 9.9331 | 1.36 | 0 | GREEN | Primary
2822141 | Roecliffe Industrial | 11 | 24 | 12 | 15 | 9.9331 | 1.35 | 1.84 | GREEN | Primary
9899 | Coneythorpe | 11 | 24 | 12 | 22 | 12.5169 | 1.3746 | 4.094 | GREEN | Primary
7129903 | Darley | 11 | 10 | 10 | 8 | 4.1773 | 0 | 0 | GREEN | Primary
9902 | Ripon | 11 | 24 | 12 | 24 | 23.3692 | 5.0299 | 0.688 | RED | Primary
9897-11 | Wormald Green 132/11kV | 11 | 30 | 15 | 36 | 8.41 | 1.278 | 0 | GREEN | BSP
9893-11 | Husthwaite 33/11kV | 11 | 15 | 7.5 | 15 | 10.5112 | 0.49883 | 0 | GREEN | Primary
2530198 | Sessay Bridge | 11 | 24 | 12 | 12 | 9.7469 | 2.2 | 0.2 | GREEN | Primary
2541519 | Sowerby | 11 | 24 | 12 | 12 | 9.7469 | 0.22 | 1.863 | AMBER | Primary
9760 | Acklam | 11 | 24 | 12 | 22.8 | 17.5401 | 5.6854 | 0 | GREEN | Primary
9785-33-11 | Bowesfield 33/11kV | 11 | 32 | 16 | 32 | 13.1477 | 2.253 | 2.9316 | GREEN | Primary
9768 | Millbank Lane | 11 | 18.75 | 15 | 22.8 | 18.078 | 2.9982 | 0.25 | GREEN | Primary
9771 | Rudby | 11 | 15 | 7.5 | 8.38 | 4.6524 | 0.84793 | 0.5 | GREEN | Primary
9774 | Stokesley | 11 | 24 | 12 | 13.11 | 7.4555 | 0.20805 | 0.27 | GREEN | Primary
9796 | Urlay Nook | 11 | 24 | 12 | 48 | 17.8535 | 0.70159 | 0 | GREEN | Primary
9803 | Belmont | 11 | 32 | 16 | 32 | 22.2016 | 4.2635 | 2.193 | GREEN | Primary
9805 | Durham East | 11 | 18.75 | 12 | 22.5 | 18.9093 | 3.8938 | 5.36 | RED | Primary
9743 | High Flatts | 11 | 18.75 | 15 | 24 | 16.0183 | 3.9202 | 0.288 | GREEN | Primary
9810-20 | Potter House T1 T3 | 20 | 25 | 20.5 | 28 | 15.9665 | 1.7521 | 0 | GREEN | Primary
9804 | Brancepeth | 20 | 40 | 20 | 28 | 14.04 | 0.82927 | 0.284 | GREEN | Primary
9807 | Fishburn | 20 | 25 | 20 | 28 | 17.4162 | 0.85989 | 0.75 | GREEN | Primary
9808 | Low Spennymoor | 11 | 24 | 12 | 24 | 0 | 1.3954 | 0 | GREEN | Primary
9809 | Meadowfield | 11 | 24 | 12 | 24 | 12.8797 | 0.34315 | 0 | GREEN | Primary
9826 | Skerneside | 20 | 40 | 20 | 34 | 19.8652 | 4.6376 | 0.5 | GREEN | Primary
9811-20 | Spennymoor 66/20kV | 20 | 44 | 22 | 44 | 16.7797 | 3.1377 | 21.447 | GREEN | Primary
9783 | Amberton Road | 11 | 40 | 20 | 40 | 23.2551 | 6.1849 | 10.925 | GREEN | Primary
9786 | Brenda Trading | 11 | 32 | 16 | 29.4 | 22.5843 | 0.15824 | 4.03 | GREEN | Primary
9787-20 | Hartmoor 66/20kV | 20 | 25 | 18.75 | 28 | 22.3607 | 0.8653 | 0 | GREEN | Primary
2569052 | Peterlee West | 11 | 32 | 16 | 32 | 10.6192 | 0.18879 | 0 | GREEN | Primary
2541255 | Wynyard | 11 | 40 | 20 | 40 | 38.2 | 0.19364 | 5.553 | RED | Primary
9806 | Eastgate Cement | 20 | 25 | 20 | 26 | 9.7628 | 0.14023 | 0 | GREEN | Primary
9821 | Fylands Bridge | 11 | 18.75 | 15 | 25.2 | 20.3149 | 3.1396 | 0 | GREEN | Primary
9822 | Harmire Bridge | 20 | 40 | 20 | 28 | 13.6235 | 2.7074 | 0 | GREEN | Primary
9812-20 | Toronto 66/20kV | 20 | 40 | 20 | 40 | 16.0611 | 2.9298 | 0.222 | GREEN | Primary
9741 | Hawthorn Pit | 20 | 25 | 20 | 28 | 20.93 | 40 | 4.95 | GREEN | Primary
9745 | Houghton | 11 | 24 | 12 | 24 | 16.54 | 1.6991 | 1.6 | GREEN | Primary
9746 | Peterlee Industrial | 11 | 24 | 12 | 20 | 8.43 | 0.11238 | 0 | GREEN | Primary
9747 | Shotton | 11 | 18.75 | 15 | 24.6 | 14.3729 | 4.3257 | 0 | GREEN | Primary
9748 | Stoney Cut | 20 | 25 | 18.75 | 31.9 | 17.0575 | 1.1262 | 1.579 | GREEN | Primary
9726 | Tunstall | 11 | 25 | 18.75 | 30.5 | 19.2565 | 5.0299 | 2.25 | GREEN | Primary
9721 | Mount Road | 11 | 24 | 12 | 24 | 20.84 | 3.5645 | 0 | GREEN | Primary
9717-11 | Offerton 33/11kV | 11 | 32 | 16 | 32 | 17.61 | 3.7577 | 0.975 | GREEN | Primary
9724 | Pallion Trading | 11 | 24 | 12 | 24 | 18.072 | 3.3748 | 2 | GREEN | Primary
9842 | Gale Lane | 11 | 24 | 12 | 24 | 9.17 | 0.9245 | 0.5 | GREEN | Primary
2537397 | Moor Monkton Pumps | 11 | 24 | 12 | 8 | 5.9444 | 1.6819 | 1.36 | AMBER | Primary
9848 | Severus Hill | 11 | 24 | 12 | 24 | 12.71 | 2.1026 | 0.5 | GREEN | Primary
9850 | Skeldergate | 11 | 32 | 16 | 32 | 14.5104 | 2.3279 | 17.036 | AMBER | Primary
9879 | Cowton | 11 | 7.5 | 7.5 | 7.5 | 1.4185 | 0.28992 | 0 | GREEN | Primary
9927-11 | Darlington 33/11kV | 11 | 18.75 | 15 | 24 | 15.21 | 3.3634 | 0.438 | GREEN | Primary
9928-11 | Darlington Central 33/11kV | 11 | 32 | 16 | 32 | 9.6 | 1.1432 | 10.54 | GREEN | Primary
9818 | Darlington East | 11 | 24 | 12 | 24 | 17.1191 | 1.7085 | 0.4 | GREEN | Primary
9646 | Ashington | 11 | 18.75 | 15 | 24 | 17.2504 | 1.5171 | 0 | GREEN | Primary
9607 | Benton Square | 11 | 18.75 | 15 | 24 | 17.6374 | 2.941 | 7.974 | RED | Primary
9610-1 | Cramlington T1 T3 | 11 | 18.75 | 15 | 24 | 11.7211 | 3.2823 | 0.35 | GREEN | Primary
9628-1 | Fawdon T1 | 20 | 25 | 18.75 | 25 | 19.8601 | 1.8 | 1.917 | GREEN | Primary
9611 | Seaton Burn T1 | 20 | 25 | 18.75 | 25 | 19.8601 | 1.8 | 0 | GREEN | Primary
9649 | Maddison Street | 11 | 24 | 12 | 24 | 16.7691 | 2.5556 | 0.375 | GREEN | Primary
9650 | Morpeth | 20 | 30 | 15 | 28 | 16.86 | 0.94173 | 1.028 | GREEN | Primary
9653 | Reservoir | 20 | 30 | 15 | 30 | 19.1831 | 3.4502 | 2.065 | GREEN | Primary
7189886 | Seghill | 11 | 32 | 16 | 32 | 10.26 | 4.1573 | 0.909 | GREEN | Primary
9655 | Wansbeck | 11 | 36 | 18 | 32 | 0.31049 | 0.15297 | 4 | GREEN | Primary
2771500 | West Hartford | 11 | 24 | 12 | 16 | 4.62 | 0.22988 | 0 | GREEN | Primary
9662 | Denwick | 20 | 25 | 20 | 30 | 22.5222 | 1.9852 | 1.288 | GREEN | Primary
9645-20 | Linton 66/20kV | 20 | 24 | 12 | 28 | 10.188 | 1.1213 | 0 | GREEN | Primary
9648 | Lynemouth | 20 | 37.5 | 30 | 38 | 2.3 | 0.01 | 0.9 | GREEN | Primary
9663 | Warkworth | 20 | 25 | 18.75 | 25 | 17.22 | 2.3697 | 6.631 | AMBER | Primary
9629 | Fossway 33/11kV | 11 | 24 | 12 | 24 | 16.1345 | 3.8429 | 2 | GREEN | Primary
9623-11 | Gosforth 33/11kV | 11 | 32 | 16 | 32 | 18.06 | 6.5541 | 2.355 | GREEN | Primary
9614 | Killingworth | 11 | 24 | 12 | 24 | 18.6058 | 6.72 | 0.268 | GREEN | Primary
9631 | Longbenton | 11 | 18.75 | 15 | 24 | 17.3167 | 3.8442 | 0 | GREEN | Primary
9612 | Flatworth Central | 11 | 32 | 16 | 32 | 16.751 | 2.1513 | 8.945 | RED | Primary
9613 | Howdon | 11 | 18.75 | 15 | 24 | 7.5448 | 1.5917 | 0 | RED | Primary
9617 | Willington | 11 | 18.75 | 15 | 24 | 12.8499 | 2.983 | 2.123 | RED | Primary
9608 | Billy Mill | 11 | 18.75 | 15 | 24 | 17.1105 | 4.0964 | 0.5 | GREEN | Primary
9615 | Monkseaton | 11 | 18.75 | 15 | 24 | 17.1186 | 4.2271 | 1.5 | GREEN | Primary
9616 | Tynemouth Central | 11 | 18.75 | 15 | 24 | 15.7555 | 3.9816 | 0 | GREEN | Primary
9693 | Garwood Street | 11 | 32 | 16 | 32 | 17.5762 | 4.6724 | 0.275 | GREEN | Primary
9697 | Jarrow | 11 | 18.75 | 15 | 24 | 6.8014 | 0.11577 | 0 | GREEN | Primary
9698 | Simonside | 11 | 24 | 12 | 24 | 13.1803 | 2.4441 | 1.555 | GREEN | Primary
9701 | Westoe | 11 | 24 | 12 | 24 | 10.816 | 2.479 | 0.35 | GREEN | Primary
9739-20 | Annfield 66/20kV | 20 | 25 | 18.75 | 28 | 21.0004 | 1.5347 | 0 | GREEN | Primary
2707936 | Consett | 20 | 40 | 20 | 40 | 22.9647 | 0.41464 | 1.6816 | GREEN | Primary
9749 | Tanfield | 11 | 32 | 16 | 32 | 13.41 | 2.2822 | 0.8 | GREEN | Primary
2841083 | Newburn Haugh | 11 | 30 | 22.5 | 38.1 | 6.6068 | 1.3434 | 1.343 | GREEN | BSP
9621-11 | Blucher 33/11kV | 11 | 24 | 12 | 24 | 14.8805 | 3.7742 | 0.6362 | GREEN | Primary
9630 | Kenton | 11 | 24 | 12 | 24 | 15.85 | 5.8361 | 1.5 | GREEN | Primary
2805930 | Newcastle Airport | 11 | 24 | 12 | 24 | 12.0024 | 5.8426 | 5.8 | GREEN | Primary
9636 | Westerhope | 11 | 18.75 | 15 | 24 | 11.6893 | 2.4094 | 0.712 | GREEN | Primary
9626 | Corporation Street | 11 | 18.75 | 15 | 24 | 15.2 | 3.2445 | 0 | GREEN | Primary
9627 | Educational Precinct | 11 | 18.75 | 15 | 22.8 | 16.2693 | 4.3519 | 0 | GREEN | Primary
9676 | Gateshead Central | 11 | 18.75 | 15 | 22.1 | 13.9116 | 3.6275 | 3.455 | GREEN | Primary
9633 | Pilgrim | 11 | 32 | 16 | 32 | 19.1608 | 4.1602 | 0 | GREEN | Primary
9634 | University | 11 | 32 | 16 | 32 | 21.8302 | 6.3932 | 3.52 | GREEN | Primary
9672 | Bensham | 11 | 32 | 16 | 32 | 21.4786 | 2.2863 | 1.5 | GREEN | Primary
9625 | Benwell | 11 | 40 | 20 | 29 | 18.11 | 5.342 | 0.38 | GREEN | Primary
9674 | Blaydon Burn | 11 | 18.75 | 15 | 24 | 11 | 0.11348 | 2.799 | GREEN | Primary
9913 | Close | 11 | 32 | 16 | 32 | 25.2368 | 8.4946 | 1.787 | GREEN | Primary
9671-20 | Dunston 66/20kV | 20 | 30 | 15 | 28 | 14.9051 | 2.3839 | 0.5 | GREEN | Primary
9706 | Hexham | 20 | 37.5 | 30 | 36 | 21.9026 | 7.0597 | 1.175 | GREEN | Primary
9709 | West Wylam | 20 | 30 | 15 | 30 | 18.9615 | 5.1064 | 0.8 | GREEN | Primary
9716 | Harraton | 11 | 30 | 15 | 36 | 19.5921 | 10.2 | 13.624 | GREEN | BSP
9673-20 | Birtley Grove 66/20kV | 20 | 30 | 15 | 28 | 9.5897 | 1.267 | 0 | RED | Primary
9679 | Team Valley | 20 | 42 | 30 | 41 | 31.3647 | 5.8329 | 13.193 | RED | Primary
9705-20 | Spadeadam 20kV | 20 | 15 | 7.5 | 12 | 0 | 2.0212 | 0.3264 | GREEN | BSP
2868348-20 | Fourstones 20kV | 20 | 40 | 40 | NGET | 15.68 | -54.25 | 0 | GREEN | BSP
9817 | Aycliffe Industrial | 11 | 24 | 12 | 19 | 0.45 | 1.1592 | 0 | GREEN | Primary
9820 | Darlington West | 11 | 18.75 | 15 | 24 | 13.6911 | 5.3732 | 1.354 | GREEN | Primary
9823 | Heighington | 11 | 32 | 16 | 29 | 14.0992 | 2.1455 | 3.28 | GREEN | Primary
9824 | Newton Aycliffe South | 11 | 18.75 | 15 | 23 | 14.86 | 0.11452 | 0.6 | GREEN | Primary
9825 | Rise Carr | 6 | 18.75 | 15 | 23 | 10.3231 | 1.6087 | 0.56 | GREEN | Primary
3357866-11 | Norton 132/11kV | 11 | 40 | 20 | 38.1 | 30.8 | 0.77768 | 2.525 | GREEN | BSP
9692 | Boldon Downhill | 20 | 19 | 15 | 25.3 | 10.68 | 2.1325 | 3.5 | GREEN | Primary
7377944 | Breamish Street | 11 | 30 | 15 | 18 | 10.5385 | 2.3556 | 4.87 | GREEN | Primary
9718 | Carley Hill | 11 | 18.75 | 15 | 24 | 16.9914 | 2.278 | 0 | GREEN | Primary
9675 | Carr Hill | 11 | 18.75 | 15 | 22 | 17.8889 | 3.0479 | 0.75 | GREEN | Primary
2889655 | Gateshead East | 11 | 32 | 16 | 34.13 | 9.32 | 0.38363 | 0 | GREEN | Primary
9677 | Harlow Green | 11 | 24 | 12 | 18 | 16.08 | 4.1451 | 0.8 | AMBER | Primary
9694 | Hebburn | 5.75 | 10 | 10 | 12 | 3.8131 | 0.2348 | 0 | GREEN | Primary
9695 | Hebburn West | 11 | 24 | 12 | 24 | 2.8064 | 0.11368 | 1.564 | GREEN | Primary
9696 | Hedworth | 11 | 32 | 16 | 32 | 10.8988 | 1.3693 | 5.464 | GREEN | Primary
9720 | High Barmston | 11 | 18.75 | 15 | 24 | 23.3333 | 5.9981 | 0.8 | RED | Primary
9725-1 | Sunderland T1 T2 | 11 | 24 | 12 | 24 | 17.79 | 4.1483 | 16.556 | RED | Primary
9699 | Temple Park | 11 | 18.75 | 15 | 24 | 15.6883 | 3.7944 | 0 | GREEN | Primary
9727 | Usworth | 11 | 24 | 12 | 24 | 15.8154 | 3.7645 | 8.165 | AMBER | Primary
9635 | Walker | 11 | 20 | 12 | 24 | 15.2131 | 5.4119 | 0.5 | GREEN | Primary
9700 | Wardley | 5.75 | 15 | 11.25 | 19 | 8.1603 | 1.7354 | 0.8 | GREEN | Primary
9729 | West Southwick | 11 | 32 | 16 | 32 | 10.9 | 2.3279 | 10.59 | GREEN | Primary
9784 | Billingham Marsh House | 11 | 24 | 12 | 24 | 14.6224 | 0.11509 | 4.56 | GREEN | Primary
9763 | Faraday Street | 11 | 18.75 | 15 | 22 | 18.867 | 0.11681 | 3.1 | AMBER | Primary
9792 | Malleable | 11 | 32 | 16 | 32 | 17.1621 | 3.6379 | 0.505 | GREEN | Primary
9780-1 | North Tees T1 T2 | 11 | 30 | 15 | 34 | 16.53 | 2.7207 | 8.218 | GREEN | Primary
9795 | Tees Industrial T1 T2 | 11 | 18.75 | 15 | 20 | 13.6575 | 2.3279 | 3.9 | GREEN | Primary
9778 | Greatham | 11 | 30 | 15 | 35 | 21.918 | 1.2354 | 0 | GREEN | BSP
9761 | Carlin How T3 T4 | 11 | 24 | 12 | 24 | 13.75 | 1.3811 | 0 | GREEN | Primary
9764 | Grangetown | 11 | 24 | 12 | 24 | 17.4246 | 1.9399 | 2.513 | GREEN | Primary
9765 | Guisborough T1 T2 | 11 | 24 | 12 | 24 | 16.266 | 1.166 | 0.2 | GREEN | Primary
9769 | Prissick | 11 | 18.75 | 15 | 22.8 | 20.6441 | 4.9677 | 0 | GREEN | Primary
9770 | Redcar | 11 | 45 | 22.5 | 38.1 | 27.4509 | 4.0244 | 1.792 | GREEN | Primary
9773 | Spencerbeck | 11 | 40 | 20 | 38.11 | 20.7112 | 10.1647 | 5.304 | GREEN | Primary
9839 | Poppleton | 33 | 120 | 120 | 120 | 37.5533 | 12.41 | 19.396 | GREEN | BSP
9690 | South Shields | 33 | 100 | 100 | 130 | 47.91 | -8.79 | 2.18 | GREEN | BSP
9717-33 | Offerton | 33 | 100 | 100 | 114 | 37.8048 | 17.75 | 2.975 | GREEN | BSP
2810936 | Knaresborough | 132 | 240 | 240 | 240 | 151.12 | 24.63 | 18.217 | GREEN | GSP
3357866-132 | Norton | 132 | 240 | 240 | 864 | 364.93 | 84.89 | 50.3136 | GREEN | GSP
9926 | Saltholme | 132 | 240 | 240 | 288 | 78.41 | -127.02 | 102.3 | GREEN | GSP
9912 | Stella North | 132 | 120 | 120 | 720 | 186.36 | 44.8545 | 32.2562 | GREEN | GSP
301538 | Stella South | 132 | 240 | 240 | 720 | 251.61 | 3.93 | 34.2736 | GREEN | GSP
9811-132 | Spennymoor GSP | 132 | 240 | 240 | 576 | 197.63 | -2.9 | 31.562 | GREEN | GSP
9929 | Osbaldwick | 132 | 240 | 240 | 576 | 261.37 | 58.69 | 18.7486 | GREEN | GSP
9915-132 | Blyth 132kV | 132 | 240 | 240 | 288 | 23.32 | -442.2 | 8.819 | GREEN | GSP
7494777 | Tynemouth | 132 | 240 | 240 | 576 | 152.22 | 46.41 | 40.091 | GREEN | GSP
9785-33 | Bowesfield | 33 | 90 | 45 | 108 | 88.0182 | 9 | 3.9516 | GREEN | BSP
9819 | Darlington North | 33 | 90 | 45 | 109 | 62.7481 | 9.5803 | 11.896 | GREEN | BSP
9875 | Leeming Bar | 33 | 90 | 45 | 141 | 115.7791 | 4.5 | 4.18 | GREEN | BSP
9605 | Chirton Grange | 33 | 60 | 30 | 72 | 48 | 7.14 | 2 | GREEN | BSP
9621-33 | Blucher | 33 | 90 | 45 | 114 | 87.213 | 11.18 | 8.6482 | GREEN | BSP
9897-33 | Wormald Green 132/33kV | 33 | 60 | 30 | 72 | 48.1386 | 6.25 | 6.622 | GREEN | BSP
9838-33 | Melrosegate 132/33kV | 33 | 90 | 45 | 180 | 119.2118 | 12.1777 | 10.9956 | GREEN | BSP
9620 | Barrack Road | 33 | 120 | 60 | 114 | 75.0959 | 15.37 | 6.975 | GREEN | BSP
9928-33 | Darlington Central | 33 | 60 | 30 | 72 | 43.8 | 4.9 | 11.378 | GREEN | BSP
9858 | Scarborough Grid | 33 | 120 | 60 | 100 | 76.27 | 9.87 | 3.95 | GREEN | BSP
9910 | Flatworth | 33 | 60 | 30 | 72 | 41.9039 | 4.73 | 33.468 | RED | BSP
9623-33 | Gosforth | 33 | 90 | 45 | 108 | 93.0948 | 11.2 | 4.623 | GREEN | BSP
9893-33 | Husthwaite | 33 | 45 | 22.5 | 54 | 27.3359 | 0.81 | 2.063 | GREEN | BSP
9891-33 | Harrogate 132/33kV | 33 | 60 | 30 | 120 | 68.7938 | 6.6 | 7.041 | GREEN | BSP
9739-66 | Annfield | 66 | 75 | 37.5 | 90.8 | 57.78 | 3.28 | 2.4816 | GREEN | BSP
2594836 | Ravensworth | 66 | 75 | 37.5 | 90 | 85.1506 | 8.174 | 16.193 | RED | BSP
9670 | Coalburns | 66 | 75 | 37.5 | 91.3 | 63.3058 | 7.6 | 1.975 | GREEN | BSP
9810-66 | Potter House 132/66kV | 66 | 120 | 60 | 86.25 | 75.8377 | 12.8 | 8.359 | GREEN | BSP
9812-66 | Toronto | 66 | 90 | 45 | 108 | 92.0589 | 3.25 | 0.222 | GREEN | BSP
9811-66 | Spennymoor 132/66kV | 66 | 75 | 37.5 | 188 | 80.555 | 9.14 | 22.981 | GREEN | BSP
9835 | Malton Grid | 66 | 75 | 37.5 | 82 | 69.5072 | 6.14 | 3.803 | GREEN | BSP
9645-66 | Linton | 66 | 60 | 30 | 72 | 56.3848 | -51.23 | 8.819 | GREEN | BSP
9671-66 | Dunston | 66 | 150 | 75 | 195 | 88.9764 | 13.2 | 15.29 | GREEN | BSP
9782 | Seal Sands | 66 | 90 | 45 | 112 | 35.39 | -135.75 | 3.9 | GREEN | BSP
9780-66 | North Tees | 66 | 150 | 75 | 150.6 | 105.18 | 6.5069 | 16.383 | GREEN | BSP
9787-66 | Hartmoor | 66 | 120 | 120 | 120 | 88.54 | -19.67 | 20.508 | GREEN | BSP
9915-66 | Blyth 66kV | 66 | 120 | 120 | 309 | 127.2095 | -48.49 | 98.618 | GREEN | BSP
9691 | West Boldon | 66 | 120 | 120 | 388 | 212.7558 | 65.84 | 86.909 | GREEN | BSP
9759 | Lackenby | 66 | 120 | 120 | 306 | 151.1513 | 20.43 | 9.809 | GREEN | BSP
9918 | Hawthorn Pit Grid | 66 | 180 | 180 | 234 | 90.4 | 11.88 | 10.379 | GREEN | BSP
9610-2 | Cramlington T2 T4 | 11 | 19 | 12 | 24 | 13.7927 | 3.1202 | 0 | GREEN | Primary
9671-11 | Dunston 66/11kV | 11 | 24 | 12 | 24 | 15.4575 | 1.8723 | 8.324 | AMBER | Primary
9673-11 | Birtley Grove 66/11kV | 11 | 32 | 16 | 30 | 14.1706 | 3.0691 | 3 | RED | Primary
9780-2 | North Tees T3 T4 | 11 | 30 | 15 | 36 | 18.59 | 0.76141 | 0 | GREEN | Primary
9785-66-11 | Bowesfield 66/11kV | 11 | 32 | 16 | 32 | 14.2103 | 8.6831 | 0 | GREEN | Primary
9927-6 | Darlington 132/6kV | 6 | 30 | 15 | 12 | 3.5355 | 0.62038 | 0 | GREEN | BSP
9866-2 | Whitby T2 | 11 | 24 | 12 | 19.1 | 5.75 | 0.083138 | 0.64 | GREEN | Primary
9867-2 | Whitby West T2 | 11 | 24 | 12 | 24 | 5.77 | 0.22614 | 0 | GREEN | Primary
9882-1 | Richmond T1 | 11 | 24 | 12 | 24 | 10.5627 | 0.083138 | 0 | RED | Primary
7753909 | Harrogate West | 11 | 30 | 15 | 30 | 12.97 | 3.065 | 1.5 | GREEN | Primary
9810-11 | Potter House T4 T5 | 11 | 30 | 15 | 30 | 6.3161 | 0.96648 | 0.518 | GREEN | Primary
9725-5 | Sunderland T5 T6 | 11 | 30 | 15 | 30 | 0 | 0 | 0 | GREEN | Primary
7344629 | Skeeby | 33 | 90 | 57 | 90 | 115.7791 | 4.5 | 0 | RED | BSP
7775573 | Aycliffe Forrest | 11 | 30 | 15 | 30 | 0 | 0 | 4.852 | GREEN | Primary
3337559 | Kielder | 20 | 4 | 4 | 4 | 0 | 0.2 | 0 | GREEN | Primary

## Yorkshire Demand
Substation ID | Substation Name | Nominal Voltage | Transformer Capacity |  | Firm Capacity | Demand |  | Demand Heat Map |  | Substation Class
Downstream
|  | (kV) | OFAF (MVA) | ONAN (MVA) | Load (MVA) | Maximum (MVA) | Minimum (MVA) | Accepted Demand (Diversified MVA) | Demand Classification | GSP, BSP or Primary
4038567 | Darnall | 11 | 24 | 12 | 23 | 15.6712 | 3.8471 | 0.56 | GREEN | Primary
4038610 | Orgreave | 11 | 23 | 15 | 23 | 9.3642 | 2.366 | 3.025 | GREEN | Primary
4038573 | Revill Lane | 11 | 23 | 15 | 23 | 7.2159 | 1.5564 | 0 | GREEN | Primary
4038565 | Shirland Lane | 11 | 24 | 12 | 24 | 9.5818 | 1.696 | 1.2 | GREEN | Primary
4038562 | Stoke Street | 11 | 24 | 12 | 24 | 13.0091 | 1.0064 | 0 | GREEN | Primary
4038575 | Barnsley | 11 | 18.75 | 15 | 21.5 | 14.2451 | 3.8597 | 0.8 | GREEN | Primary
4038788 | Barugh 66/11kV | 11 | 30 | 15 | 30 | 18.9 | 3.34 | 0 | GREEN | Primary
4038792-1 | Elmhirst Lane 1 | 11 | 24 | 12 | 24 | 12.5839 | 0.65119 | 0 | GREEN | Primary
4038531 | Scissett | 11 | 18.75 | 15 | 23 | 16.5567 | 3.9364 | 0 | GREEN | Primary
4038576 | Smithy Green | 11 | 7.5 | 7.5 | 7.5 | 7.0272 | 1.2448 | 0 | AMBER | Primary
4038574 | Woolley | 11 | 18.75 | 15 | 23 | 9.1964 | 1.2907 | 2.25 | GREEN | Primary
4038661-1 | Beeston Royds 33/11kV | 11 | 18.75 | 15 | 23 | 5.9285 | 1.0365 | 1.775 | GREEN | Primary
4038654 | Gildersome | 11 | 23 | 11.5 | 23 | 15.9776 | 1.2899 | 4.072 | GREEN | Primary
4038665 | Hedley Chase | 11 | 23 | 11.5 | 23 | 7.18 | 1.4168 | 4.9 | GREEN | Primary
4038668 | Middleton Town Street | 11 | 18.75 | 15 | 23 | 22.4528 | 1.283 | 1.638 | RED | Primary
4038658 | Morley | 11 | 18.75 | 15 | 23 | 12.4838 | 3.81 | 0 | GREEN | Primary
4038664 | Tingley | 11 | 24 | 12 | 24 | 14.1837 | 3.8736 | 6.1 | GREEN | Primary
4038629 | Whitehall Road 4/5 | 11 | 18.75 | 15 | 19 | 7.7271 | 1.6541 | 3.181 | GREEN | Primary
4038707 | Endike Lane | 11 | 23 | 15 | 23 | 11.614 | 0.71038 | 2.504 | GREEN | Primary
4038711 | First Avenue | 11 | 24 | 12 | 24 | 18.4168 | 3.057 | 0 | GREEN | Primary
4038821 | Holme Upon Spalding Moor | 11 | 24 | 12 | 8 | 6.56 | 0.63145 | 1.45 | RED | Primary
4038701 | Norwood | 11 | 23 | 11.5 | 23 | 13.7458 | 1.5913 | 2.153 | GREEN | Primary
4038767 | Southgate | 11 | 23 | 11.5 | 8 | 5.466 | 0.47359 | 1.88 | AMBER | Primary
4038702 | Southwood Road | 11 | 23 | 11.5 | 23 | 15.4743 | 4.2505 | 0 | GREEN | Primary
4038703 | Spark Mill Lane | 11 | 23 | 11.5 | 23 | 15.2939 | 2.3102 | 1.583 | GREEN | Primary
4038502 | Airedale Road | 11 | 18.75 | 15 | 23 | 10.2585 | 1.97 | 2.15 | GREEN | Primary
4038796 | Bingley 33/11kV | 11 | 24 | 12 | 23.8 | 14.8384 | 3.8037 | 0.527 | GREEN | Primary
4038503 | Harden | 11 | 23 | 11.5 | 8 | 4.2563 | 0.72025 | 0 | GREEN | Primary
4038497-1 | Haworth 1 | 11 | 30 | 15 | 30 | 9.0761 | 0.43412 | 0 | GREEN | Primary
4038505 | Nabwood | 11 | 23 | 11.5 | 23 | 12.4103 | 2.7231 | 0 | GREEN | Primary
4038499 | South Street | 11 | 23 | 11.5 | 23 | 9.9323 | 2.2195 | 0.35 | GREEN | Primary
4038570 | Blackburn Meadows 33/11kV | 11 | 24 | 12 | 24 | 14.28 | 3.1966 | 1.75 | GREEN | Primary
4038607 | BOC Brinsworth | 11 | 18.75 | 15 | 23 | 5.137 | 1.0756 | 0.773 | GREEN | Primary
4038609 | Templeborough 33/11kV | 11 | 18.75 | 15 | 23 | 12.3166 | 2.4428 | 1.1 | GREEN | Primary
4038569 | Tinsley Wire Industries | 11 | 24 | 12 | 24 | 5.2095 | 1.324 | 6.53 | GREEN | Primary
4038776 | Corringham Road | 11 | 23 | 11.5 | 23 | 14.0379 | 1.369 | 0 | GREEN | Primary
4038601 | Epworth | 11 | 24 | 12 | 10 | 7.6556 | 1.1245 | 0 | GREEN | Primary
4038778 | Harpswell | 11 | 24 | 12 | 8 | 7.82 | -3.3349 | 0 | AMBER | Primary
4038605 | Haxey | 11 | 12 | 12 | 8 | 5.34 | 0.77945 | 0 | GREEN | Primary
4038775 | Lea Road | 11 | 23 | 11.5 | 15.8 | 10.46 | 2.3284 | 0 | GREEN | Primary
4038783 | Normanby | 11 | 12 | 12 | 8 | 5.89 | 0.85838 | 0.4 | AMBER | Primary
4038777 | Stow | 11 | 24 | 12 | 6.5 | 5.3467 | -9.087 | 0 | AMBER | Primary
4038470 | Balme Street | 11 | 24 | 12 | 24 | 14.7759 | 3.5386 | 2 | GREEN | Primary
4038463 | Gaisby Lane | 11 | 18.75 | 15 | 23 | 14.2414 | 3.748 | 0 | GREEN | Primary
4038471 | Idle | 11 | 18.75 | 15 | 23 | 14.7209 | 3.3851 | 1.52 | GREEN | Primary
4038477 | Killinghall Road | 11 | 24 | 12 | 7.5 | 0.66121 | 0.0098664 | 0 | GREEN | Primary
4038468 | Manchester Road | 11 | 23 | 11.5 | 23 | 8.8896 | 3.1827 | 0.5 | GREEN | Primary
4038473 | Moorside Road | 11 | 18.75 | 15 | 23 | 12.3725 | 2.0659 | 0.279 | GREEN | Primary
4038472 | Mount Street | 11 | 18.75 | 15 | 23 | 22.7105 | 2.715 | 0 | AMBER | Primary
4038462 | Shipley | 11 | 24 | 12 | 23 | 10.615 | 3.0319 | 0 | GREEN | Primary
4038648 | Audby Lane | 11 | 23 | 11.5 | 23 | 17.7916 | 4.6344 | 2.99 | GREEN | Primary
4038635 | Dunkeswick | 11 | 12 | 12 | 8 | 6.9288 | 1.2223 | 0 | AMBER | Primary
4038694 | Fenton Lane | 11 | 23 | 11.5 | 23 | 7.3546 | 0.94718 | 0 | GREEN | Primary
4038647 | Leeds Road | 11 | 24 | 12 | 8 | 5.6158 | 1.0365 | 0 | GREEN | Primary
4038814 | Sherburn | 11 | 25 | 12.5 | 25 | 14.4884 | -1.7365 | 10.037 | AMBER | Primary
4038650 | Tadcaster | 11 | 23 | 11.5 | 23 | 13.4694 | 4.6623 | 0 | GREEN | Primary
4038649 | Warren Lane | 11 | 23 | 11.5 | 8 | 4.4977 | -0.35519 | 0 | GREEN | Primary
4038720 | Holderness | 11 | 18.75 | 15 | 23 | 12.1155 | 2.4875 | 0.404 | GREEN | Primary
4038718 | Saltshouse Road | 11 | 18.75 | 15 | 23 | 11.5938 | 3.6712 | 2.13 | GREEN | Primary
4038715 | Tiverton Road | 11 | 23 | 11.5 | 23 | 14.0054 | 3.0151 | 0.9 | GREEN | Primary
4038714 | Wawne Road | 11 | 24 | 12 | 24 | 8.5736 | 1.2516 | 0.68 | GREEN | Primary
4038523 | Bailiff Bridge | 11 | 24 | 12 | 24 | 7.999 | 1.8845 | 6.058 | GREEN | Primary
4038525 | Brighouse 33/11kV | 11 | 12 | 12 | 12 | 10.9842 | 1.5997 | 0.7 | AMBER | Primary
4038528 | Deighton | 11 | 18.75 | 15 | 23 | 19.47 | 5.0462 | 3 | AMBER | Primary
4038787 | Lowfields | 11 | 24 | 12 | 19 | 5.0175 | 1.332 | 0 | GREEN | Primary
4038795 | Millroyd Street | 11 | 12.5 | 10 | 15.3 | 11.5572 | 2.9817 | 0.747 | GREEN | Primary
4038474 | Snelsins Lane | 11 | 18.75 | 15 | 23 | 11.1226 | 0.62159 | 1.215 | GREEN | Primary
4038480 | Spenborough | 11 | 30 | 15 | 30 | 12.986 | 2.3868 | 0 | GREEN | Primary
4038757 | Drax Primary | 11 | 7.5 | 7.5 | 8 | 7.97 | 0.39466 | 0.56 | RED | Primary
4038602 | Crowle | 11 | 7.5 | 7.5 | 6.5 | 5.05 | 0.76958 | 1.974 | RED | Primary
4038761 | Goole | 11 | 18.75 | 15 | 23 | 16.2887 | 5.1433 | 0 | GREEN | Primary
4038828 | Guardian Glass | 11 | 30 | 15 | 30 | 3.9727 | 2.4339 | 17.48 | GREEN | Primary
4038759 | Rawcliffe | 11 | 18.75 | 15 | 8 | 4.2814 | 1.3819 | 0 | GREEN | Primary
4038877 | Cornwall Street | 11 | 30 | 15 | 39 | 16.9576 | 3.1827 | 2.05 | GREEN | BSP
4038598 | Armthorpe | 11 | 18.75 | 15 | 12 | 11.0056 | -2.5653 | 1.108 | RED | Primary
4038696 | Askern | 11 | 23 | 11.5 | 23 | 9.3765 | -1.401 | 0 | GREEN | Primary
4038623 | Austerfield | 11 | 12.5 | 10 | 8 | 4.5808 | 0.67092 | 0.912 | GREEN | Primary
4038591 | Balby | 11 | 18.75 | 15 | 22.86 | 11.6155 | 1.4517 | 3.196 | GREEN | Primary
4038586 | Barnburgh | 11 | 24 | 12 | 24 | 9.5314 | -5.7127 | 0 | GREEN | Primary
4038587 | Brodsworth | 11 | 18.75 | 15 | 23 | 14.3275 | 1.2557 | 0 | GREEN | Primary
4038585 | Hickleton | 11 | 18.75 | 15 | 23 | 6.1387 | -2.7626 | 1 | GREEN | Primary
4038593 | ICI Fibres | 11 | 18.75 | 15 | 23 | 10.2633 | -2.0128 | 1.25 | GREEN | Primary
4038596 | Kirk Sandall | 11 | 24 | 12 | 24 | 11.5184 | 2.1706 | 3.25 | GREEN | Primary
4038597 | Markham Gates | 11 | 18.75 | 15 | 23 | 15.8404 | 3.8387 | 0.881 | GREEN | Primary
4038595 | Rockware | 11 | 18.75 | 15 | 23 | 19.3797 | 6.95 | 0 | GREEN | Primary
4038599 | Stainforth | 11 | 18.75 | 15 | 23 | 7.2026 | 0.55252 | 4.8 | GREEN | Primary
4038600 | Thorne | 11 | 18.75 | 15 | 23 | 16.61 | 1.5355 | 2.515 | GREEN | Primary
4038604 | West End Lane | 11 | 18.75 | 15 | 23 | 11.7769 | 1.9832 | 0.6 | GREEN | Primary
4038801 | West Moor Park | 11 | 24 | 12 | 25 | 17.7453 | 2.2446 | 3.85 | GREEN | Primary
4038594 | Wheatley Park | 11 | 18.75 | 15 | 23 | 8.7753 | 2.0869 | 0.88 | GREEN | Primary
4038589 | Belmont Avenue | 11 | 23 | 11.5 | 23 | 18.3554 | 2.9402 | 1.298 | GREEN | Primary
4038588 | Bentley | 11 | 24 | 12 | 24 | 11.9009 | 2.0729 | 0.3 | GREEN | Primary
4038590 | Greyfriars Rd | 11 | 23 | 15 | 24 | 9.7157 | 2.6718 | 0.783 | GREEN | Primary
7256105 | Greyfriars Road 3/4 | 11 | 30 | 15 | 30 | 8.4335 | 1.8686 | 0.69 | GREEN | Primary
4038592 | Jarratt Street | 11 | 23 | 11.5 | 23 | 20.05 | 6.9376 | 2.14 | AMBER | Primary
4038763 | Belthorpe Lane | 11 | 24 | 12 | 8 | 4.5466 | 0.73998 | 0 | GREEN | Primary
4038723 | Brett Street | 11 | 24 | 12 | 24 | 19.0523 | 5.9717 | 0.5 | GREEN | Primary
4038725 | Burton Pidsea | 11 | 24 | 12 | 9 | 4.8181 | -9.087 | 0 | GREEN | Primary
4038700 | Butterwick | 11 | 15 | 7.5 | 6.5 | 5.0798 | -7.3702 | 0 | AMBER | Primary
4038790 | Driffield | 11 | 24 | 12 | 24 | 16.8032 | 3.8025 | 0 | GREEN | Primary
4038822 | Hayton | 11 | 12.5 | 10 | 15.3 | 13.25 | 1.7069 | 0.458 | AMBER | Primary
4038713 | Hunmanby | 11 | 24 | 12 | 24 | 8.4325 | 1.8549 | 0 | GREEN | Primary
4038699 | Kirkburn | 11 | 30 | 15 | 8 | 6.7 | -2.0128 | 0.4 | AMBER | Primary
4038724 | Martongate | 11 | 12.5 | 10 | 15.3 | 12.9579 | 1.361 | 0.362 | AMBER | Primary
4038760 | Sandhill Lane | 11 | 10 | 5 | 8 | 5.0497 | 1.3517 | 0 | GREEN | Primary
4038826 | Seaton | 11 | 20 | 10 | 20 | 16.9617 | 2.3482 | 0 | GREEN | Primary
4038683 | Commonside Lane | 11 | 24 | 12 | 24 | 16.6747 | -1.184 | 0.442 | GREEN | Primary
4038680 | Normanton | 11 | 23 | 11.5 | 23 | 17.5124 | 6.1908 | 0 | GREEN | Primary
4038690 | Prince of Wales | 11 | 23 | 11.5 | 23 | 10.7629 | 2.3975 | 0.75 | GREEN | Primary
4038681 | Sharlston | 11 | 23 | 11.5 | 23 | 11.3658 | 2.6047 | 0 | GREEN | Primary
4038685 | Wellington Street | 11 | 23 | 11.5 | 23 | 16.7655 | 4.7391 | 1.59 | GREEN | Primary
4038461 | Crown Street | 11 | 23 | 11.5 | 8 | 4.7883 | 0.85071 | 0.9 | GREEN | Primary
4038456 | Four Lane Ends | 11 | 23 | 11.5 | 23 | 14.3174 | 2.4847 | 0 | GREEN | Primary
4038458 | Legrams Mill Lane | 11 | 18.75 | 15 | 23 | 9.9161 | 2.8058 | 0.328 | GREEN | Primary
4038467 | Rawson Road | 11 | 23 | 11.5 | 23 | 10.9938 | 1.3849 | 1.5 | GREEN | Primary
4038459 | Saint Street | 11 | 23 | 11.5 | 23 | 6.48 | 1.2516 | 0.25 | GREEN | Primary
4038457 | Toller Lane | 11 | 18.75 | 15 | 23 | 10.7585 | 2.9872 | 1.381 | GREEN | Primary
4038843 | Halifax 33/11kV | 11 | 40 | 20 | 40 | 33.6825 | 7.1236 | 2.139 | GREEN | Primary
4038484 | Burnleyville | 11 | 23 | 11.5 | 23 | 13.0392 | 2.9244 | 0.4 | AMBER | Primary
4038481 | Liversedge | 11 | 18.75 | 15 | 23 | 10.8698 | 2.7639 | 1.714 | AMBER | Primary
4038810 | Nab Lane | 11 | 25 | 12.5 | 12 | 9.3588 | 1.5096 | 0 | AMBER | Primary
4038651 | White Lee | 11 | 23 | 15 | 23 | 11.6044 | 3.2315 | 0 | AMBER | Primary
4038501 | Denholme | 11 | 12 | 12 | 6.5 | 3.8452 | 0.31573 | 0 | GREEN | Primary
4038507 | Furness Avenue | 11 | 23 | 11.5 | 23 | 12.2767 | 3.0389 | 0.8 | GREEN | Primary
4038508 | Gibraltar Road | 11 | 24 | 12 | 24 | 15.3658 | 5.4301 | 0 | GREEN | Primary
4038514 | Queensbury | 11 | 24 | 12 | 24 | 14.5277 | 3.1994 | 0 | GREEN | Primary
4038510 | Swan Bank Lane | 11 | 24 | 12 | 24 | 12.3087 | 2.3383 | 0 | GREEN | Primary
4038455 | Thornton | 11 | 18.75 | 15 | 23 | 12.6588 | 3.3222 | 0 | GREEN | Primary
4038728 | Easington | 11 | 24 | 12 | 17 | 5.4446 | 1.6751 | 0 | GREEN | Primary
4038721 | Hedon Road | 11 | 23 | 11.5 | 23 | 15.7319 | 2.2055 | 0 | GREEN | Primary
4038893 | Hull East 33/11kV | 11 | 25 | 12.5 | 23 | 12.4933 | 2.8711 | 0 | GREEN | Primary
4038719 | King George Dock | 11 | 30 | 15 | 30 | 8.3319 | 2.01 | 1.6 | GREEN | Primary
4038807 | Ottringham Road | 11 | 24 | 12 | 15 | 13.062 | -13.9807 | 0 | AMBER | Primary
4038726 | Patrington Road | 11 | 24 | 12 | 8 | 5.29 | -4.1735 | 0 | GREEN | Primary
4038717 | Westcott Street | 11 | 23 | 11.5 | 23 | 14.1893 | 2.0799 | 0 | GREEN | Primary
4038727 | Withernsea | 11 | 24 | 12 | 10 | 5.7786 | 0.96691 | 0.408 | GREEN | Primary
4038704 | Elgar Road | 11 | 18.75 | 15 | 23 | 15.5115 | 4.5227 | 0.55 | GREEN | Primary
4038698 | Gibson Lane | 11 | 18.75 | 15 | 23 | 15.7459 | 3.4548 | 7.65 | RED | Primary
4038766-1 | Newport 1 | 11 | 24 | 12 | 18.4 | 16.7086 | -1.1938 | 4.006 | RED | Primary
4038697 | Skillings Lane | 11 | 23 | 15 | 24 | 9.7078 | 0.26639 | 5.6 | GREEN | Primary
4038797 | Eggborough | 11 | 7.5 | 7.5 | 8 | 4.44 | 1.2136 | 0 | GREEN | Primary
4038692-11 | Ferrybridge A 11kV | 11 | 30 | 15 | 30 | 22.9 | 6 | 9.603 | RED | Primary
7501276 | South Elmsall | 11 | 30 | 15 | 30 | 14.5864 | 2.0885 | 6.072 | GREEN | Primary
4038816 | Grimethorpe | 11 | 25 | 12.5 | 25 | 8.3748 | -2.9501 | 1 | GREEN | Primary
4038684 | Hemsworth | 11 | 12.5 | 10 | 10 | 8.5184 | 1.2728 | 2.88 | RED | Primary
4038686 | Ledston | 11 | 18.75 | 15 | 23 | 12.1228 | 3.1178 | 7.32 | GREEN | Primary
4038581 | Monckton | 11 | 12.5 | 10 | 15.3 | 8.8669 | 2.038 | 0 | GREEN | Primary
4038689 | South Kirkby | 11 | 18.75 | 15 | 23 | 19.6512 | 3.3941 | 2.175 | AMBER | Primary
4038738 | Convamore Road | 11 | 23 | 15 | 23 | 11.295 | 2.9593 | 2.261 | GREEN | Primary
4038740 | Conyard Road | 11 | 18.75 | 15 | 23 | 8.7008 | 1.8056 | 0 | GREEN | Primary
4038741 | Wesley Crescent | 11 | 23 | 11.5 | 23 | 13.1628 | 1.184 | 0 | GREEN | Primary
4038580 | Burton Road | 11 | 30 | 15 | 22.9 | 17.4619 | 9.8664 | 0 | GREEN | Primary
4038578 | Fish Dam Lane | 11 | 24 | 12 | 24 | 10.0436 | 3.4409 | 0 | GREEN | Primary
4038579 | Stairfoot | 11 | 24 | 12 | 24 | 18.6 | 3.392 | 0 | GREEN | Primary
4038534 | Hope | 11 | 18.75 | 15 | 23 | 4.8414 | 1.3819 | 0 | GREEN | Primary
4038533 | Penistone | 11 | 24 | 12 | 24 | 13.3421 | -2.2101 | 0.452 | GREEN | Primary
4038535 | Wheatacre Road | 11 | 12.5 | 10 | 8 | 8.01 | 2.1022 | 0.298 | RED | Primary
4038782 | Barrow | 11 | 24 | 12 | 11.6 | 7.2688 | 1.9338 | 0 | RED | Primary
4038786 | Clough Lane | 11 | 24 | 12 | 8 | 3.3019 | 0.34533 | 7.315 | RED | Primary
4038730 | Eastfield Road | 11 | 23 | 15 | 7 | 6.53 | 0.78932 | 0 | RED | Primary
4038731 | Humber Road | 11 | 23 | 11.5 | 23 | 11.1944 | 3.0704 | 0 | RED | Primary
4038732 | Queens Road | 11 | 40 | 20 | 37 | 21.4295 | 4.1769 | 5.368 | RED | Primary
4038539 | Baslow Road | 11 | 24 | 12 | 24 | 9.92 | 1.2489 | 0 | GREEN | Primary
4038556 | Dronfield | 11 | 24 | 12 | 24 | 10.8402 | 2.6522 | 0 | GREEN | Primary
4038547 | Greenhill | 11 | 24 | 12 | 10 | 6.2416 | 1.4602 | 0 | GREEN | Primary
4038544 | Millhouses | 11 | 24 | 12 | 24 | 6.93 | 1.7405 | 3.325 | GREEN | Primary
4038549 | Woodseats | 11 | 24 | 12 | 24 | 15.2749 | 2.8267 | 0 | GREEN | Primary
4038840 | Keighley | 11 | 30 | 15 | 39 | 16.96 | 1.5969 | 2.115 | GREEN | BSP
4038695 | Beal | 11 | 30 | 15 | 16.2 | 8.21 | -8.4259 | 2.05 | GREEN | Primary
4038687 | Carr Lane | 11 | 18.75 | 15 | 23 | 13.5747 | 4.5227 | 0.825 | GREEN | Primary
4038688 | Smith Street | 11 | 23 | 11.5 | 23 | 7.9287 | 2.0589 | 0 | GREEN | Primary
7395321 | Pollington | 11 | 30 | 15 | 8.5 | 6.6758 | -6.1665 | 2.29 | RED | Primary
4038693 | Weeland Road | 11 | 23 | 11.5 | 21.1 | 21.04 | 11.5301 | 0 | AMBER | Primary
4038624 | Abbey Road | 11 | 23 | 11.5 | 23 | 13.1605 | 2.2683 | 0 | GREEN | Primary
4038656 | Bramley | 11 | 18.75 | 15 | 23 | 17.7399 | 3.8178 | 5.378 | RED | Primary
4038657 | Farnley Crescent | 11 | 24 | 12 | 24 | 12.6 | 1.6751 | 0 | GREEN | Primary
4038634 | Fir Tree Lane | 11 | 23 | 11.5 | 23 | 16.3741 | 4.8578 | 3.8 | GREEN | Primary
4038625 | Iveson House | 11 | 18.75 | 15 | 23 | 13.8485 | 3.5316 | 0 | GREEN | Primary
4038626 | West Park | 11 | 23 | 11.5 | 12 | 8.4178 | 2.0226 | 0.798 | GREEN | Primary
4038659 | Whingate | 11 | 18.75 | 15 | 23 | 6.9637 | 2.3591 | 0 | GREEN | Primary
4038802 | Burley Street | 11 | 40 | 20 | 34.8 | 22.6538 | 3.6012 | 3.688 | GREEN | Primary
4038628 | Clarendon Road | 11 | 23 | 11.5 | 23 | 13.8281 | 0.71038 | 0.56 | GREEN | Primary
4038630 | Upper Basinghall Street | 11 | 24 | 12 | 24 | 14.1102 | 4.36 | 0 | GREEN | Primary
4038633-1 | Allerton Hill T1 | 11 | 18.75 | 15 | 23 | 8.8574 | 0.039466 | 0 | GREEN | Primary
4038637 | Burmantofts | 11 | 18.75 | 15 | 23 | 14.01 | 2.1023 | 0.5 | GREEN | Primary
4038638 | Hillcrest | 11 | 18.75 | 15 | 23 | 12.5209 | 4.4459 | 0 | GREEN | Primary
4038789 | Knostrop | 11 | 24 | 12 | 24 | 6.9168 | 0.64132 | 6 | GREEN | Primary
4038639 | Pontefract Lane 1/2 | 11 | 23 | 11.5 | 23 | 12.7467 | 2.4638 | 1.28 | GREEN | Primary
4038643 | Selby Road | 11 | 18.75 | 15 | 23 | 14.8966 | 2.1706 | 8.05 | AMBER | Primary
4038641 | York Road | 11 | 18.75 | 15 | 23 | 18.8376 | 5.2556 | 2.484 | AMBER | Primary
4038632 | Buslingthorpe Green | 11 | 23 | 11.5 | 23 | 12.2792 | 1.5843 | 0 | GREEN | Primary
4038631 | Carlton Hill | 11 | 18.75 | 15 | 23 | 18.8125 | 5.6324 | 1.3 | GREEN | Primary
4038636 | Leylands Road | 11 | 23 | 11.5 | 23 | 14.219 | 4.7042 | 4.476 | GREEN | Primary
4038627 | Moor Road | 11 | 18.75 | 15 | 23 | 20.0428 | 5.2346 | 3.952 | RED | Primary
4038515 | Dowker Street | 11 | 23 | 15 | 24 | 12.4885 | 2.119 | 0 | GREEN | Primary
4038522 | Grove Street | 11 | 23 | 11.5 | 23 | 10.92 | 2.3242 | 0.44 | GREEN | Primary
4038517 | Honley | 11 | 24 | 12 | 24 | 10.7645 | 2.4624 | 0 | GREEN | Primary
4038512 | Meltham | 11 | 23 | 11.5 | 23 | 9.1606 | 1.2432 | 0 | GREEN | Primary
4038516 | Oakes Road | 11 | 24 | 12 | 24 | 15.3706 | 3.6768 | 1.7 | GREEN | Primary
4038511 | Prospect Road | 11 | 23 | 11.5 | 23 | 19.7704 | 1.1248 | 1.5 | AMBER | Primary
4038506 | Slaithwaite | 11 | 24 | 12 | 24 | 7.3632 | 1.8579 | 0 | GREEN | Primary
7096966 | Armouries Drive | 11 | 30 | 15 | 30 | 9.5282 | 1.7587 | 1.92 | GREEN | Primary
4038670 | Brookfield Street | 11 | 23 | 11.5 | 23 | 10.2622 | 4.2645 | 0.32 | GREEN | Primary
4038669 | Clarence Road | 11 | 30 | 15 | 22.86 | 11.49 | 4.1834 | 2.9 | GREEN | Primary
4038667 | Holbeck | 11 | 23 | 11.5 | 23 | 17.0384 | 4.9834 | 3.878 | GREEN | Primary
4038671 | Leasowe Road | 11 | 23 | 11.5 | 23 | 11.278 | 3.6014 | 0 | GREEN | Primary
4038672 | Stourton 33/11kV | 11 | 18.75 | 15 | 19.4 | 15.4821 | 1.7658 | 4.025 | RED | Primary
4038831 | Sweet Street | 11 | 30 | 15 | 30 | 11.0751 | 1.7901 | 23.134 | RED | Primary
7322111 | Whitehall Road 2/3 | 11 | 30 | 15 | 30 | 6.4404 | 1.3005 | 6.863 | GREEN | Primary
4038488 | Bramhope | 11 | 24 | 12 | 8 | 3.391 | 1.0261 | 0.57 | GREEN | Primary
4038475 | Chevin End | 11 | 30 | 15 | 30 | 7.9272 | 1.2234 | 0 | GREEN | Primary
4038478 | Hallam Street | 11 | 24 | 12 | 23 | 10.7484 | 0.75972 | 0 | GREEN | Primary
4038464 | Kirk Drive | 11 | 23 | 11.5 | 23 | 19.9158 | 3.7394 | 0 | GREEN | Primary
4038483 | North Avenue | 11 | 18.75 | 15 | 23 | 12.0455 | 2.5196 | 0.39 | GREEN | Primary
4038823 | Pool | 11 | 24 | 12 | 23.3 | 8.1653 | 1.2591 | 0.2 | GREEN | Primary
4038736 | Doughty Road | 11 | 24 | 12 | 20.9 | 17.5 | 5.1718 | 1 | GREEN | Primary
4038737 | Grimsby Docks | 6.6 | 18.75 | 15 | 23 | 2.2466 | 0.63145 | 0 | GREEN | Primary
4038739 | Marsden Road | 11 | 24 | 12 | 18 | 15.2 | 5.4789 | 1.31 | AMBER | Primary
4038550 | Blue Boy Street | 11 | 24 | 12 | 24 | 10.345 | 1.5355 | 2.284 | GREEN | Primary
4038542 | Claywheels Lane | 11 | 24 | 12 | 24 | 20.4374 | 4.6735 | 1.4 | GREEN | Primary
4038545 | Crookesmoor Road | 11 | 23 | 11.5 | 24 | 16.6523 | 4.1807 | 0 | GREEN | Primary
4038537 | Loxley Road | 11 | 24 | 12 | 8 | 3.0585 | 0.42426 | 0 | GREEN | Primary
4038546 | Penistone Road | 11 | 23 | 11.5 | 20.2 | 8.3203 | 0.18746 | 3.491 | GREEN | Primary
4038543 | Rawson Spring Road | 11 | 23 | 11.5 | 20.2 | 12.5014 | 4.1738 | 0.511 | GREEN | Primary
4038540 | Stannington Road | 11 | 23 | 11.5 | 24 | 15.4328 | 3.1896 | 0 | GREEN | Primary
4038561 | Gleadless Valley | 11 | 24 | 12 | 24 | 10.3744 | 2.387 | 0 | GREEN | Primary
4038541 | Marmion Road | 11 | 24 | 12 | 24 | 22.89 | 3.8108 | 0 | AMBER | Primary
4038559 | Norfolk Park | 11 | 24 | 12 | 24 | 15.465 | 1.2694 | 0 | GREEN | Primary
4038805 | Saxon Road | 11 | 24 | 12 | 24 | 10.99 | 2.9312 | 1.5 | GREEN | Primary
4038538 | Snaithing Park Road | 11 | 24 | 12 | 24 | 11.0101 | 1.5913 | 0 | GREEN | Primary
4038753 | Olympia Mills | 11 | 30 | 15 | 30 | 15.94 | 2.7951 | 2.352 | GREEN | Primary
4038752 | Selby | 11 | 30 | 15 | 29 | 23.2 | 2.4271 | 0.75 | GREEN | Primary
4038762 | Thorpe Road | 11 | 24 | 12 | 24 | 17.8987 | 2.6941 | 3.009 | GREEN | Primary
4038853 | Park Street | 11 | 30 | 15 | 39 | 13.5384 | 3.6963 | 0 | GREEN | BSP
7256106 | Barnsley Road | 11 | 30 | 15 | 30 | 9.9439 | 3.1562 | 0 | GREEN | Primary
4038560 | Bellhouse Road | 11 | 23 | 11.5 | 23 | 11.231 | 1.7937 | 0 | GREEN | Primary
4038563 | Newhall Road | 11 | 24 | 12 | 24 | 17.1893 | 1.9403 | 3.3 | GREEN | Primary
4038555 | Stanley Street | 11 | 24 | 12 | 24 | 14.5206 | 3.3013 | 6.713 | GREEN | Primary
4038564 | Stevenson Road | 11 | 24 | 12 | 19.4 | 9.5038 | 1.1832 | 2.08 | GREEN | Primary
4038854 | Rawmarsh Road 1_2 | 11 | 30 | 30 | 39 | 23.2389 | 6.9683 | 0.935 | GREEN | BSP
4038898 | Rawmarsh Road 3_4 | 11 | 30 | 30 | 39 | 28.16 | 4.23 | 1.2 | GREEN | BSP
4038482 | Rawdon | 11 | 30 | 15 | 23 | 12.8095 | 4.0452 | 1.8 | GREEN | Primary
4038486 | Rodley Lane | 11 | 12.5 | 10 | 15.3 | 13.4276 | 1.4992 | 1.975 | RED | Primary
4038653 | Swinnow Moor | 11 | 18.75 | 15 | 23 | 14.096 | 3.4423 | 0 | GREEN | Primary
4038479 | Thornbury | 11 | 18.75 | 15 | 23 | 14.0849 | 5.3533 | 1.04 | GREEN | Primary
4038485 | Varley Street | 11 | 18.75 | 15 | 23 | 14.4775 | 4.6344 | 1.75 | GREEN | Primary
4038815 | Ellifoot Lane | 11 | 25 | 12.5 | 2.1 | 2.38 | -1.628 | 0 | RED | Primary
4038809 | Yorkshire Water Hull Road | 11 | 24 | 12 | 23 | 6.6863 | -0.41439 | 0 | GREEN | Primary
4038773 | Firth Brown | 11 | 24 | 12 | 24 | 11.2712 | 1.9347 | 1.55 | GREEN | Primary
4038779 | Hibaldstow | 11 | 12.5 | 10 | 15.3 | 9.7595 | 1.5355 | 0 | GREEN | Primary
4038781 | Pasture Road South | 11 | 24 | 12 | 20 | 9.6322 | 1.3517 | 0.272 | GREEN | Primary
4038774 | South Ferriby | 11 | 30 | 15 | 21 | 15.2528 | 1.2728 | 0.325 | GREEN | Primary
7378946 | Wrawby | 11 | 30 | 15 | 30 | 17.5982 | 4.6637 | 2.195 | GREEN | Primary
4038875 | Sculcoates A | 11 | 30 | 15 | 39 | 24.5848 | 6.6892 | 0 | GREEN | BSP
4038791 | Billet Lane | 11 | 24 | 12 | 24 | 12.1518 | 2.1 | 0.442 | GREEN | Primary
4038768 | Flixborough | 11 | 24 | 12 | 24 | 17.885 | 3.2734 | 10.9 | RED | Primary
4038770 | Foxhills | 11 | 24 | 12 | 18 | 15.8435 | 3.63 | 0 | GREEN | Primary
4038771 | Station Road | 11 | 30 | 15 | 24.8 | 21.1337 | 6.8259 | 0 | GREEN | Primary
4038772 | Bottesford | 11 | 18.75 | 18.75 | 22.86 | 12.2909 | 6.7289 | 0 | GREEN | Primary
4038769 | Bridges Road | 11 | 23 | 11.5 | 23 | 14.1253 | 2.7429 | 2.412 | GREEN | Primary
4038554 | Arundel Street | 11 | 24 | 12 | 24 | 17.6921 | 4.4878 | 4.4 | AMBER | Primary
4038551 | Ellin Street 1/3 | 11 | 24 | 12 | 40.8 | 15.0758 | 5.0588 | 2.146 | GREEN | Primary
4038568-1 | Mansfield Road | 11 | 24 | 12 | 16 | 11.2406 | 2.5056 | 1.056 | GREEN | Primary
4038557 | Park Hill | 11 | 24 | 12 | 24 | 13.2059 | 1.9942 | 1.227 | GREEN | Primary
4038553 | Silver Street | 11 | 24 | 12 | 24 | 12.6353 | 2.8063 | 4.02 | GREEN | Primary
4038548 | Victoria Street | 11 | 24 | 12 | 24 | 19.1234 | 7.3424 | 2.3 | GREEN | Primary
4038489 | Barnoldswick | 11 | 12.5 | 10 | 15.3 | 10.1292 | 2.8546 | 0 | GREEN | Primary
4038498 | Bolton Road | 11 | 12.5 | 10 | 15.3 | 6.9672 | 1.9124 | 0 | GREEN | Primary
4038500 | Chelker Reservoir | 11 | 24 | 12 | 8 | 4.041 | 0.88798 | 0 | GREEN | Primary
4038493 | Cracoe | 11 | 10 | 10 | 12.5 | 6.9924 | 1.4657 | 2.609 | GREEN | Primary
4038496 | Crosshills | 11 | 12.5 | 10 | 15.3 | 10.9804 | 2.4358 | 0.268 | GREEN | Primary
4038504 | Ilkley | 11 | 18.75 | 15 | 23 | 12.8094 | 3.1617 | 0.75 | GREEN | Primary
4038491 | Ings Lane | 11 | 23 | 11.5 | 8 | 6.36 | 1.6427 | 0.36 | AMBER | Primary
4038490 | Salterforth | 11 | 12.5 | 10 | 15.3 | 10.1052 | 1.9068 | 0 | GREEN | Primary
7096982 | Skipton | 11 | 30 | 15 | 19.2 | 13.6769 | 1.6331 | 0 | GREEN | Primary
4038513 | Elland 33/11kV | 11 | 18.75 | 15 | 18.21 | 14.2125 | 3.2315 | 6.08 | RED | Primary
4038492 | Hebden Bridge | 11 | 7.5 | 7.5 | 7.5 | 3.2131 | 0.31573 | 0 | GREEN | Primary
4038495 | Mytholmroyd | 11 | 12.5 | 10 | 15.3 | 9.8221 | 2.0031 | 0 | GREEN | Primary
4038793 | Salterhebble | 11 | 24 | 12 | 24 | 17.5882 | 5.0516 | 0.363 | GREEN | Primary
4038806 | Sowerby Bridge 33/11kV | 11 | 24 | 12 | 23 | 17.0646 | 1.8592 | 0 | GREEN | Primary
4038804 | Todmorden | 11 | 24 | 12 | 23 | 12.7671 | 1.4787 | 1.5 | GREEN | Primary
4038520 | Birkby | 11 | 24 | 12 | 24 | 12.0962 | 1.5145 | 0.325 | GREEN | Primary
4038527 | Dalton | 11 | 24 | 12 | 24 | 14.22 | 4.11 | 0 | GREEN | Primary
4038521 | Folly Hall | 11 | 24 | 12 | 24 | 13.4105 | 3.6517 | 2.6 | GREEN | Primary
4038524 | Saint Andrews Road 33/11kV | 11 | 23 | 11.5 | 23 | 12.5005 | 1.7728 | 0.25 | GREEN | Primary
4038518 | Yew Green Road | 11 | 24 | 12 | 23 | 11.5991 | 2.052 | 0 | GREEN | Primary
4038812 | Dudley Hill | 11 | 25 | 15 | 30 | 17.3149 | 4.1735 | 7.703 | GREEN | Primary
4038466 | Low Moor | 11 | 23 | 11.5 | 23 | 17.3841 | -2.0325 | 0.25 | GREEN | Primary
4038465 | Odsal | 11 | 23 | 11.5 | 23 | 16.2247 | 4.5576 | 2 | GREEN | Primary
4038469 | Spring Mill Street | 11 | 23 | 11.5 | 23 | 15.2059 | 4.5228 | 1.7 | GREEN | Primary
4038476 | Tong Street | 11 | 18.75 | 15 | 23 | 12.296 | 4.0202 | 0.788 | GREEN | Primary
4038460 | Wibsey | 11 | 18.75 | 15 | 23 | 12.6841 | 1.6123 | 0 | GREEN | Primary
4000000 | Stourton 132/11kV | 11 | 30 | 15 | 12 | 11.2758 | 3.3151 | 0.3 | AMBER | BSP
4038611 | Fullerton Road | 11 | 24 | 12 | 24 | 11.633 | 2.0339 | 0 | GREEN | Primary
4038655 | Batley | 11 | 18.75 | 15 | 22.9 | 22.664 | 5.9814 | 1.104 | RED | Primary
4038652 | Calder Wharf | 11 | 18.75 | 15 | 23 | 14.9329 | 2.4428 | 1 | GREEN | Primary
4038660 | Denby Grange | 11 | 23 | 15 | 8 | 3.1822 | 1.0261 | 0 | GREEN | Primary
4038529 | Hazlehead | 11 | 24 | 12 | 24 | 10.2837 | -9.5606 | 2.4 | GREEN | Primary
4038666 | Horbury | 11 | 24 | 12 | 23 | 10.9349 | 1.48 | 0.97 | GREEN | Primary
4038530 | Mirfield | 11 | 24 | 12 | 23 | 14.7315 | 4.5227 | 0 | GREEN | Primary
4038799 | Park Road | 11 | 18.75 | 15 | 23 | 15.7656 | 2.0518 | 2 | GREEN | Primary
4038526 | Scholes | 11 | 24 | 12 | 24 | 11.2766 | 2.2594 | 0 | GREEN | Primary
4038819 | Beighton | 11 | 25 | 12.5 | 25 | 16.3647 | 3.0685 | 0.57 | GREEN | Primary
4038621 | Costhorpe | 11 | 12.5 | 10 | 10 | 6.5652 | 1.9141 | 1.75 | AMBER | Primary
4038619 | Dinnington | 11 | 30 | 15 | 30 | 16.3939 | 2.6047 | 5.046 | GREEN | Primary
4038603 | Edlington | 11 | 18.75 | 15 | 23 | 16.073 | 3.5735 | 1.324 | GREEN | Primary
4038572 | Hackenthorpe | 11 | 24 | 12 | 24 | 12.8604 | 2.1636 | 7.6 | GREEN | Primary
4038622 | Harworth | 11 | 30 | 15 | 30 | 10.0693 | 2.3285 | 2.12 | GREEN | Primary
4038616 | Kiveton Park | 11 | 12.5 | 10 | 15.3 | 8.9408 | -2.0424 | 0 | GREEN | Primary
4038615 | Mexborough 1_2 | 11 | 24 | 12 | 24 | 18.0352 | 3.124 | 1.88 | GREEN | Primary
4038617 | New Orchard Lane | 11 | 18.75 | 15 | 23 | 14.9976 | 3.3502 | 4.76 | GREEN | Primary
4038614 | Silverwood | 11 | 18.75 | 15 | 23 | 14.5453 | 2.0226 | 0.72 | GREEN | Primary
4038620 | Tickhill Road | 11 | 30 | 15 | 23 | 10.8524 | 1.7744 | 0.234 | GREEN | Primary
4038676 | Denby Dale Road | 11 | 24 | 12 | 24 | 10.8699 | 1.3005 | 4.75 | GREEN | Primary
4038674 | Durkar Low Lane | 11 | 18.75 | 15 | 24 | 16.6721 | 4.1039 | 0.6 | GREEN | Primary
4038678 | Woodcock Street | 11 | 23 | 11.5 | 20.2 | 13.0401 | 3.2734 | 0.75 | GREEN | Primary
4038677 | York Street | 11 | 23 | 11.5 | 23 | 17.4121 | 2.4079 | 1.74 | GREEN | Primary
4038673 | Alverthorpe Road | 11 | 18.75 | 15 | 23 | 14.5854 | 3.8183 | 0.4 | GREEN | Primary
4038785 | Kenmore Road | 11 | 24 | 12 | 24 | 16.55 | 4.4 | 2.618 | GREEN | Primary
4038662 | Milton Place | 11 | 18.75 | 15 | 23 | 16.1449 | 3.6573 | 0.206 | GREEN | Primary
4038675 | Outwood | 11 | 18.75 | 15 | 23 | 19.6762 | 3.0487 | 0 | GREEN | Primary
4038679 | Royds Lane | 11 | 23 | 11.5 | 23 | 13.6006 | 2.3186 | 0 | GREEN | Primary
4038808 | Aldham | 11 | 25 | 12.5 | 25 | 13.103 | 2.1146 | 0 | GREEN | Primary
4038800 | Dearne Road | 11 | 24 | 12 | 24 | 12.86 | 2.1022 | 1.25 | GREEN | Primary
4038558 | Ecclesfield | 11 | 18.75 | 15 | 23 | 13.3851 | 2.722 | 0 | GREEN | Primary
4038582 | Elsecar | 11 | 18.75 | 12 | 23 | 8.4439 | 2.6442 | 0.228 | GREEN | Primary
4038583 | Houghton Main | 11 | 12.5 | 10 | 15.3 | 7.6552 | -9.7974 | 0 | GREEN | Primary
7393498 | Kilnhurst | 11 | 30 | 15 | 30 | 16.567 | 3.1248 | 2.7 | GREEN | Primary
4038552 | Tankersley Park | 11 | 18.75 | 15 | 23 | 19.5734 | 4.1542 | 1.28 | GREEN | Primary
4038584 | Wath Upon Dearne | 11 | 30 | 15 | 24 | 13.1587 | 2.9895 | 0 | GREEN | Primary
4038577 | Worsbrough Park | 11 | 18.75 | 15 | 23 | 15.6335 | 3.9364 | 0.293 | GREEN | Primary
4038646 | Barwick | 11 | 23 | 11.5 | 23 | 12.6638 | 2.6634 | 3.366 | GREEN | Primary
4038682 | Ninelands Lane | 11 | 23 | 11.5 | 23 | 13.3931 | 1.5006 | 0.253 | GREEN | Primary
4038642 | Oakwood Lane | 11 | 18.75 | 15 | 23 | 9.9753 | 2.0031 | 0 | GREEN | Primary
4038640 | Roman Avenue | 11 | 18.75 | 15 | 23 | 12.3189 | 2.5266 | 0 | GREEN | Primary
4038644 | Seacroft | 11 | 23 | 11.5 | 23 | 11.0494 | 2.373 | 0.3 | GREEN | Primary
4038645 | Sledmere Garth | 11 | 18.75 | 15 | 23 | 5.2067 | 0.73998 | 3.44 | GREEN | Primary
4038606 | New Droppingwell Road | 11 | 30 | 15 | 25.4 | 9.6571 | 2.057 | 0 | GREEN | Primary
4038566 | Tinsley Park Road | 11 | 24 | 12 | 24 | 17.0853 | 4.1947 | 3.135 | GREEN | Primary
4038829 | Waverley Business Park | 11 | 40 | 20 | 38 | 8.51 | 1.8372 | 10.6 | GREEN | Primary
7208979 | Shepcote Tinsley | 11 | 30 | 15 | 30 | 1.7531 | 0.098664 | 5.09 | GREEN | Primary
4038744 | Belmont Covert | 11 | 24 | 12 | 8 | 3.6206 | 0.18746 | 0 | GREEN | Primary
4038743 | Binbrook | 11 | 7.5 | 7.5 | 7.5 | 1.8496 | 0.10853 | 0 | GREEN | Primary
4038729 | Caistor | 11 | 12 | 12 | 9.5 | 6.4 | 1.7266 | 0 | GREEN | Primary
4038747 | Grainthorpe | 11 | 7.5 | 7.5 | 7.5 | 5.2038 | 1.2826 | 0 | GREEN | Primary
4038811 | Keddington Road | 11 | 25 | 12.5 | 12 | 6.79 | -3.8874 | 0.4 | GREEN | Primary
4038746 | Louth | 11 | 23 | 11.5 | 23 | 19.8664 | 3.8471 | 0 | GREEN | Primary
4038745 | North Thoresby | 11 | 24 | 12 | 8 | 4.2112 | 0.62159 | 0 | GREEN | Primary
4038748 | South Reston | 11 | 24 | 12 | 8 | 3.748 | -2.6738 | 0 | GREEN | Primary
4038820 | Walesby | 11 | 24 | 12 | 8 | 6.06 | 0.80905 | 0 | AMBER | Primary
4038734 | BTP | 11 | 18.75 | 15 | 23 | 15.5727 | 2.8407 | 0 | GREEN | Primary
4038733 | Great Coates | 11 | 23 | 11.5 | 23 | 18.0139 | 2.3521 | 0 | GREEN | Primary
4038735 | Scartho | 11 | 18.75 | 15 | 23 | 19.02 | 1.8007 | 0.82 | GREEN | Primary
4038892 | Yarborough Road 33/11kV | 11 | 24 | 12 | 23 | 13.1116 | 1.253 | 0.25 | GREEN | Primary
4038716 | Alfred Gelder Street | 11 | 24 | 12 | 24 | 13.7504 | 3.1129 | 3.734 | GREEN | Primary
4038712 | Clarendon Street | 11 | 18.75 | 15 | 23 | 15.246 | 5.6185 | 0 | GREEN | Primary
4038706 | County Road North | 11 | 23 | 11.5 | 23 | 15.1037 | 3.748 | 0 | GREEN | Primary
4038705-1 | Hessle Road 1 | 11 | 23 | 11.5 | 23 | 5.9628 | 1.1938 | 1.35 | GREEN | Primary
4038708 | National Avenue | 11 | 24 | 12 | 24 | 7.9662 | 1.1544 | 0 | GREEN | Primary
4038709 | Plangeo | 11 | 24 | 12 | 24 | 14.0412 | 4.5144 | 0.75 | GREEN | Primary
4038710 | West Docks | 11 | 23 | 11.5 | 23 | 13.2987 | 2.9175 | 2.4 | GREEN | Primary
7096989 | Bradford West | 132 | 240 | 240 | 886 | 372.04 | 138.82 | 19.747 | GREEN | GSP
7096969 | Creyke Beck | 132 | 240 | 240 | 886 | 369.67 | 4.05 | 43.494 | GREEN | GSP
7096970 | Drax | 132 | 240 | 240 | 295 | 53.98 | -10.19 | 6.111 | GREEN | GSP
7096999 | Elland | 132 | 240 | 240 | 659 | 299.1 | 76.11 | 32.916 | GREEN | GSP
7097000 | Ferrybridge B | 132 | 240 | 240 | 864 | 222.94 | 13.38 | 28.333 | GREEN | GSP
7096972 | Grimsby West | 132 | 240 | 240 | 295 | 181.36 | 6.597 | 58.324 | GREEN | GSP
7096973 | Keadby | 132 | 240 | 240 | 590 | 278.08 | 12.833 | 18.896 | GREEN | GSP
7096974 | Kirkstall B | 132 | 240 | 240 | 590 | 226.9 | 77.29 | 41.79 | GREEN | GSP
4038880 | Saltend 132/33kV | 33 | 45 | 22.5 | 50.8 | 8.2408 | -6.1468 | 36 | RED | BSP
7096981 | Skelton Grange | 132 | 240 | 240 | 915 | 504.19 | 174.52 | 102.901 | GREEN | GSP
7096988-1 | West Melton / Thorpe Marsh | 132 | 120 | 120 | 696 | 381.4 | -130.31 | 46.526 | GREEN | GSP
7096988-3 | West Melton Section 3 | 132 | 180 | 180 | 418 | 212.2 | 112.39 | 17.391 | GREEN | GSP
7096998 | Camblesforth | 66 | 180 | 180 | 216 | 30.7577 | -100.32 | 20.014 | GREEN | BSP
4038692-66 | Ferrybridge A | 66 | 180 | 180 | 198 | 85.5 | 28.15 | 45.05 | GREEN | BSP
4038899 | Doncaster B/Thorpe Marsh | 66 | 120 | 50 | 223 | 136.3406 | -36.8709 | 24.242 | GREEN | BSP
4038847 | Attercliffe | 33 | 72 | 30 | 69 | 44.9105 | 4.22 | 4.785 | GREEN | BSP
4038848 | Blackburn Meadows B | 33 | 60 | 30 | 78 | 31.1 | -20.9465 | 10.153 | GREEN | BSP
4038851 | Doncaster Central | 33 | 90 | 45 | 117 | 28.6439 | 9.0377 | 1.773 | GREEN | BSP
4038849 | Barugh 132/66kV | 66 | 75 | 37.5 | 98 | 65.06 | 8.2414 | 3.05 | GREEN | BSP
4038850 | Hunningley | 33 | 90 | 45 | 117 | 42.515 | 6.9684 | 0 | GREEN | BSP
4038896 | Hunshelf | 66 | 60 | 30 | 156 | 73.6771 | 22.7375 | 0.75 | GREEN | BSP
4038865 | Wakefield Monckton Road | 33 | 90 | 45 | 117 | 48.93 | 15.3773 | 7.84 | GREEN | BSP
4038852 | West Melton | 66 | 108 | 45 | 141 | 132.6955 | 29.1968 | 5.751 | GREEN | BSP
7096955 | Templeborough 275/33kV | 33 | 75 | 75 | 98 | 27.459 | 1.23 | 0 | GREEN | BSP
4038841 | Bingley 132/33kV | 33 | 90 | 45 | 117 | 52.9149 | 14.4476 | 3.027 | GREEN | BSP
4038834 | Bradford | 33 | 90 | 45 | 117 | 80.7811 | 12.87 | 4.299 | GREEN | BSP
4038833 | Girlington | 33 | 90 | 60 | 117 | 51.44 | 16.8765 | 4.359 | GREEN | BSP
4038842 | Holmfield | 33 | 90 | 45 | 117 | 73.0966 | -2.7725 | 0.8 | GREEN | BSP
4038836 | Menston | 33 | 90 | 45 | 117 | 53.231 | 9.2967 | 1.16 | GREEN | BSP
4038839 | Silsden | 33 | 54 | 22.5 | 108 | 88.1206 | 17.1529 | 3.987 | GREEN | BSP
4038873 | Beverley 132/33kV | 33 | 90 | 45 | 103.5 | 81.2096 | -16.8617 | 9.57 | GREEN | BSP
4038878 | Bransholme | 33 | 90 | 45 | 117 | 44.9292 | 14.3723 | 4.114 | GREEN | BSP
4038872 | Driffield/Beverley Group | 66 | 60 | 30 | 147 | 101.0346 | -5.7028 | 1.72 | GREEN | BSP
4038871 | Hull West | 33 | 108 | 45 | 117 | 49.0817 | 12.5212 | 17.806 | GREEN | BSP
4038874 | Hull South | 33 | 108 | 45 | 117 | 73.5301 | 25.6289 | 8.234 | GREEN | BSP
4038886 | Osgodby 3/4 | 33 | 108 | 45 | 108 | 47.289 | -21.716 | 0 | GREEN | BSP
4038846 | Brighouse 132/33kV | 33 | 90 | 45 | 117 | 67.37 | 18.4679 | 11.72 | GREEN | BSP
4038844 | Lindley | 33 | 90 | 45 | 117 | 66.27 | 16.7927 | 3.64 | GREEN | BSP
4038897 | Sowerby Bridge 132/33kV | 33 | 90 | 45 | 117 | 65.5107 | 4.7234 | 7.943 | GREEN | BSP
4038862 | Thornhill 132kV | 33 | 90 | 45 | 114 | 86.8484 | 7.1729 | 7.474 | GREEN | BSP
4038861 | Bramham | 33 | 90 | 45 | 117 | 63.1307 | 13.7776 | 13.027 | GREEN | BSP
4038868 | Featherstone | 33 | 108 | 45 | 117 | 76.4004 | 26.257 | 2.782 | GREEN | BSP
4038869 | Kirkhaw Lane | 33 | 90 | 45 | 117 | 51.6142 | -31.2667 | 5.165 | GREEN | BSP
4038860 | Whinmoor | 33 | 108 | 45 | 117 | 64.04 | 17.2953 | 7.359 | GREEN | BSP
4038884 | Humberston | 33 | 90 | 45 | 117 | 30.455 | 5.6041 | 2.261 | GREEN | BSP
4038881 | Immingham | 33 | 90 | 45 | 117 | 68.0866 | -19.6441 | 52.683 | RED | BSP
4038883 | Moss Road | 33 | 45 | 22.5 | 59 | 36.567 | 12.4124 | 2.31 | GREEN | BSP
4038882 | Yarborough Road 132/33kV | 33 | 90 | 45 | 117 | 57.3 | 7.2364 | 1.07 | GREEN | BSP
7096996 | Jordanthorpe | 33 | 100 | 100 | 110 | 55.3636 | 12.31 | 3.325 | GREEN | BSP
4038891 | Blyton | 33 | 60 | 30 | 78 | 47.6659 | 6.74 | 0.4 | GREEN | BSP
4038889 | Santon | 33 | 90 | 45 | 117 | 41.5083 | -28.5929 | 4.342 | GREEN | BSP
4038887 | Scunthorpe North | 33 | 108 | 45 | 150 | 96.77 | 3.1405 | 11.342 | GREEN | BSP
4038885 | Wold Newton | 33 | 90 | 45 | 99 | 47.169 | -17.8484 | 0.4 | GREEN | BSP
7096967 | Beeston Royds 132/33kV | 33 | 90 | 45 | 228 | 103.97 | 14.86 | 27.566 | GREEN | BSP
7097003 | Kirkstall C 2/5 | 33 | 90 | 60 | 117 | 74.7629 | 8.2282 | 4.248 | GREEN | BSP
7096975 | Neepsend | 33 | 120 | 120 | 144 | 75.4756 | 22.32 | 7.686 | GREEN | BSP
7096976 | Norton Lees | 33 | 100 | 100 | 110 | 57.6775 | 15.47 | 1.5 | GREEN | BSP
7096977 | Pitsmoor 3/4 | 33 | 100 | 100 | 114 | 46.62 | -18.5 | 12.093 | GREEN | BSP
7096978 | Saltend North | 132 | 180 | 180 | 216 | 98.56 | -15.69 | 170.008 | RED | GSP
4038879 | Hull East 132/33kV | 33 | 108 | 45 | 117 | 57.2671 | 23.3637 | 2.008 | RED | BSP
7096980 | Sheffield City | 33 | 100 | 100 | 114 | 83.63 | 27.87 | 15.477 | GREEN | BSP
4038837 | Heckmondwike | 33 | 90 | 45 | 52 | 48.7419 | 4.15 | 2.114 | AMBER | BSP
4038859 | Leeds East | 33 | 90 | 45 | 117 | 62.7826 | 13.517 | 18.314 | GREEN | BSP
4038858 | Leeds North | 33 | 90 | 45 | 117 | 60.18 | 23.45 | 9.728 | GREEN | BSP
4038900 | Low Road | 33 | 120 | 50 | 228 | 81.8421 | 11.9968 | 43.04 | GREEN | BSP
4038838 | Rodley | 33 | 108 | 45 | 117 | 69.9987 | 18.024 | 6.565 | GREEN | BSP
4038845 | Saint Andrews Road 132/33kV | 33 | 108 | 45 | 71 | 61.9848 | 10.3598 | 3.175 | GREEN | BSP
7240601 | Staygate | 33 | 120 | 80 | 123 | 76.8896 | 13.3787 | 12.441 | GREEN | BSP
4038866 | Wakefield North | 33 | 90 | 45 | 104 | 71.62 | 18.81 | 3.224 | GREEN | BSP
7096994 | Thurcroft | 66 | 180 | 180 | 216 | 125.4524 | 15.34 | 25.77 | GREEN | BSP
7097005 | Wincobank | 33 | 100 | 100 | 130 | 31.7629 | -29.08 | 18.825 | GREEN | BSP
4038661-6 | Beeston Royds 6/7 | 11 | 40 | 20 | 26 | 21.2481 | 5.9984 | 5.9 | RED | Primary
4038705-2 | Hessle Road 2 | 11 | 23 | 11.5 | 23 | 10.6787 | 1.8635 | 0 | GREEN | Primary
4038792-2 | Elmhirst Lane 2 | 11 | 24 | 12 | 24 | 11.5604 | 1.516 | 0 | GREEN | Primary
4038633-2 | Allerton Hill T2 | 11 | 18.75 | 15 | 23 | 7.2117 | 0.29599 | 0 | GREEN | Primary
4038766-2 | Newport 2 | 11 | 24 | 12 | 18.4 | 5.8807 | -1.1938 | 0 | GREEN | Primary
4038888 | Scunthorpe South | 33 | 108 | 45 | 112 | 27.572 | -16.0644 | 2.412 | GREEN | BSP
4038497-2 | Haworth 2 | 11 | 30 | 15 | 30 | 3.6942 | 1.5688 | 0 | GREEN | Primary
7558610 | Halifax 132/33kV | 33 | 60 | 30 | 72 | 38.6401 | 4.5646 | 2.139 | GREEN | BSP
4038894 | Kirkstall C/Ring Road Horsforth | 33 | 90 | 60 | 117 | 75.4093 | 23.3045 | 9.976 | GREEN | BSP
7733114 | Mallard Way | 33 | 144 | 60 | 144 | 36.097 | 7.66 | 3.438 | GREEN | BSP

## Glossary of terms
Column Header | Definition
Substation ID | The unique Heat Map reference number for the substation.
Substation Name | Some locations have more than one substation at the same site. Where this is the case the substation name may contain the voltage or a reference number to differentiate between the substations. There may be some small discrepancies with the substation names used in other publications.
Overall Primary Classification | Red / amber / green indicate the overall likelihood of being able to connect additional generation (or demand for the demand sheets) to this substation without triggering any reinforcement works.
Nominal Voltage (upstream) | Voltage on the higher-voltage side of the transformers at the substation
Nominal Voltage (downstream) | Voltage on the lower-voltage side of the transformers at the substation
Transformer Capacity | The nameplate capacity of the transformer, based on a pre-determined set of environmental conditions associated with the transformer specification. While these values are a useful guide, the actual capability of the transformer will depend on the local environmental conditions and the nature of the load connected to the substation.
OFAF | The forced cooling rating of the transformer. Where the same as ONAN, no forced cooling exists at the site (and it may be possible to uplift the rating through retrofitting fans and pumps). OFAF - Oil Forced Air Forced cooling is utilised here. This rating is usually used during planned or unplanned plant outages, rather than during normal operating conditions and may result in accelerated ageing of the transformer.
ONAN | The natural rating of the transformer under passive cooling i.e. convective circulation of oil and natural airflow over the radiator. Oil Natural Air Natural cooling. This rating is usually used for normal operating conditions when all plant is in service.
Firm Capacity | The capacity that is available at a substation, or within a substation group, to supply demand immediately following the occurrence of a first circuit outage. This shall only include the capacity that is immediately available (or within 60 seconds) after the event without requiring manual intervention. However, at primary substations with only one transformer the supply may be restored within three hours if the overall demand is less than 12MW. The firm capacity only applies to demand and should not be used to infer any capability to accommodate generation.
Demand (Max) | The observed maximum half-hourly average demand being consumed within the substation group. A negative number would mean that the substation exports power out of the group all of the time. The observed power flow may be lower than the total demand within a substation group, due to local generation offsetting demand within the group.
Demand (Min) | The observed minimum half-hourly average demand being consumed within the substation group. A negative number would mean that the substation exports power out of the group for at least some of the time.
Existing Generation Upstream | The summated export capacity of all generation connected to the circuits from the upstream side of this substation to the Grid Supply Point (our point of connection to the GB transmission system). This does not include generation directly connection to the GB transmission system. This excludes any power stations with an agreed export capacity of less than 72kVA
Existing Generation Downstream | The summated export capacity of all generation connected to the downstream voltage of this substation and any other lower voltage network supplied from the substation. This excludes any power stations with an agreed export capacity of less than 72kVA
Fault Level Break (Duty) | Maximum prospective ac rms fault current that the downstream voltage switchgear at the substation is likely to have to interrupt in the event of a symmetrical 3-phase fault, excluding the fault contribution from contracted but not yet connected generation.
Fault Level Break (Rating) | The nameplate current rating of the downstream voltage switchgear at the substation, when it is required to interrupt a 3-phase ac rms fault. The actual capability of the switchgear may be lower due to local network parameters.
Fault Level Make (Duty) | Maximum prospective peak current that the downstream voltage switchgear at the substation is likely to have to carry in the event of the switchgear being closed on to a symmetrical 3-phase fault, excluding the fault contribution from contracted but not yet connected generation.
Fault Level Make (Rating) | The nameplate peak current rating of the downstream voltage switchgear at the substation when it is required to close on to a symmetrical 3-phase fault. The actual capability of the switchgear may be lower due to local network parameters.
Known Constraints (Downstream) | The following columns give an indication of the known issues or limits on the downstream voltage of the substation and network.
Fault Level (%) | This is the worst case of make or break duty, when compared to the fault level rating, expressed as a percentage. Green < 95% >= amber < 99% >= red. It excludes any fault level contribution from contracted but not yet connected generation, which will erode any fault level headroom.
Worst Case Tap Position | Expected lowest tap position on the substation transformer(s), under minimum load and maximum generation. It excludes the impact of contracted but not yet connected generation, which will erode any tap-changer headroom. If the worst case tap position is 1 then it is unlikely that more generation can be connected without carrying out reinforcement.
Reverse Power Flow Capability | Reverse power capability of the substation transformer(s), typically governed by the current carrying capacity of the transformer tap changer.
Downstream Voltage Constraints | An indication of any voltage issues on the downstream network, typically caused by running out of taps on the substation transformer(s). Some voltage constraint = amber Out of taps = red
Local Physical Constraints | This column identifies whether there are any local physical constraints that would make a new connection significantly more expensive. Examples of this could be our ability to extend the substation or to install new circuits in the vicinity of the substation. High physical constraint = red.
Downstream Substation Classification | The classification of the substation when considered independently from the upstream network. In some cases the substation may have a green rating in this column, but the overall classification for the substation will be red due to upstream limitations.
Known Constraints (Upstream) | The following columns give an indication of the known issues or limits on the upstream voltage of the substation and network.
Upstream Voltage Constraints | An indication of any voltage issues on the upstream voltage network, typically caused unacceptable voltage rise, or voltage swing on the upstream network circuits. Some voltage constraint = amber Voltage out of statutory limit = red.
Generation Headroom without reinforcement for New EHV Feeder (MVA) | The maximum cumulative capacity of new generation which could potentially be connected to the upstream voltage side of this substation, subject to detailed design studies, prior to considering issues at the source substation. The total capacity may not be achievable as a single site due to voltage swing limitations and will vary depending on the location of the generation along the upstream circuit.
Generation Headroom without reinforcement for New Substation (MVA) | The maximum cumulative capacity of new generation which could potentially be connected to the downstream voltage side of this substation, subject to detailed design studies. The total capacity might not be achievable at a single power station site due to voltage swing limitations.
NGESO Statement of Works Threshold (MVA) | The amount of generation that may be contracted before a Statement of Works is required from National Grid. A Statement of Works may identify that additional works or constraints of operation are required to mitigate any impact on the GB transmission system.
Upstream Constraint Levels (NPg/NGET) (MVA) | What is the available capacity remaining before either, reinforcements are required or before a Statement of Works is required, whichever is the lower.
Upstream Substation Classification | The classification of the upstream voltage at the substation when considered independently from the downstream voltage at the substation. In some cases the substation may have a green rating in this column, indicating that generation can be connected at the upstream voltage, but there might be no generation capacity at the downstream voltage for smaller power stations.
Is this an Active Network Management (ANM) area? | Generation wishing to connect in an ANM area will be subject to some degree of active constraint based on real-time network loadings. Customers may opt to receive an unconstrained connection offer, but this would include reinforcement works that are generally prohibitively expensive.
Quoted Generation Connections (kW) | The summated capacity of valid connection offers to connect to the downstream voltage of the substation. This does not include offers that have been accepted or have lapsed.
Valid Until: | The latest expiry date of any of the valid connection offers.
Number of Valid Quotes | The number of valid connection offers to connect to the downstream voltage of the substation. This does not include offers that have been accepted or have lapsed.
Contracted Generation Connections (kW) | The summated capacity of all accepted connection offers that are not yet connected to the downstream voltage of the substation.
Number of Accepted Quotes | The number of accepted connection offers that are not yet connected to the downstream voltage of the substation. Field not yet implemented for demand schemes.
Related Substations (Upstream) | The ID number of the upstream substation. Where the substation connects directly to the GB transmission system or to another DNO network, the name of the network operator is given.
Related Substations (Downstream) | The ID number of the downstream substations.
Substation Class: GSP, BSP or Primary | The class of substation. Typically, the substations are classified as follows (however 132/11kV sites are classed as BSPs): Primary: downstream voltage of <25kV BSP: downstream voltage of 33kV or 66kV (or in one case 20kV) GSP: downstream voltage of 132kV

## Thresholds
Read Me
You can find further assistance on the use of the heat maps from our |  | webinar
The tables below show the parameters that define the Red / Amber / Green classifications
Please contact us if you require any assistance | email

## ANM
Active Network Management
There is a generation Active Network Management (ANM) scheme which has been developed and deployed within the Driffield area. This is a standardised product that can be efficiently rolled out elsewhere as and when required. The Driffield ANM scheme manages the export from a number of generators to ensure that the power flows within the Driffield 66kV network and the local 132kV network remain within their design limits. We have identified the following areas as approaching their export capability limits: • Keadby GSP (Scunthorpe and surrounding area); • Grimsby West GSP (Grimsby and Cleethorpes); and • Creyke Beck GSP and Saltend North GSP (Hull and surrounding area). These areas have been approved for the roll-out of ANM, which will enable us to continue to connect generation in the areas without triggering significant connection reinforcement costs. We are now actively making ANM connection offers to generation customers wishing to connect to Keadby and will do likewise in the other areas as and when the trigger point for ANM is reached.

## SoW & Appendix G - Northeast
SoW & Appendix G Table - Northeast - Correct as 28/05/2024
Primary Substation | Supply Point | Grid Supply Point | SoW/Appendix G? | NGESO Statement of Works or Appendix G Threshold (MW) | NGESO Statement of Works or Appendix G Remaining Threshold (MW) - Headroom | Specific Customer Requirements (Appendix G only) - see below for fuller details regarding each Conditon
- | - | Blyth 132kV | Appendix G | 10 | < 1.0 | -
- | Linton | Blyth 132kV | Appendix G | 10 | < 1.0 | -
- | Linton | Blyth 132kV | Appendix G | 10 | < 1.0 | -
Denwick | Linton | Blyth 132kV | Appendix G | 10 | < 1.0 | -
Linton 66/20kV | Linton | Blyth 132kV | Appendix G | 10 | < 1.0 | -
Lynemouth | Linton | Blyth 132kV | Appendix G | 10 | < 1.0 | -
Warkworth | Linton | Blyth 132kV | Appendix G | 10 | < 1.0 | -
- | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Ashington | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Benton Square | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Cramlington T1 T3 | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Cramlington T2 T4 | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Fawdon T1 | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Maddison Street | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Morpeth | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Reservoir | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Seaton Burn T1 | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Seghill | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
Wansbeck | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
West Hartford | Blyth 66kV | Blyth 66kV | Appendix G | 10 | < 1.0 | -
- | Fourstones 20kV | Fourstones | SoW | 15 | 11.6 | -
- | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
Amberton Road | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
Brenda Trading | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
Hartmoor 66/20kV | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
Peterlee West | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
Wynyard | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
Wynyard Data | Hartmoor | Hartmoor | Appendix G | 50 | < 1.0 | -
- | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
Hawthorn Pit | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
Houghton | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
Peterlee Industrial | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
Shotton | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
Stoney Cut | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
Tunstall | Hawthorn Pit Grid | Hawthorn Pit Grid | Appendix G | 50 | < 1.0 | -
- | - | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Harrogate 132/11kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Harrogate 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Harrogate West | Harrogate 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Oatlands | Harrogate 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Starbeck | Harrogate 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Husthwaite | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Husthwaite 33/11kV | Husthwaite | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Sessay Bridge | Husthwaite | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Sowerby | Husthwaite | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Wormald Green 132/11kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Wormald Green 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Boroughbridge | Wormald Green 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Coneythorpe | Wormald Green 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Darley | Wormald Green 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Ripon | Wormald Green 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Roecliffe Industrial | Wormald Green 132/33kV | Knaresborough | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
Carlin How T3 T4 | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
Grangetown | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
Guisborough T1 T2 | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
Prissick | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
Redcar | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
Spencerbeck | Lackenby | Lackenby | Appendix G | 15 | < 1.0 | -
- | - | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Acklam | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Bowesfield 33/11kV | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Millbank Lane | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Rudby | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Stokesley | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Urlay Nook | Bowesfield | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Darlington 132/6kV | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Darlington Central | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Cowton | Darlington Central | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Darlington 33/11kV | Darlington Central | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Darlington Central 33/11kV | Darlington Central | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Darlington East | Darlington Central | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Aycliffe Forrest | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Aycliffe Industrial | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Darlington West | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Heighington | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Newton Aycliffe South | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Richmond T2 | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Rise Carr | Darlington North | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Leeming Bar | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Barden Friar | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Bedale | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Catterick Camp | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Hipswell | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Northallerton | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Richmond T1 | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Romanby | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Thirsk | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Wensleydale | Leeming Bar/Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Billingham Marsh House | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Bowesfield 66/11kV | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Faraday Street | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Haverton Generation | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Haverton Incinerator | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
Malleable | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
North Tees T1 T2 | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
North Tees T3 T4 | North Tees | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Norton 132/11kV | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Skeeby | Norton | Appendix G | 0 | < 1.0 | Condition 1 & Condition 2
- | Offerton | Offerton | SoW | 50 | 48.1 | -
Mount Road | Offerton | Offerton | SoW | 50 | 48.1 | -
Offerton 33/11kV | Offerton | Offerton | SoW | 50 | 48.1 | -
Pallion Trading | Offerton | Offerton | SoW | 50 | 48.1 | -
- | - | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Kirbymoorside | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Malton | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Scarborough 66/11kV | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Sheriff Hutton | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Thornton Dale | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Whitby T2 | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Whitby West T2 | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Yedingham | Malton Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Campleshon Road | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Elvington | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Foss Islands | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Haxby Road T2 T3 | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Huntington New Lane | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Melrosegate 33/11kV | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Rawcliffe Lane | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
York University | Melrosegate | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Eastfield | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Newby | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
North Street | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Ravenscar | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Scarborough 33/11kV | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Whitby T1 | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Whitby West T1 | Scarborough Grid | Osbaldwick | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | - | Poppleton | SoW | 50 | < 1.0 | -
Gale Lane | Poppleton | Poppleton | SoW | 50 | < 1.0 | -
Moor Monkton Pumps | Poppleton | Poppleton | SoW | 50 | < 1.0 | -
Severus Hill | Poppleton | Poppleton | SoW | 50 | < 1.0 | -
Skeldergate | Poppleton | Poppleton | SoW | 50 | < 1.0 | -
- | - | Saltholme | Appendix G | 50 | < 1.0 | -
- | Greatham | Saltholme | Appendix G | 50 | < 1.0 | -
- | North Bank | Saltholme | Appendix G | 50 | < 1.0 | -
Tees Industrial T1 T2 | Seal Sands | Saltholme | Appendix G | 50 | < 1.0 | -
| Seal Sands | Saltholme | Appendix G | 50 | < 1.0 | -
- | - | South Shields | SoW | 50 | 15 | -
Garwood Street | South Shields | South Shields | SoW | 50 | 15 | -
Jarrow | South Shields | South Shields | SoW | 50 | 15 | -
Simonside | South Shields | South Shields | SoW | 50 | 15 | -
Westoe | South Shields | South Shields | SoW | 50 | 15 | -
- | - | Spadeadam | SoW | 1 | < 1.0 | This site is connected to a third party network and as such a 1 MW threshold has been applied.
- | Spadeadam 20kV | Spadeadam | SoW | 1 | < 1.0
Kielder | Spadeadam 33kV | Spadeadam | SoW | 1 | < 1.0
| Spadeadam 33kV | Spadeadam | SoW | 1 | < 1.0
- | - | Spennymoor GSP | SoW | 50 | < 1.0 | -
- | Potter House | Spennymoor GSP | SoW | 50 | < 1.0 | -
Belmont | Potter House | Spennymoor GSP | SoW | 50 | < 1.0 | -
Durham East | Potter House | Spennymoor GSP | SoW | 50 | < 1.0 | -
High Flatts | Potter House | Spennymoor GSP | SoW | 50 | < 1.0 | -
Potter House T1 T3 | Potter House | Spennymoor GSP | SoW | 50 | < 1.0 | -
Potter House T4 T5 | Potter House | Spennymoor GSP | SoW | 50 | < 1.0 | -
- | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
Brancepeth | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
Fishburn | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
Low Spennymoor | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
Meadowfield | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
Skerneside | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
Spennymoor 66/20kV | Spennymoor | Spennymoor GSP | SoW | 50 | < 1.0 | -
- | Toronto | Spennymoor GSP | SoW | 50 | < 1.0 | -
Eastgate Cement | Toronto | Spennymoor GSP | SoW | 50 | < 1.0 | -
Fylands Bridge | Toronto | Spennymoor GSP | SoW | 50 | < 1.0 | -
Harmire Bridge | Toronto | Spennymoor GSP | SoW | 50 | < 1.0 | -
Toronto 66/20kV | Toronto | Spennymoor GSP | SoW | 50 | < 1.0 | -
- | - | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Barrack Road | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Corporation Street | Barrack Road | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Educational Precinct | Barrack Road | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Gateshead Central | Barrack Road | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Pilgrim | Barrack Road | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
University | Barrack Road | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Blucher | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Blucher 33/11kV | Blucher | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Kenton | Blucher | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Newcastle Airport | Blucher | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Westerhope | Blucher | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Bensham | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Benwell | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Blaydon Burn | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Close | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Dunston 66/11kV | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
Dunston 66/20kV | Dunston | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | Newburn Haugh | Stella North | Appendix G | 50 | < 1.0 | Condition 1 & Condition 2
- | - | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
- | Annfield | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Annfield 66/20kV | Annfield | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Consett | Annfield | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Tanfield | Annfield | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
- | Coalburns | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Hexham | Coalburns | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
West Wylam | Coalburns | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
- | Harraton | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
- | Ravensworth | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Birtley Grove 66/11kV | Ravensworth | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Birtley Grove 66/20kV | Ravensworth | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
Team Valley | Ravensworth | Stella South | Appendix G | 25 | < 1.0 | Condition 1 & Condition 2
- | - | Tynemouth | SoW | 50 | < 1.0 | -
- | Chirton Grange | Tynemouth | SoW | 50 | < 1.0 | -
Billy Mill | Chirton Grange | Tynemouth | SoW | 50 | < 1.0 | -
Monkseaton | Chirton Grange | Tynemouth | SoW | 50 | < 1.0 | -
Tynemouth Central | Chirton Grange | Tynemouth | SoW | 50 | < 1.0 | -
- | Flatworth | Tynemouth | SoW | 50 | < 1.0 | -
Flatworth Central | Flatworth | Tynemouth | SoW | 50 | < 1.0 | -
Howdon | Flatworth | Tynemouth | SoW | 50 | < 1.0 | -
Willington | Flatworth | Tynemouth | SoW | 50 | < 1.0 | -
- | Gosforth | Tynemouth | SoW | 50 | < 1.0 | -
Fossway 33/11kV | Gosforth | Tynemouth | SoW | 50 | < 1.0 | -
Gosforth 33/11kV | Gosforth | Tynemouth | SoW | 50 | < 1.0 | -
Killingworth | Gosforth | Tynemouth | SoW | 50 | < 1.0 | -
Longbenton | Gosforth | Tynemouth | SoW | 50 | < 1.0 | -
- | - | West Boldon | SoW | 50 | < 1.0 | -
Boldon Downhill | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Breamish Street | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Carley Hill | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Carr Hill | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Gateshead East | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Harlow Green | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Hebburn | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Hebburn West | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Hedworth | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
High Barmston | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Leam Central | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Sunderland T1 T2 | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Sunderland T5 T6 | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Temple Park | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Usworth | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Walker | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Wardley | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
West Southwick | West Boldon | West Boldon | SoW | 50 | < 1.0 | -
Condition 1: Voltage Regulation at a Grid Supply Point In accordance with the ENA Engineering Recommendation G99, the Embedded Power Station shall be capable of operating throughout the power factor range of: (i) 0.92 lagging to 0.92 leading for a synchronous Power Generator Module; and (ii) 0.95 lagging to 0.95 leading for a Power Park Module. However the generator shall operate at a fixed reactive import setting (lead power factor) to offset the susceptance of the dedicated connection cable to ensure that there is no net increase of reactive power export at the Grid Supply Point. This reactive power import shall be maintained at all times irrespective of whether or not the generator is in operation.
Condition 2: Emergency Tripping Instructions Northern Powergrid will require the capability to remotely switch off embedded power stations with a connection voltage greater than 25kV under emergency conditions and following a direct instruction from NGESO to de-energise excess generation. This will be a very rare event and will be achieved by remotely issuing a tripping signal to the generator metering circuit breaker or synchronising circuit breaker, the details of which shall be agreed between Northern Powergrid and the customer.
Notes The values in the table above detail the available headroom (before a Statement of Works is required) as at the 28th May 2024, this could be further eroded by any customers who have accepted connection offers since the 28th May 2024. If the proposed size of any new connection is greater than the available headroom (as detailed in the table above), we will be required to submit a “Modification Application” (ModApp) to NGESO who will identify if any works are required on the transmission network to facilitate this connection. Customers who trigger this “ModApp” process may be subject to additional charges.

## SoW & Appendix G - Yorkshire
SoW & Appendix G Table - Yorkshire - Correct as at 28/05/2024
Primary Substation | Supply Point | Grid Supply Point | SoW/Appendix G? | NGESO Statement of Works or Appendix G Threshold (MW) | NGESO Statement of Works or Appendix G Remaining Threshold (MW) - Headroom | Specific Customer Requirements (Appendix G only) - see below for fuller details regarding each Conditon
- | - | Bradford West | SoW | 50 | < 1.0 | -
- | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
Airedale Road | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
Bingley 33/11kV | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
Harden | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
Haworth 1 | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
Nabwood | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
South Street | Bingley 132/33kV | Bradford West | SoW | 50 | < 1.0 | -
- | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Balme Street | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Gaisby Lane | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Idle | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Killinghall Road | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Manchester Road | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Moorside Road | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Mount Street | Bradford | Bradford West | SoW | 50 | < 1.0 | -
Shipley | Bradford | Bradford West | SoW | 50 | < 1.0 | -
- | Girlington | Bradford West | SoW | 50 | < 1.0 | -
Crown Street | Girlington | Bradford West | SoW | 50 | < 1.0 | -
Four Lane Ends | Girlington | Bradford West | SoW | 50 | < 1.0 | -
Legrams Mill Lane | Girlington | Bradford West | SoW | 50 | < 1.0 | -
Rawson Road | Girlington | Bradford West | SoW | 50 | < 1.0 | -
Saint Street | Girlington | Bradford West | SoW | 50 | < 1.0 | -
Toller Lane | Girlington | Bradford West | SoW | 50 | < 1.0 | -
- | Holmfield | Bradford West | SoW | 50 | < 1.0 | -
Denholme | Holmfield | Bradford West | SoW | 50 | < 1.0 | -
Furness Avenue | Holmfield | Bradford West | SoW | 50 | < 1.0 | -
Gibraltar Road | Holmfield | Bradford West | SoW | 50 | < 1.0 | -
Queensbury | Holmfield | Bradford West | SoW | 50 | < 1.0 | -
Thornton | Holmfield | Bradford West | SoW | 50 | < 1.0 | -
- | Keighley | Bradford West | SoW | 50 | < 1.0 | -
- | Menston | Bradford West | SoW | 50 | < 1.0 | -
Bramhope | Menston | Bradford West | SoW | 50 | < 1.0 | -
Chevin End | Menston | Bradford West | SoW | 50 | < 1.0 | -
Hallam Street | Menston | Bradford West | SoW | 50 | < 1.0 | -
Kirk Drive | Menston | Bradford West | SoW | 50 | < 1.0 | -
North Avenue | Menston | Bradford West | SoW | 50 | < 1.0 | -
Pool | Menston | Bradford West | SoW | 50 | < 1.0 | -
- | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Barnoldswick | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Bolton Road | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Chelker Reservoir | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Cracoe | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Crosshills | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Haworth 2 | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Ilkley | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Ings Lane | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Salterforth | Silsden | Bradford West | SoW | 50 | < 1.0 | -
Skipton | Silsden | Bradford West | SoW | 50 | < 1.0 | -
- | Camblesforth | Camblesforth | SoW | 1 | < 1.0 | -
Crowle | Camblesforth | Camblesforth | SoW | 1 | < 1.0 | -
Drax Primary | Camblesforth | Camblesforth | SoW | 1 | < 1.0 | -
Goole | Camblesforth | Camblesforth | SoW | 1 | < 1.0 | -
Guardian Glass | Camblesforth | Camblesforth | SoW | 1 | < 1.0 | -
Rawcliffe | Camblesforth | Camblesforth | SoW | 1 | < 1.0 | -
- | - | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Endike Lane | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
First Avenue | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Holme Upon Spalding Moor | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Norwood | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Southgate | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Southwood Road | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Spark Mill Lane | Beverley 132/33kV | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Bransholme | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Holderness | Bransholme | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Saltshouse Road | Bransholme | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Tiverton Road | Bransholme | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Wawne Road | Bransholme | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Cornwall Street | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Belthorpe Lane | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Brett Street | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Burton Pidsea | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Butterwick | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Driffield | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Hayton | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Hunmanby | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Kirkburn | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Martongate | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Sandhill Lane | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Seaton | Driffield/Beverley Group | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Alfred Gelder Street | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Clarendon Street | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
County Road North | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Hessle Road 1 | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
National Avenue | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Plangeo | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
West Docks | Hull South | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Hull West | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Elgar Road | Hull West | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Gibson Lane | Hull West | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Hessle Road 2 | Hull West | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Newport 1 | Hull West | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
Skillings Lane | Hull West | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | Sculcoates A | Creyke Beck | Appendix G | 1 | < 1.0 | Condition 1 & Condition 2
- | - | Drax | SoW | 25 | < 1.0 | -
- | Osgodby 1/2 | Drax | SoW | 25 | < 1.0 | -
- | Osgodby 3/4 | Drax | SoW | 25 | < 1.0 | -
Newport 2 | Osgodby 3/4 | Drax | SoW | 25 | < 1.0 | -
Olympia Mills | Osgodby 3/4 | Drax | SoW | 25 | < 1.0 | -
Selby | Osgodby 3/4 | Drax | SoW | 25 | < 1.0 | -
Thorpe Road | Osgodby 3/4 | Drax | SoW | 25 | < 1.0 | -
- | - | Elland | SoW | 50 | 38.216 | -
- | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Bailiff Bridge | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Brighouse 33/11kV | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Deighton | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Lowfields | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Millroyd Street | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Snelsins Lane | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
Spenborough | Brighouse 132/33kV | Elland | SoW | 50 | 38.216 | -
- | Halifax 132/33kV | Elland | SoW | 50 | 38.216 | -
Halifax 33/11kV | Halifax 132/33kV | Elland | SoW | 50 | 38.216 | -
Swan Bank Lane | Halifax 132/33kV | Elland | SoW | 50 | 38.216 | -
- | Lindley | Elland | SoW | 50 | 38.216 | -
Dowker Street | Lindley | Elland | SoW | 50 | 38.216 | -
Grove Street | Lindley | Elland | SoW | 50 | 38.216 | -
Honley | Lindley | Elland | SoW | 50 | 38.216 | -
Meltham | Lindley | Elland | SoW | 50 | 38.216 | -
Oakes Road | Lindley | Elland | SoW | 50 | 38.216 | -
Prospect Road | Lindley | Elland | SoW | 50 | 38.216 | -
Slaithwaite | Lindley | Elland | SoW | 50 | 38.216 | -
- | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
Elland 33/11kV | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
Hebden Bridge | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
Mytholmroyd | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
Salterhebble | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
Sowerby Bridge 33/11kV | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
Todmorden | Sowerby Bridge 132/33kV | Elland | SoW | 50 | 38.216 | -
- | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Batley | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Calder Wharf | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Denby Grange | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Hazlehead | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Horbury | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Mirfield | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Park Road | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
Scholes | Thornhill 132kV | Elland | SoW | 50 | 38.216 | -
- | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
Eggborough | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
Ferrybridge A 11kV | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
Grimethorpe | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
Hemsworth | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
Ledston | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
Monckton | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
South Elmsall | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
South Kirkby | Ferrybridge A | Ferrybridge A | SoW | 50 | < 1.0 | -
- | - | Ferrybridge B | SoW | 50 | < 1.0 | -
- | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Audby Lane | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Dunkeswick | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Fenton Lane | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Leeds Road | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Sherburn | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Tadcaster | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
Warren Lane | Bramham | Ferrybridge B | SoW | 50 | < 1.0 | -
- | Featherstone | Ferrybridge B | SoW | 50 | < 1.0 | -
Commonside Lane | Featherstone | Ferrybridge B | SoW | 50 | < 1.0 | -
Normanton | Featherstone | Ferrybridge B | SoW | 50 | < 1.0 | -
Prince of Wales | Featherstone | Ferrybridge B | SoW | 50 | < 1.0 | -
Sharlston | Featherstone | Ferrybridge B | SoW | 50 | < 1.0 | -
Wellington Street | Featherstone | Ferrybridge B | SoW | 50 | < 1.0 | -
- | Kirkhaw Lane | Ferrybridge B | SoW | 50 | < 1.0 | -
Beal | Kirkhaw Lane | Ferrybridge B | SoW | 50 | < 1.0 | -
Carr Lane | Kirkhaw Lane | Ferrybridge B | SoW | 50 | < 1.0 | -
Pollington | Kirkhaw Lane | Ferrybridge B | SoW | 50 | < 1.0 | -
Smith Street | Kirkhaw Lane | Ferrybridge B | SoW | 50 | < 1.0 | -
Weeland Road | Kirkhaw Lane | Ferrybridge B | SoW | 50 | < 1.0 | -
- | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
Barwick | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
Ninelands Lane | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
Oakwood Lane | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
Roman Avenue | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
Seacroft | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
Sledmere Garth | Whinmoor | Ferrybridge B | SoW | 50 | < 1.0 | -
- | - | Grimsby West | SoW | 50 | < 1.0 | -
- | Humberston | Grimsby West | SoW | 50 | < 1.0 | -
Convamore Road | Humberston | Grimsby West | SoW | 50 | < 1.0 | -
Conyard Road | Humberston | Grimsby West | SoW | 50 | < 1.0 | -
Wesley Crescent | Humberston | Grimsby West | SoW | 50 | < 1.0 | -
- | Immingham | Grimsby West | SoW | 50 | < 1.0 | -
Barrow | Immingham | Grimsby West | SoW | 50 | < 1.0 | -
Clough Lane | Immingham | Grimsby West | SoW | 50 | < 1.0 | -
Eastfield Road | Immingham | Grimsby West | SoW | 50 | < 1.0 | -
Humber Road | Immingham | Grimsby West | SoW | 50 | < 1.0 | -
Queens Road | Immingham | Grimsby West | SoW | 50 | < 1.0 | -
- | Moss Road | Grimsby West | SoW | 50 | < 1.0 | -
Doughty Road | Moss Road | Grimsby West | SoW | 50 | < 1.0 | -
Grimsby Docks | Moss Road | Grimsby West | SoW | 50 | < 1.0 | -
Marsden Road | Moss Road | Grimsby West | SoW | 50 | < 1.0 | -
- | Yarborough Road 132/33kV | Grimsby West | SoW | 50 | < 1.0 | -
BTP | Yarborough Road 132/33kV | Grimsby West | SoW | 50 | < 1.0 | -
Great Coates | Yarborough Road 132/33kV | Grimsby West | SoW | 50 | < 1.0 | -
Scartho | Yarborough Road 132/33kV | Grimsby West | SoW | 50 | < 1.0 | -
Yarborough Road 33/11kV | Yarborough Road 132/33kV | Grimsby West | SoW | 50 | < 1.0 | -
- | Jordanthorpe | Jordanthorpe | SoW | 50 | 50 | -
Baslow Road | Jordanthorpe | Jordanthorpe | SoW | 50 | 50 | -
Dronfield | Jordanthorpe | Jordanthorpe | SoW | 50 | 50 | -
Greenhill | Jordanthorpe | Jordanthorpe | SoW | 50 | 50 | -
Millhouses | Jordanthorpe | Jordanthorpe | SoW | 50 | 50 | -
Woodseats | Jordanthorpe | Jordanthorpe | SoW | 50 | 50 | -
- | - | Keadby | SoW | 1 | < 1.0 | -
- | Blyton | Keadby | SoW | 1 | < 1.0 | -
Corringham Road | Blyton | Keadby | SoW | 1 | < 1.0 | -
Epworth | Blyton | Keadby | SoW | 1 | < 1.0 | -
Harpswell | Blyton | Keadby | SoW | 1 | < 1.0 | -
Haxey | Blyton | Keadby | SoW | 1 | < 1.0 | -
Lea Road | Blyton | Keadby | SoW | 1 | < 1.0 | -
Normanby | Blyton | Keadby | SoW | 1 | < 1.0 | -
Stow | Blyton | Keadby | SoW | 1 | < 1.0 | -
- | Santon | Keadby | SoW | 1 | < 1.0 | -
Firth Brown | Santon | Keadby | SoW | 1 | < 1.0 | -
Hibaldstow | Santon | Keadby | SoW | 1 | < 1.0 | -
Pasture Road South | Santon | Keadby | SoW | 1 | < 1.0 | -
South Ferriby | Santon | Keadby | SoW | 1 | < 1.0 | -
Wrawby | Santon | Keadby | SoW | 1 | < 1.0 | -
- | Scunthorpe North | Keadby | SoW | 1 | < 1.0 | -
Billet Lane | Scunthorpe North | Keadby | SoW | 1 | < 1.0 | -
Flixborough | Scunthorpe North | Keadby | SoW | 1 | < 1.0 | -
Foxhills | Scunthorpe North | Keadby | SoW | 1 | < 1.0 | -
Station Road | Scunthorpe North | Keadby | SoW | 1 | < 1.0 | -
- | Scunthorpe South | Keadby | SoW | 1 | < 1.0 | -
Bottesford | Scunthorpe South | Keadby | SoW | 1 | < 1.0 | -
Bridges Road | Scunthorpe South | Keadby | SoW | 1 | < 1.0 | -
- | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Belmont Covert | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Binbrook | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Caistor | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Grainthorpe | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Keddington Road | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Louth | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
North Thoresby | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
South Reston | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
Walesby | Wold Newton | Keadby | SoW | 1 | < 1.0 | -
- | - | Kirkstall B | SoW | 50 | < 1.0 | -
- | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Beeston Royds 33/11kV | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Beeston Royds 6/7 | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Gildersome | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Hedley Chase | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Middleton Town Street | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Morley | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Tingley | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
Whitehall Road 4/5 | Beeston Royds 132/33kV | Kirkstall B | SoW | 50 | < 1.0 | -
- | Kirkstall C 2/5 | Kirkstall B | SoW | 50 | < 1.0 | -
Burley Street | Kirkstall C 2/5 | Kirkstall B | SoW | 50 | < 1.0 | -
Clarendon Road | Kirkstall C 2/5 | Kirkstall B | SoW | 50 | < 1.0 | -
Upper Basinghall Street | Kirkstall C 2/5 | Kirkstall B | SoW | 50 | < 1.0 | -
- | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
Abbey Road | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
Bramley | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
Farnley Crescent | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
Fir Tree Lane | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
Iveson House | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
West Park | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
Whingate | Kirkstall C/Ring Road Horsforth | Kirkstall B | SoW | 50 | < 1.0 | -
- | Neepsend | Neepsend | SoW | 50 | 50 | -
Blue Boy Street | Neepsend | Neepsend | SoW | 50 | 50 | -
Claywheels Lane | Neepsend | Neepsend | SoW | 50 | 50 | -
Crookesmoor Road | Neepsend | Neepsend | SoW | 50 | 50 | -
Loxley Road | Neepsend | Neepsend | SoW | 50 | 50 | -
Penistone Road | Neepsend | Neepsend | SoW | 50 | 50 | -
Rawson Spring Road | Neepsend | Neepsend | SoW | 50 | 50 | -
Stannington Road | Neepsend | Neepsend | SoW | 50 | 50 | -
- | Norton Lees | Norton Lees | SoW | 50 | 50 | -
Gleadless Valley | Norton Lees | Norton Lees | SoW | 50 | 50 | -
Marmion Road | Norton Lees | Norton Lees | SoW | 50 | 50 | -
Norfolk Park | Norton Lees | Norton Lees | SoW | 50 | 50 | -
Saxon Road | Norton Lees | Norton Lees | SoW | 50 | 50 | -
Snaithing Park Road | Norton Lees | Norton Lees | SoW | 50 | 50 | -
- | Pitsmoor 3/4 | Pitsmoor 3/4 | SoW | 50 | 20 | -
Barnsley Road | Pitsmoor 3/4 | Pitsmoor 3/4 | SoW | 50 | 20 | -
Bellhouse Road | Pitsmoor 3/4 | Pitsmoor 3/4 | SoW | 50 | 20 | -
Newhall Road | Pitsmoor 3/4 | Pitsmoor 3/4 | SoW | 50 | 20 | -
Stanley Street | Pitsmoor 3/4 | Pitsmoor 3/4 | SoW | 50 | 20 | -
Stevenson Road | Pitsmoor 3/4 | Pitsmoor 3/4 | SoW | 50 | 20 | -
- | - | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
- | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Easington | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Hedon Road | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Hull East 33/11kV | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
King George Dock | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Ottringham Road | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Patrington Road | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Westcott Street | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Withernsea | Hull East 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
- | Saltend 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Ellifoot Lane | Saltend 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
Yorkshire Water Hull Road | Saltend 132/33kV | Saltend North | Appendix G | 50 | 21.3 | Condition 1 & Condition 2
- | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Arundel Street | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Ellin Street 1/3 | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Ellin Street 2 | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Mansfield Road 1 | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Park Hill | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Silver Street | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
Victoria Street | Sheffield City | Sheffield City | SoW | 50 | 41.35 | -
- | - | Skelton Grange | SoW | 50 | < 1.0 | -
- | Heckmondwike | Skelton Grange | SoW | 50 | < 1.0 | -
Burnleyville | Heckmondwike | Skelton Grange | SoW | 50 | < 1.0 | -
Liversedge | Heckmondwike | Skelton Grange | SoW | 50 | < 1.0 | -
Nab Lane | Heckmondwike | Skelton Grange | SoW | 50 | < 1.0 | -
White Lee | Heckmondwike | Skelton Grange | SoW | 50 | < 1.0 | -
- | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
Allerton Hill T1 | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
Burmantofts | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
Hillcrest | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
Knostrop | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
Pontefract Lane 1/2 | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
Selby Road | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
York Road | Leeds East | Skelton Grange | SoW | 50 | < 1.0 | -
- | Leeds North | Skelton Grange | SoW | 50 | < 1.0 | -
Allerton Hill T2 | Leeds North | Skelton Grange | SoW | 50 | < 1.0 | -
Buslingthorpe Green | Leeds North | Skelton Grange | SoW | 50 | < 1.0 | -
Carlton Hill | Leeds North | Skelton Grange | SoW | 50 | < 1.0 | -
Leylands Road | Leeds North | Skelton Grange | SoW | 50 | < 1.0 | -
Moor Road | Leeds North | Skelton Grange | SoW | 50 | < 1.0 | -
- | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Armouries Drive | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Brookfield Street | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Clarence Road | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Holbeck | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Leasowe Road | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Pontefract Lane 3 | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Stourton 33/11kV | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Sweet Street | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
Whitehall Road 2/3 | Low Road | Skelton Grange | SoW | 50 | < 1.0 | -
- | Rodley | Skelton Grange | SoW | 50 | < 1.0 | -
Rawdon | Rodley | Skelton Grange | SoW | 50 | < 1.0 | -
Rodley Lane | Rodley | Skelton Grange | SoW | 50 | < 1.0 | -
Swinnow Moor | Rodley | Skelton Grange | SoW | 50 | < 1.0 | -
Thornbury | Rodley | Skelton Grange | SoW | 50 | < 1.0 | -
Varley Street | Rodley | Skelton Grange | SoW | 50 | < 1.0 | -
- | Saint Andrews Road 132/33kV | Skelton Grange | SoW | 50 | < 1.0 | -
Birkby | Saint Andrews Road 132/33kV | Skelton Grange | SoW | 50 | < 1.0 | -
Dalton | Saint Andrews Road 132/33kV | Skelton Grange | SoW | 50 | < 1.0 | -
Folly Hall | Saint Andrews Road 132/33kV | Skelton Grange | SoW | 50 | < 1.0 | -
Saint Andrews Road 33/11kV | Saint Andrews Road 132/33kV | Skelton Grange | SoW | 50 | < 1.0 | -
Yew Green Road | Saint Andrews Road 132/33kV | Skelton Grange | SoW | 50 | < 1.0 | -
- | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
Dudley Hill | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
Low Moor | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
Odsal | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
Spring Mill Street | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
Tong Street | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
Wibsey | Staygate | Skelton Grange | SoW | 50 | < 1.0 | -
- | Stourton 132/11kV | Skelton Grange | SoW | 50 | < 1.0 | -
- | Wakefield North | Skelton Grange | SoW | 50 | < 1.0 | -
Alverthorpe Road | Wakefield North | Skelton Grange | SoW | 50 | < 1.0 | -
Kenmore Road | Wakefield North | Skelton Grange | SoW | 50 | < 1.0 | -
Milton Place | Wakefield North | Skelton Grange | SoW | 50 | < 1.0 | -
Outwood | Wakefield North | Skelton Grange | SoW | 50 | < 1.0 | -
Royds Lane | Wakefield North | Skelton Grange | SoW | 50 | < 1.0 | -
- | Templeborough 275/33KV | Templeborough 275/33kV | SoW | 1 | < 1.0 | This site is connected to a third party network and as such a 1 MW threshold has been applied.
Fullerton Road | Templeborough 275/33KV | Templeborough 275/33kV | SoW | 1 | < 1.0
- | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Beighton | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Costhorpe | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Dinnington | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Edlington | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Hackenthorpe | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Harworth | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Kiveton Park | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Mexborough 1_2 | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Mexborough 3 | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
New Orchard Lane | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Silverwood | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
Tickhill Road | Thurcroft | Thurcroft | SoW | 20 | < 1.0 | -
- | - | West Melton Section 3 | SoW | 50 | < 1.0 | -
- | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
Barnsley | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
Barugh 66/11kV | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
Elmhirst Lane 1 | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
Scissett | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
Smithy Green | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
Woolley | Barugh 132/66kV | West Melton Section 3 | SoW | 50 | < 1.0 | -
- | Hunningley | West Melton Section 3 | SoW | 50 | < 1.0 | -
Burton Road | Hunningley | West Melton Section 3 | SoW | 50 | < 1.0 | -
Fish Dam Lane | Hunningley | West Melton Section 3 | SoW | 50 | < 1.0 | -
Stairfoot | Hunningley | West Melton Section 3 | SoW | 50 | < 1.0 | -
- | Hunshelf | West Melton Section 3 | SoW | 50 | < 1.0 | -
Elmhirst Lane 2 | Hunshelf | West Melton Section 3 | SoW | 50 | < 1.0 | -
Hope | Hunshelf | West Melton Section 3 | SoW | 50 | < 1.0 | -
Penistone | Hunshelf | West Melton Section 3 | SoW | 50 | < 1.0 | -
Wheatacre Road | Hunshelf | West Melton Section 3 | SoW | 50 | < 1.0 | -
- | Wakefield Monckton Road | West Melton Section 3 | SoW | 50 | < 1.0 | -
Denby Dale Road | Wakefield Monckton Road | West Melton Section 3 | SoW | 50 | < 1.0 | -
Durkar Low Lane | Wakefield Monckton Road | West Melton Section 3 | SoW | 50 | < 1.0 | -
Woodcock Street | Wakefield Monckton Road | West Melton Section 3 | SoW | 50 | < 1.0 | -
York Street | Wakefield Monckton Road | West Melton Section 3 | SoW | 50 | < 1.0 | -
- | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Aldham | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Dearne Road | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Ecclesfield | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Elsecar | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Houghton Main | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Kilnhurst | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Tankersley Park | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Wath Upon Dearne | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
Worsbrough Park | West Melton | West Melton Section 3 | SoW | 50 | < 1.0 | -
- | - | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Darnall | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Mansfield Road 2 | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Orgreave | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Revill Lane | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Shirland Lane | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Stoke Street | Attercliffe | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Blackburn Meadows B | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Blackburn Meadows 33/11kV | Blackburn Meadows B | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
BOC Brinsworth | Blackburn Meadows B | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Templeborough 33/11kV | Blackburn Meadows B | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Tinsley Wire Industries | Blackburn Meadows B | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Armthorpe | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Askern | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Austerfield | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Balby | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Barnburgh | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Brodsworth | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Hickleton | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
ICI Fibres | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Kirk Sandall | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Markham Gates | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Rockware | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Stainforth | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Thorne | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
West End Lane | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
West Moor Park | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Wheatley Park | Doncaster B/Thorpe Marsh | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Doncaster Central | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Bentley | Doncaster Central | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Greyfriars Rd | Doncaster Central | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Greyfriars Road 3/4 | Doncaster Central | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Mallard Way | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Belmont Avenue | Mallard Way | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
Jarratt Street | Mallard Way | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Park Street | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Rawmarsh Road 1_2 | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Rawmarsh Road 3_4 | West Melton/Thorpe Marsh | SoW | 50 | < 1.0 | -
- | Wincobank | Wincobank | SoW | 50 | 50 | -
New Droppingwell Road | Wincobank | Wincobank | SoW | 50 | 50 | -
Shepcote Tinsley | Wincobank | Wincobank | SoW | 50 | 50 | -
Tinsley Park Road | Wincobank | Wincobank | SoW | 50 | 50 | -
Waverley Business Park | Wincobank | Wincobank | SoW | 50 | 50 | -
Condition 1: Voltage Regulation at a Grid Supply Point In accordance with the ENA Engineering Recommendation G99, the Embedded Power Station shall be capable of operating throughout the power factor range of: (i) 0.92 lagging to 0.92 leading for a synchronous Power Generator Module; and (ii) 0.95 lagging to 0.95 leading for a Power Park Module. However the generator shall operate at a fixed reactive import setting (lead power factor) to offset the susceptance of the dedicated connection cable to ensure that there is no net increase of reactive power export at the Grid Supply Point. This reactive power import shall be maintained at all times irrespective of whether or not the generator is in operation.
Condition 2: Emergency Tripping Instructions Northern Powergrid will require the capability to remotely switch off embedded power stations with a connection voltage greater than 25kV under emergency conditions and following a direct instruction from NGESO to de-energise excess generation. This will be a very rare event and will be achieved by remotely issuing a tripping signal to the generator metering circuit breaker or synchronising circuit breaker, the details of which shall be agreed between Northern Powergrid and the customer.
Notes The values in the table above detail the available headroom (before a Statement of Works is required) as at the 28th May 2024; this could be further eroded by any customers who have accepted connection offers since the 28th May 2024. If the proposed size of any new connection is greater than the available headroom (as detailed in the table above), we will be required to submit a “Modification Application” (ModApp) to NGESO who will identify if any works are required on the transmission network to facilitate this connection. Customers who trigger this “ModApp” process may be subject to additional charges.

## Northeast GSP Constraints
Generation heat map - Distribution/Transmission interface
A view of Grid Supply Points (GSP) where transmission level reinforcement will be required
License area | Northern Powergrid (Northeast) plc
Date | 2024-05-28
GSP | ESO proposed customer energisation date* | Constraint information |  |  | Further constraint information
|  | Thermal Generation | Thermal Demand | Fault level
Blyth 66kV | 2036-10-01 | Yes | Yes | Yes
Hartmoor | 2033-10-01 | Yes | - | -
Hawthorn Pit | 2033-10-01 | Yes | - | -
Fourstones 20kV | 2036-10-01 | - | - | -
Knaresborough | 2035-10-01 | Yes | Yes | -
Lackenby | 2031-10-01 | Yes | - | Yes
Norton | 2033-10-01 | Yes | - | -
Osbaldwick | 2033-08-01 | Yes | - | Yes
Poppleton | 2034-10-01 | Yes | Yes | Yes
Saltholme | 2033-10-28 | Yes | - | -
Spennymoor | 2033-10-01 | Yes | Yes | -
Stella South & North 132kV (N) | 2036-10-01 | Yes | Yes | Yes
Stella South & North 132kV (S) | 2036-10-01 | Yes | Yes | Yes
Tynemouth | 2033-10-01 | Yes | - | Yes
West Boldon | 2033-10-01 | Yes | Yes | -
* This is the completion date as per the construction agreement in the Bilateral Connection Agreement between Northern Powergrid and National Grid.
Important information to note
We are committed to working with customers impacted and to being open and transparent about what we know. We are updating our network availability heat maps with information on known constraints, as a result of transmission reinforcement at the affected GSPs and reviewing this information on a monthly basis. The information provided represents our best view at the current time and is updated when we receive offers and relevant information from National Grid ESO, so that our customers can make more informed choices about how and where to connect. If you have questions about the information provided, contact transmission.enquiries@northernpowergrid.com
Other relevant information
The NGET website features further information about the transmission constraints and reinforcement works required in Northern Powergrid licence areas.
www.customer.nationalgridet.com/s/pre-application

## Yorkshire GSP Constraints
Generation heat map - Distribution/Transmission interface
A view of Grid Supply Points (GSP) where transmission level reinforcement will be required
License area | Northern Powergrid (Yorkshire) plc
Date | 2024-05-28
GSP | ESO proposed customer energisation date* | Constraint information |  |  | Further constraint information
|  | Thermal Generation | Thermal Demand | Fault level
Bradford West | 2037-10-31 | - | - | -
Camblesforth | 2033-10-01 | Yes | - | Yes
Creyke Beck | 2034-10-01 | Yes | - | Yes
Drax | 2035-10-01 | Yes | - | Yes
Elland | 2037-10-01 | - | Yes | -
Ferrybridge A | 2035-10-01 | Yes | Yes | Yes
Ferrybridge B | 2035-10-01 | Yes | Yes | Yes
Grimsby West | 2033-11-01 | Yes | Yes | -
Keadby | 2034-10-01 | Yes | - | Yes
Kirkstall B | 2037-10-01 | - | - | Yes
Neepsend | 2036-10-01 | - | - | -
Pitsmoor 1/2 | 2033-10-01 | - | - | - | Mar-2027 completion date driven by DNO works - condition based asset replacement.
Pitsmoor 3/4 | 2033-10-01 | - | - | -
Saltend North | 2037-10-01 | Yes | Yes | Yes
Skelton Grange | 2035-10-01 | No | Yes | No
Templeborough | 2033-10-01 | - | - | -
Thurcroft | 2034-10-01 | - | - | -
West Melton3 | 2033-10-01 | Yes | Yes | Yes
West Melton/TM | 2033-10-01 | - | - | -
* This is the completion date as per the construction agreement in the Bilateral Connection Agreement between Northern Powergrid and National Grid.
Important information to note
We are committed to working with customers impacted and to being open and transparent about what we know. We are updating our network availability heat maps with information on known constraints, as a result of transmission reinforcement at the affected GSPs and reviewing this information on a monthly basis. The information provided represents our best view at the current time and is updated when we receive offers and relevant information from National Grid ESO, so that our customers can make more informed choices about how and where to connect. If you have questions about the information provided, contact transmission.enquiries@northernpowergrid.com
Links and other relevant information
The NGET website features further information about the transmission constraints and reinforcement works required in Northern Powergrid licence areas.
www.customer.nationalgridet.com/s/pre-application