## Introduction
Distribution Network Options Assessment (DNOA) Report 2 Datasheets 2024
Summary Page
Published October 2024
This document is the excel format version of the Distribution Network Options Assessment (DNOA) Report. The purpose of the DNOA is to transparently communicate our investment decisions and future network intervention plans to stakeholders, and to highlight areas where Flexibility Services may be required over the next five years. This benefits our stakeholders by enabling them to factor our network plans and requirements for Flexibility Services into their planning.
Contents
Worksheet | Description
Table 1 | Our planned network interventions over the next 5 years for our whole network down to the primary substation level

## Table 1
[12 empty] | Flexibility Required (Best View) (MW) |  |  |  |  | Flexibility Procured (MW) |  | Flexibility Procured (%)
Substation Name | Voltages | Substation Postcode | Licence Area | Number of Transformers | Transformer Rating ONAN/OFAF (MVA) | Substation Capacity (MVA) | DNOA Intervention Decision | Constraint Year | Constraint Season | Flexibility ceiling price (£/MWh) | Reinforcement delivery time (years) | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2024/25 | 2025/26 | 2024/25 | 2025/26 | Postal Sectors | Scheme Description
Crowle | 66/11kV | DN17 4BB | Yorkshire | Single | 7.5/15 | 4.5 | Flexibility/Reinforcement | 2024/25 | Autumn and Winter | 248 | 2 | 0.4 | 0.7 | 2.3639 | 2.6336 | 2.845 | 0.218 | 0.18 | 55 | 26 | DN17 1; DN17 3; DN17 4; DN8 5; DN9 1 | -Crowle 66/11 kV substation is equipped with a single 7.5/15 MVA transformer, and has a firm capacity of 4.5 MVA. Network load is forecasted to exceed firm capacity in 2024/25. -Insufficient Flexibility Services have been procured. Hence we will start reinforcement works and use partial Flexibility Services to help relieve the network overload in the interim. -We will continue Flexibility tendering and may stall reinforcement works if enough Flexibility is procured.
Faraday Street | 66/11kV | TS1 4JG | Northeast | Double | 15/18.75 | 22.6 | Signpost | 2026/27 | TBC | TBC | TBC | - | - | 3.2708 | 3.7368 | 4.0503 | - | - | 0 | 0 | TS1 2; TS1 3; TS1 4; TS1 5; TS177; TS2 1; TS3 7; TS4 2; TS5 4; TS5 5; TS5 6 | - Faraday Street 66/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 22.6 MVA. Network load is forecasted to exceed firm capacity in 2026/27. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Hemsworth | 66/11kV | WF9 5BZ | Yorkshire | Single | 2024-12-12 | 10 | Signpost | 2027/28 | TBC | TBC | TBC | - | - | - | 0.11222 | 0.47365 | - | - | 0 | 0 | WF4 1; WF4 2; WF7 7; WF8 3; WF9 1; WF9 4; WF9 5 | - Hemsworth 66/11 kV substation is equipped with a single 12/24 MVA transformer, and has a firm capacity of 10.0 MVA. Network load is forecasted to exceed firm capacity in 2027/28. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Holme Upon Spalding Moor | 33/11kV | YO43 4BX | Yorkshire | Single | 2024-12-12 | 8 | Signpost | 2028/29 | TBC | TBC | TBC | - | - | - | - | 0.3 | - | - | 0 | 0 | DN14 7; HU15 2; YO42 1; YO42 4; YO43 3; YO43 4; YO62 5; YO8 6; YO8 7 | - Holme Upon Spalding Moor 33/11 kV substation is equipped with a single 12/24 MVA transformer, and has a firm capacity of 8 MVA. Network load is forecasted to exceed firm capacity in 2028/29. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Husthwaite | 33/11kV | YO61 4PN | Northeast | Double | 7.5/15 | 15 | Signpost | 2025/26 | TBC | TBC | TBC | - | 0.24923 | 0.92403 | 1.6092 | 2.1947 | - | - | 0 | 0 | DL6 3; TS9 7; YO51 9; YO60 6; YO61 1; YO61 2; YO61 3; YO61 4; YO61 5; YO62 4; YO62 5; YO6 3; YO7 2; YO7 3 | - Husthwaite 33/11 kV substation is equipped with 2x 7.5/15 MVA transformers, and has a firm capacity of 15.0 MVA. Network load is forecasted to exceed firm capacity in 2025/26. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Kirkburn | 66/11kV | YO25 9EH | Yorkshire | Single | 15/30 | 8 | Flexibility | 2024/25 | Autumn and Winter | 1200 | 2 | 0.30713 | 0.3 | 0.49521 | 0.6508 | 0.79379 | - | - | 0 | 0 | YO17 9; YO25 0; YO25 1; YO25 3; YO25 4; YO25 8; YO25 9; YO42 1 | - Kirkburn 66/11 kV substation is equipped with a single 15/30 MVA transformer, and has a firm capacity of 8 MVA. Network load is forecasted to exceed firm capacity in 2024/25. -To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement.
Martongate | 66/11kV | YO16 6RX | Yorkshire | Double | 10/12.5 | 14.1 | Signpost | 2028/29 | TBC | TBC | TBC | - | - | - | - | 0.8 | - | - | 0 | 0 | YO14 0; YO14 9; YO15 1; YO15 2; YO16 4; YO16 6; YO16 7 | - Martongate 66/11 kV substation is equipped with 2x 10/12.5 MVA transformers, and has a firm capacity of 14.1 MVA. Network load is forecasted to exceed firm capacity in 2028/29. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Monkseaton | 33/11kV | NE25 9AF | Northeast | Double | 15/18.75 | 20.5 | Signpost | 2026/27 | TBC | TBC | TBC | - | - | 0.14024 | 0.75595 | 1.2212 | - | - | 0 | 0 | NE25 0; NE25 8; NE25 9; NE26 1; NE26 2; NE26 3; NE26 4; NE27 0; NE29 8 | - Monseaton 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 20.5 MVA. Network load is forecasted to exceed firm capacity in 2026/27. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Moor Road | 33/11kV | LS6 4BJ | Yorkshire | Double | 15/18.75 | 20.1 | Signpost | 2025/26 | TBC | TBC | TBC | - | 2.2649 | 3.0946 | 3.8557 | 4.3791 | - | - | 0 | 0 | LS16 5; LS16 7; LS16 8; LS4 2; LS5 3; LS6 1; LS6 2; LS6 3; LS6 4 | - Moor Road 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 20.1 MVA. Network load is forecasted to exceed firm capacity in 2025/26. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Ripon | 33/11kV | HG4 1QE | Northeast | Double | 2024-12-12 | 18.7 | Signpost | 2028/29 | TBC | TBC | TBC | - | - | - | - | 0.3 | - | - | 0 | 0 | DL7 9; DL8 2; HG3 3; HG4 1; HG4 2; HG4 3; HG4 4; HG4 5; YO7 3; YO7 4 | - Ripon 33/11 kV substation is equipped with 2x 12/24 MVA transformers, and has a firm capacity of 18.7 MVA. Network load is forecasted to exceed firm capacity in 2028/29. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Selby | 33/11kV | YO8 8NB | Yorkshire | Double | 15/30 | 29 | Signpost | 2028/29 | TBC | TBC | TBC | - | - | - | - | 0.24865 | - | - | 0 | 0 | LN8 3; LS24 9; YO19 6; YO8 0; YO8 3; YO8 4; YO8 5; YO8 6; YO8 8; YO8 9 | - Selby 33/11 kV substation is equipped with 2x 15/30 MVA transformers, and has a firm capacity of 29.0 MVA. Network load is forecasted to exceed firm capacity in 2028/29. - To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Southgate | 33/11kV | YO43 3BE | Yorkshire | Single | 11.5/23 | 8 | Signpost | 2028/29 | TBC | TBC | TBC | - | - | - | - | 0.2 | - | - | 0 | 0 | HU15 2; HU17 7; YO25 9; YO42 4; YO4 3; YO43 3; YO43 4 | -Southgate 33/11 kV substation is equipped with a single 11.5/23 MVA transformer, and has a firm capacity of 8.0 MVA. Network load is forecasted to exceed firm capacity in 2028/29. -To relieve the network overload, we have signposted the need for Flexibility Services in our 2024 Autumn flexibility tendering round.
Starbeck | 33/11kV | HG2 7PT | Northeast | Double | 15/18.75 | 21.1 | Flexibility | 2024/25 | Autumn and Winter | 5190 | 2 | 0.5 | 0.5 | 2.1052 | 2.8103 | 3.3264 | - | - | 0 | 0 | HG1 3; HG1 4; HG2 7; HG2 8; HG3 1; HG3 3; HG5 0; HG5 8; HG5 10 | -Starbeck 33/11 kV substation is equipped with 2x 15/18.75 MVA transformers, and has a firm capacity of 21.1 MVA. Network load is forecasted to exceed firm capacity in 2024/25. -To relieve the network overload, we will deploy Flexibility Services solution until it is no longer viable to delay reinforcement. -We have tendered for Flexibility Services procurement in our 2024 Autumn flexibility tendering round.